Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238213 - VALANCE HEATING AND COOLING UNITS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Electric radiant heaters.

2. Hydronic heating and cooling panels.

1.2 ACTION SUBMITTALS

A. Product Data: Include rated capacities, specialties, and accessories for each product indicated.

B. Shop Drawings:

1. Include plans, elevations, sections, details, and attachments to other work. Detail equipment assemblies and suspension and attachment.

2. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain subparagraph below if equipment includes wiring.

3. Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 ELECTRIC RADIANT HEATERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Berko Electric Heating; a division of Marley Engineered Products.
2. Chromalox Inc.; a division of Emerson Electric Company.
3. Fostoria Industries, Inc.; a division of TPI Corporation.
4. Markel Products; a division of TPI Corporation.
5. Omega Engineering, Inc.
6. QMark Electric Heating; a division of Marley Engineered Products.
7. <Insert manufacturer's name>.

Retain "Quartz Lamp Heating Elements," "Quartz Tube Heating Elements," or "Metal-Sheathed Heating Elements" Paragraph below. If more than one type of heating element is required, indicate each type in a schedule on Drawings.

C. Quartz Lamp Heating Elements: Coiled tungsten-wire heating element enclosed in clear quartz tube.

D. Quartz Tube Heating Elements: Nickel-chromium-wire heating element enclosed in quartz tube.

E. Metal-Sheathed Heating Elements: Nickel-chromium-wire heating element embedded in magnesium oxide powder enclosed in metal sheath. Comply with UL 1030.

In first paragraph below, retain UL 499 for supplemental heating applications requiring humidity control; retain UL 2021 for comfort heating applications. Retain all three options if both applications are required.

F. Comply with [UL 499] [and] [UL 2021].

G. Enclosures: [Aluminized] [Stainless] [Painted]-steel housing with anodized-aluminum reflector.

Retain "Finish" Subparagraph below for painted enclosures.

1. Finish: Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

H. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain "Unit Controls" Paragraph below for integral control device if control devices are not specified in Section 230900 "Instrumentation and Control for HVAC."

I. Unit Controls:

Retain one or more of three subparagraphs below. If more than one type of control device is required, indicate each type in a schedule on Drawings.

1. Line-voltage thermostat.

2. Enclosed contactor for remote thermostat.

3. Snow and ice detector with moisture sensor and integral temperature sensor.

If Project has more than one type or size of electric radiant heater, delete "Capacities and Characteristics" Paragraph below and schedule heaters on Drawings.

J. Capacities and Characteristics:

1. Enclosure Length: <Insert inches (mm)>.

2. Mounting Height: <Insert feet (m)>.

3. Heating Capacity: <Insert kilowatts>.

4. Radiation Pattern: [30] [60] [90] <Insert number> [symmetric] [asymmetric]-degree-included angle.

5. Electrical Characteristics for Single-Point Connection:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 HYDRONIC HEATING[ AND COOLING] PANELS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AIRTEX Radiant Systems; a division of Engineered Air Ltd.
2. Rosemex Products.
3. Sun-El Corporation.
4. Twa Panel Systems Inc.
5. <Insert manufacturer's name>.

C. Description: [Modular] [Linear] sheet-metal panel with serpentine water piping, suitable for [lay-in installation flush with T-bar ceiling grid] [surface mounting] [recessed mounting].

1. Panels: Minimum [0.0336-inch- (0.86-mm-) thick, galvanized-steel] [0.0396-inch- (1.0-mm-) thick, aluminum] sheet.

2. Backing Insulation: Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] <Insert dimension> thick, mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 612, Type IA or Type IB with factory-applied jacket.

Retain one of three "Exposed-Side Panel Finish" subparagraphs below. If more than one type of finish is required, indicate each type in a schedule on Drawings.

3. Exposed-Side Panel Finish: Apply silk-screened finish to match appearance of acoustical ceiling tiles selected by Architect.

4. Exposed-Side Panel Finish: Factory prime coated, ready for field painting.

5. Exposed-Side Panel Finish: Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

6. Factory Piping: [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)] copper tube with ASME B16.22 wrought-copper fittings and brazed joints. Piping shall be mechanically bonded to panel.

Retain "Surface-Mounted Trim" Subparagraph below for surface-mounted panels.

7. Surface-Mounted Trim: Sheet metal with baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain "Accessories" Subparagraph below for linear panels only.

8. Accessories:

a. [5-inch (127-mm)] [6-inch (152-mm)] [8-inch (203-mm)] panel with drape track recess.

b. 5-inch (127-mm) male bullnose panel.

c. 5-inch (127-mm) female bullnose panel.

d. 4-inch (102-mm) male corner panel.

e. 4-inch (102-mm) female corner panel.

f. Inside corner panel.

g. 1/2-inch (13-mm) filler panel.

If Project has more than one type or size of hydronic heating and cooling panel, delete "Capacities and Characteristics" Paragraph below and schedule panels on Drawings.

D. Capacities and Characteristics:

1. Nominal Panel Size: [24 by 24 inches (600 by 600 mm)] [24 by 36 inches (600 by 900 mm)] [24 by 48 inches (600 by 1200 mm)] [24 by 60 inches (600 by 1500 mm)] <Insert dimensions>.

2. Piping Inlet and Outlet: [NPS 1/2 (DN 15)] <Insert pipe size>.

3. Heating:

a. Capacity: <Insert Btu/h (kW)>.

b. Room Temperature: <Insert deg F (deg C)>.

c. Entering-Water Temperature: <Insert deg F (deg C)>.

d. Average Water Temperature: <Insert deg F (deg C)>.

e. Water Flow: <Insert gpm (L/s)>.

f. Water-Side Pressure Loss: <Insert psig (kPa)>.

4. Cooling:

a. Sensible Capacity: <Insert Btu/h (kW)>.

b. Dry-Bulb Room Temperature: <Insert deg F (deg C)>.

c. Wet-Bulb Room Temperature: <Insert deg F (deg C)>.

d. Entering-Water Temperature: <Insert deg F (deg C)>.

e. Average Water Temperature: <Insert deg F (deg C)>.

f. Water Flow: <Insert gpm (L/s)>.

g. Water-Side Pressure Loss: <Insert psig (kPa)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install radiant heating and cooling units level and plumb.

B. Suspend radiant heaters from structure.

Revise first paragraph below for other types of construction that penetrate or are supported by ceilings.

C. Coordinate layout and installation of radiant heaters and suspension-system components with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, communications system, security system, and partition assemblies.

D. Support for Radiant Heating and Cooling Panels in or on Grid-Type Suspended Ceilings: Use grid as a support element.

1. Install a minimum of four ceiling support-system rods or wires for each panel. Locate not more than 6 inches (150 mm) from panel corners.

2. Support Clips: Fasten to panel and to ceiling grid members at or near each panel corner with clips designed for the application.

3. Panels of Sizes Less Than Ceiling Grid: Install as indicated on reflected ceiling plans, or center in acoustical panel and support panels independently with at least two 3/4-inch (19-mm) metal channels spanning and secured to ceiling tees.

To comply with requirements of the Americans with Disabilities Act, verify mounting height in first paragraph below with authorities having jurisdiction. Verify locations of thermostats with Drawings and room details before installation.

E. Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

Retain first three paragraphs below for hydronic heating and cooling panels. Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Piping installation requirements are specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

G. Unless otherwise indicated, install shutoff valve and union or flange at each connection.

H. Install piping adjacent to unit to allow service and maintenance.

I. Ground electric units according to Section 260526 "Grounding and Bonding for Electrical Systems."

J. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

Retain first subparagraph below if units have electric heat.

1. Operate electric heating elements through each stage to verify proper operation and electrical connections.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and units.

B. Remove and replace malfunctioning units and retest as specified above.

C. After installing panels, inspect unit cabinet for damage to finish. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.

D. Prepare test and inspection reports.

END OF SECTION 238213

	VALANCE HEATING AND COOLING UNITS
	238213 - 1



