Copyright 2011 AIA
MasterSpec Professional
12/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238216.11 - HYDRONIC AIR COILS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes hydronic heating and cooling air coils.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 DESCRIPTION

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, humidification and dehumidification, drain-pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

A. ASHRAE Compliance: Comply with applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

2.2 COILS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aerofin Corporation.

2. Carrier Corporation; a UTC company.

3. Coil Company, LLC.

4. Colmac Coil Manufacturing, Inc.

5. Dunham-Bush, Inc.

6. Greenheck Fan Corporation.

7. Heatcraft Refrigeration Products LLC.

8. Super Radiator Coils.

9. Trane.

10. USA Coil & Air.

11. <Insert manufacturer's name>.

C. Performance Ratings: Tested and rated according to AHRI 410 and ASHRAE 33.

Pressure/temperature ratings in "Minimum Working-Pressure/Temperature Ratings" Paragraph below are common. Some manufacturers may vary ratings.

D. Minimum Working-Pressure/Temperature Ratings: 200 psig (1380 kPa), 325 deg F (163 deg C).

E. Source Quality Control: Factory tested to 300 psig (2070 kPa).

F. Tubes: ASTM B 743 copper, minimum [0.020 inch (0.508 mm)] [0.035 inch (0.889 mm)] [0.049 inch (1.245 mm)] <Insert dimension> thick.

G. Fins: [Aluminum] [Copper], minimum [0.006 inch (0.152 mm)] [0.010 inch (0.254 mm)] <Insert dimension> thick.

H. Headers: [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Steel with brazed joints, prime coated].

I. Frames: Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] thick for [slip-in] [flanged] mounting.

If Project has more than one type or size of hot-water coil, delete "Hot-Water Coil Capacities and Characteristics" Paragraph below and schedule coils on Drawings.

J. Hot-Water Coil Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length: <Insert inches (mm)>.

b. Finned Width: <Insert inches (mm)>.

2. Minimum Fin Spacing: [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert dimension>.

3. Tube Diameter: [0.375 inch (9.5 mm)] [0.50 inch (12.7 mm)] [0.625 inch (15.9 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert dimension>.

4. Number of Rows: <Insert number>.

5. Serpentine: [Single] [Half] [Full].

6. Mounting: [Slip in] [Flanged].

7. Coating: [Baked phenolic] [Cathodic epoxy e-coat].

8. Air Side:

a. Flow Rate: <Insert cfm (L/s)>.

b. Finned Area Face Velocity: <Insert fpm (m/s)>.

c. Static Pressure Drop: <Insert inches wg (Pa)>.

d. Total Capacity: <Insert Btu/h (kW)>.

e. Entering Temperature: <Insert deg F (deg C)>.

f. Leaving Temperature: <Insert deg F (deg C)>.

9. Water Side:

a. Flow Rate: <Insert gpm (L/s)>.

b. Tube Velocity: <Insert fpm (m/s)>.

c. Glycol Type: [Ethylene] [Propylene].

d. Aqueous Glycol Solution Concentration: <Insert percentage>.

e. Pressure Drop: <Insert feet (kPa)>.

f. Entering Temperature: <Insert deg F (deg C)>.

g. Leaving Temperature: <Insert deg F (deg C)>.

If Project has more than one type or size of chilled-water coil, delete "Chilled-Water Coil Capacities and Characteristics" Paragraph below and schedule coils on Drawings.

K. Chilled-Water Coil Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length: <Insert inches (mm)>.

b. Finned Width: <Insert inches (mm)>.

2. Minimum Fin Spacing: [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert dimension>.

3. Tube Diameter: [0.375 inch (9.5 mm)] [0.50 inch (12.7 mm)] [0.625 inch (15.9 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert dimension>.

4. Number of Rows: <Insert number>.

5. Serpentine: [Half] [Single] [Double].

6. Mounting: [Slip in] [Flanged].

7. Coating: [Baked phenolic] [Cathodic epoxy e-coat].

8. Air Side:

a. Flow Rate: <Insert cfm (L/s)>.

b. Finned Area Face Velocity: <Insert fpm (m/s)>.

c. Static Pressure Drop: <Insert inches wg (Pa)>.

d. Total Capacity: <Insert Btu/h (kW)>.

e. Sensible Capacity: <Insert Btu/h (kW)>.

f. Entering Dry-Bulb Temperature: <Insert deg F (deg C)>.

g. Entering Wet-Bulb Temperature: <Insert deg F (deg C)>.

h. Leaving Dry-Bulb Temperature: <Insert deg F (deg C)>.

i. Leaving Wet-Bulb Temperature: <Insert deg F (deg C)>.

9. Water Side:

a. Flow Rate: <Insert gpm (L/s)>.

b. Tube Velocity: <Insert fpm (m/s)>.

c. Glycol Type: [Ethylene] [Propylene].

d. Aqueous Glycol Solution Concentration: <Insert percentage>.

e. Pressure Drop: <Insert feet (Pa)>.

f. Entering Temperature: <Insert deg F (deg C)>.

g. Leaving Temperature: <Insert deg F (deg C)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install coils level and plumb.

B. Install coils in metal ducts and casings constructed according to SMACNA's "HVAC Duct Construction Standards, Metal and Flexible."

C. Install [galvanized] [stainless]-steel drain pan under each cooling coil.

Option in first subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain option to comply with LEED Prerequisite IEQ 1.

1. Construct drain pans with connection for drain; insulated[ and complying with ASHRAE 62.1].

2. Construct drain pans to extend beyond coil length and width and to connect to condensate trap and drainage.

3. Extend drain pan upstream and downstream from coil face.

4. Extend drain pan under coil headers and exposed supply piping.

D. Install moisture eliminators for cooling coils. Extend drain pan under moisture eliminator.

E. Straighten bent fins on air coils.

F. Clean coils using materials and methods recommended in writing by manufacturers, and clean inside of casings and enclosures to remove dust and debris.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified for hydronic piping systems.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to coils to allow service and maintenance.

C. Connect water piping with unions and shutoff valves to allow coils to be disconnected without draining piping. Control valves are specified in Section 230900 "Instrumentation and Control for HVAC," and other piping specialties are specified in Section 232116 "Hydronic Piping Specialties."

END OF SECTION 238216.11
	HYDRONIC AIR COILS
	238216.11 - 1



