Copyright 2011 AIA
MasterSpec Professional
12/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238216.12 - STEAM AIR COILS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes steam heating air coils.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 DESCRIPTION

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, humidification and dehumidification, drain-pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

A. ASHRAE Compliance: Comply with applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

2.2 COILS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Aerofin Corporation.

2. Carrier Corporation; a UTC company.

3. Coil Company, LLC.

4. Colmac Coil Manufacturing, Inc.

5. Dunham-Bush, Inc.

6. Greenheck Fan Corporation.

7. Heatcraft Refrigeration Products LLC.

8. Super Radiator Coils.

9. Trane.

10. USA Coil & Air.

11. <Insert manufacturer's name>.

C. Performance Ratings: Tested and rated according to AHRI 410 and ASHRAE 33.

Pressure/temperature ratings in "Minimum Working-Pressure/Temperature Ratings" Paragraph below are common. Some manufacturers may vary ratings.

D. Minimum Working-Pressure/Temperature Ratings: 100 psig (690 kPa), 400 deg F (204 deg C).

E. Source Quality Control: Factory tested to 300 psig (2070 kPa).

F. Tubes: ASTM B 743 copper, minimum [0.025 inch (0.635 mm)] [0.035 inch (0.889 mm)] [0.049 inch (1.245 mm)] <Insert dimension> thick.

G. Fins: [Aluminum] [Copper], minimum [0.006 inch (0.152 mm)] [0.010 inch (0.254 mm)] <Insert dimension> thick.

H. Headers: [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs, and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Steel with brazed joints, prime coated].

Indicate single- or distributing-tube type in "Capacities and Characteristics" Paragraph or in schedule on Drawings.

I. Tube Type: Single or distributing as indicated.

J. Frames: Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] thick for [slip-in] [flanged] mounting.

If Project has more than one type or size of steam coil, delete "Capacities and Characteristics" Paragraph below and schedule coils on Drawings.

K. Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length: <Insert inches (mm)>.

b. Finned Width: <Insert inches (mm)>.

2. Minimum Fin Spacing: [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert dimension>.

3. Tube Diameter: [0.375 inch (9.5 mm)] [0.50 inch (12.7 mm)] [0.625 inch (15.9 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert dimension>.

4. Number of Rows: <Insert number>.

5. Mounting: [Slip in] [Flanged].

6. Air Side:

a. Flow Rate: <Insert cfm (L/s)>.

b. Finned Area Face Velocity: <Insert fpm (m/s)>.

c. Static Pressure Drop: <Insert inches wg (Pa)>.

d. Total Capacity: <Insert Btu/h (kW)>.

e. Entering Temperature: <Insert deg F (deg C)>.

f. Leaving Temperature: <Insert deg F (deg C)>.

7. Steam Side:

a. Inlet Pressure: <Insert psig (kPa)>.

b. Tube Type: [Single] [Distributing].

c. Condensing Capacity: <Insert lb/h (g/s)>.

d. Pressure Drop: <Insert psig (kPa)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install coils level and plumb.

B. Install coils in metal ducts and casings constructed according to SMACNA's "HVAC Duct Construction Standards, Metal and Flexible."

C. Straighten bent fins on air coils.

D. Clean coils using materials and methods recommended in writing by manufacturers, and clean inside of casings and enclosures to remove dust and debris.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified for steam and condensate piping systems.

A. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to coils to allow service and maintenance.

C. Connect steam piping with gate valve and union and steam condensate piping with union, strainer, trap, and gate valve to allow coils to be disconnected without draining piping. Control valves are specified in Section 230900 "Instrumentation and Control for HVAC," and other piping specialties are specified in Section 232213 "Steam and Condensate Heating Piping."

END OF SECTION 238216.12
	STEAM AIR COILS
	238216.12 - 1



