Copyright 2011 AIA
MasterSpec Professional
06/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238233 - CONVECTORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes [hydronic] [electric] convectors.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:

1. Include plans, elevations, sections, and details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include details and dimensions of custom-fabricated enclosures.

4. Indicate location and size of each field connection.

Retain first subparagraph below for hydronic convectors.

5. Indicate location and arrangement of piping valves and specialties.

Retain first subparagraph below for convectors with integral controls; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

6. Indicate location and arrangement of integral controls.

7. Include enclosure joints, corner pieces, access doors, and other accessories.

Retain subparagraph below for electric convectors.

8. Include diagrams for power, signal, and control wiring.

C. Samples: For each exposed product and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 ELECTRIC CONVECTORS

Copy this article and re-edit for each style of convector, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Berko; Marley Engineered Products.

2. Chromalox.

3. Indeeco.

4. Markel Products Company; TPI Corporation.

5. Marley Engineered Products.

6. Ouellet Canada Inc.

7. Qmark; Marley Engineered Products.

8. <Insert manufacturer's name>.

C. Description: Factory-packaged units constructed according to UL 499, UL 1030, and UL 2021.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Heating Elements: Nickel-chromium-wire heating element enclosed in metallic sheath mechanically bonded to fins, with high-temperature cutout and sensor running the full length of element. Element supports shall eliminate thermal expansion noise.

If more than one configuration is required, delete subparagraphs below and schedule on Drawings.

1. Volts: <Insert value>.

2. Phase: <Insert value>.

3. Hertz: <Insert value>.

4. Heat Output: [300] [500] [750] [1000] [1250] [1500] [1750] [2000] [2250] [2500] <Insert number> W.

E. Front and Top Panel: Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] <Insert dimension> thick steel with exposed corners rounded; removable front panels with tamper-resistant fasteners braced and reinforced for stiffness.

F. Wall-Mounted Back and End Panels: Minimum 0.0428-inch- (1.1-mm-) thick steel.

G. Floor-Mounted Pedestals: Conceal conduit for power and control wiring at maximum 36-inch (914-mm) spacing. Pedestal-mounted back panel shall be solid panel matching front panel.

H. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.

I. Insulation: 1/2-inch- (13-mm-) thick, fibrous glass on inside of the back of the enclosure.

J. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

K. Damper: Knob-operated internal damper.

L. Access Doors: Factory made, permanently hinged with tamper-resistant fastener, minimum size 6 by 7 inches (150 by 175 mm), integral with enclosure.

M. Enclosure Style: [Sloped] [Flat] top.

Retain features required for Project in subparagraphs below.

1. Front Inlet Grille: Punched louver; painted to match enclosure.

2. Front Inlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

3. [Top] [Front] Outlet Grille: Punched louver; painted to match enclosure.

4. [Top] [Front] Outlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

5. Enclosure Height: <Insert inches (mm)>.

6. Enclosure Depth: <Insert inches (mm)>.

7. Enclosure Length: <Insert inches (mm)>.

Retain "Unit Controls" Paragraph below for integral control device; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

N. Unit Controls: Integral [line-voltage thermostat with minimum range of 60 to 90 deg F (15 to 32 deg C)] [low-voltage relay and control transformer for remote thermostat].

O. Accessories: Integral disconnect switch, recessing flanges finished to match enclosure or overlapping front cover for fully recessed units, and rubber gaskets to seal cabinet at wall.

2.2 HOT-WATER CONVECTORS

Copy this article and re-edit for each style of convector, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Engineered Air.

2. Rosemex.

3. Slant/Fin Corporation.

4. Sterling Hydronics; a Mestek company.

5. Trane Inc.

6. <Insert manufacturer's name>.

C. Heating Elements: Seamless copper tubing mechanically expanded into evenly spaced aluminum fins and rolled into cast-[iron] [or] [brass] headers with inlet/outlet and air vent; steel side plates and supports. Factory-pressure-test element at minimum 100 psig (690 kPa).

If more than one configuration is required, delete subparagraphs below and schedule on Drawings.

1. Element Height: <Insert inches (mm)>.

2. Element Depth: <Insert inches (mm)>.

3. Element Length: <Insert inches (mm)>.

4. Entering-Air Temperature: [65 deg F (18 deg C)] <Insert temperature>.

5. Heat Output: <Insert Btu/h per ft. (W/m)>.

6. Average Water Temperature: [180 deg F (82 deg C)] <Insert temperature>.

7. Temperature Drop: [10 deg F (5.56 deg C)] [20 deg F (11.1 deg C)] [30 deg F (16.6 deg C)] <Insert temperature>.

8. Pressure Loss: <Insert feet wg (kPa)>.

D. Front and Top Panel: Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] <Insert dimension> thick steel with exposed corners rounded; removable front panels with tamper-resistant fasteners braced and reinforced for stiffness.

E. Wall-Mounted Back and End Panels: Minimum 0.0428-inch- (1.1-mm-) thick steel.

F. Floor-Mounted Pedestals: Conceal conduit for power and control wiring at maximum 36-inch (914-mm) spacing. Pedestal-mounted back panel shall be solid panel matching front panel.

G. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.

H. Insulation: 1/2-inch- (13-mm-) thick, fibrous glass on inside of the back of the enclosure.

I. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

J. Damper: Knob-operated internal damper.

Units with operable front panels may not require access doors.

K. Access Doors: Factory made, permanently hinged with tamper-resistant fastener, minimum size 6 by 7 inches (150 by 175 mm), integral with enclosure.

L. Enclosure Style: [Sloped] [Flat] top.

Retain features required for Project in subparagraphs below.

1. Front Inlet Grille: Punched louver; painted to match enclosure.

2. Front Inlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

3. [Top] [Front] Outlet Grille: Punched louver; painted to match enclosure.

4. [Top] [Front] Outlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

Enclosure dimensions in three subparagraphs below include end pockets for controls and piping.

5. Enclosure Height: <Insert inches (mm)>.

6. Enclosure Depth: <Insert inches (mm)>.

7. Enclosure Length: <Insert inches (mm)>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install convectors level and plumb.

B. Install valves within reach of access door provided in enclosure.

C. Install air-seal gasket between wall and recessed flanges or front cover of fully recessed unit.

D. Install piping within pedestals for freestanding units.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect hot-water convectors and components to piping according to Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

1. Install shutoff valves on inlet and outlet, and balancing valve on outlet.

2. Install shutoff valve on inlet; install strainer, steam trap, and shutoff valve on outlet.

C. Install control valves as required by Section 230900 "Instrumentation and Control for HVAC."

D. Install piping adjacent to convectors to allow service and maintenance.

Retain two paragraphs below for electric convectors.

E. Ground electric convectors according to Section 260526 "Grounding and Bonding for Electrical Systems."

F. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections:

Retain "Leak Test" Subparagraph below for hot-water convectors.

1. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Retain "Operational Test" Subparagraph below for electric convectors.

2. Operational Test: After electrical circuitry has been energized, start convectors to confirm proper operation.

3. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Convectors will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 238233

	CONVECTORS
	238233 - 1



