Copyright 2011 AIA
MasterSpec Professional
06/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238236 - FINNED-TUBE RADIATION HEATERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes [hydronic] [electric], [baseboard] [and] [finned-tube] radiation heaters.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:

1. Include plans, elevations, sections, and details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include details and dimensions of custom-fabricated enclosures.

4. Indicate location and size of each field connection.

5. Indicate location and arrangement of piping valves and specialties.

Retain first subparagraph below for finned-tube radiation heaters with integral controls; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

6. Indicate location and arrangement of integral controls.

7. Include enclosure joints, corner pieces, access doors, and other accessories.

Retain subparagraph below for electric convection units.

8. Include diagrams for power, signal, and control wiring.

C. Samples: For each exposed product and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 ELECTRIC BASEBOARD RADIATION HEATERS

Copy this article and re-edit for each style of baseboard radiation heater, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Berko; Marley Engineered Products.

2. Chromalox.

3. Indeeco.

4. Markel Products Company; TPI Corporation.

5. Marley Engineered Products.

6. Ouellet Canada Inc.

7. Qmark; Marley Engineered Products.

8. <Insert manufacturer's name>.

C. Description: Factory-packaged units constructed according to UL 499, UL 1030, and UL 2021.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Heating Elements: Nickel-chromium-wire heating element enclosed in metallic sheath mechanically bonded to fins, with high-temperature cutout and sensor running the full length of the element. Element supports shall eliminate thermal expansion noise.

Indicate length and total capacity on Drawings.

1. Volts: <Insert value>.

2. Phase: <Insert value>.

3. Hertz: <Insert value>.

4. Heat Output: <Insert W/ft. (W/m)>.

Retain "Enclosures" or "Rust-Resistant Enclosures" Paragraph below, or retain both and indicate location of each enclosure type on Drawings. Verify optional features with manufacturer.

E. Enclosures: Minimum [0.0329-inch- (0.85-mm-)] [0.0428-inch- (1.1-mm-)] <Insert dimension> thick steel, removable front cover.

1. Full-height back.

2. Full-length damper.

3. End panel.

4. [Plastic end] [End] caps.

5. Inside and outside corners.

6. Joiner pieces to snap together.

7. Enclosure Height: <Insert inches (mm)>.

8. Enclosure Depth: <Insert inches (mm)>.

9. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

10. Element Brackets: Primed and painted steel to support front panel and element.

F. Rust-Resistant Enclosures: Minimum [0.040-inch- (1.0-mm-)] [0.052-inch- (1.3-mm-)] <Insert dimension> thick ASTM A 653/A 653M, G60 (Z180) galvanized-steel, removable front cover.

1. Full-height back.

2. Full-length damper.

3. End panel.

4. [Plastic end] [End] caps.

5. Inside and outside corners.

6. Joiner pieces to snap together.

7. Enclosure Height: <Insert inches (mm)>.

8. Enclosure Depth: <Insert inches (mm)>.

9. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

10. Element Brackets: Primed and painted steel to support front panel and element.

Retain "Unit Controls" Paragraph below for integral control device; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

G. Unit Controls: [Integral line-voltage thermostat] [Integral electronic thermostat] [Remote line-voltage thermostat].

H. Accessories:

1. Filler sections without a heating element matching the adjacent enclosure.

2. Straight-blade-type receptacles complying with DSCC W-C-596G/GEN, NEMA WD 1, NEMA WD 6, and UL 498; in color selected by Architect.

2.2 HOT-WATER BASEBOARD RADIATION HEATERS

Copy this article and re-edit for each style of baseboard radiation heater, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. A.I.M. Radiant Heating.

2. Embassy Industries, Inc.

3. Haydon Corporation, Inc.

4. Hydro-Air Components Inc.

5. Rosemex.

6. Slant/Fin Corporation.

7. Sterling Hydronics; a Mestek company.

8. <Insert manufacturer's name>.

C. Performance Ratings: Rate baseboard radiation heaters according to Hydronics Institute's "I=B=R Testing and Rating Standard for Baseboard Radiation."

Retain one of two "Heating Elements" paragraphs below.

D. Heating Elements: Copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins resting on polypropylene element glides. One end of tube shall be belled.

If more than one configuration is required, delete eight subparagraphs below and schedule on Drawings.

1. Tube Diameter: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] <Insert pipe size>.

2. Fin Size: [2-1/2 by 2-1/2 inches (63 by 63 mm)] [3 by 3 inches (76 by 76 mm)] <Insert dimensions>.

3. Fin Spacing: [40 per foot (131 per m)] [50 per foot (164 per m)] [58 per foot (190 per m)] <Insert value>.

4. Number of Tiers: <Insert number>.

5. Heat Output: <Insert Btu/h per ft. (W/m)>.

6. Entering-Air Temperature: [65 deg F (18 deg C)] <Insert temperature>.

7. Average Water Temperature: [180 deg F (82 deg C)] <Insert temperature>.

8. Minimum Water Velocity: [1/2 fps (0.15 m/s)] <Insert value>.

E. Heating Elements: Steel tubing mechanically expanded into flanged collars of evenly spaced steel fins resting on polypropylene element glides. Tube ends shall be threaded.

If more than one configuration is required, delete eight subparagraphs below and schedule on Drawings.

1. Tube Diameter: [NPS 1-1/4 (DN 32)] <Insert pipe size>.

2. Fin Size: [3 by 3 inches (76 by 76 mm)] <Insert dimensions>.

3. Fin Spacing: [52 per foot (171 per m)] <Insert value>.

4. Number of Tiers: <Insert number>.

5. Heat Output: <Insert Btu/h per ft. (W/m)>.

6. Entering-Air Temperature: [65 deg F (18 deg C)] <Insert temperature>.

7. Average Water Temperature: [180 deg F (82 deg C)] <Insert temperature>.

8. Minimum Water Velocity: [1/2 fps (0.15 m/s)] <Insert value>.

Retain "Enclosures" or "Rust-Resistant Enclosures" Paragraph below, or retain both and indicate location of each enclosure type on Drawings. Verify optional features with manufacturer.

F. Enclosures: Minimum [0.0329-inch- (0.85-mm-)] [0.0428-inch- (1.1-mm-)] <Insert dimension> thick steel, removable front cover.

1. Full-height back.

2. Full-length damper.

3. End panel.

4. End caps.

5. Inside and outside corners.

6. Valve access door.

7. Joiner pieces to snap together.

8. Enclosure Height: <Insert inches (mm)>.

9. Enclosure Depth: <Insert inches (mm)>.

10. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

11. Element Brackets: Primed and painted steel to support front panel and element.

G. Rust-Resistant Enclosures: Minimum [0.040-inch- (1.0-mm-)] [0.052-inch- (1.3-mm-)] <Insert dimension> thick ASTM A 653/A 653M, G60 (Z180) galvanized-steel, removable front cover.

1. Full-height back.

2. Full-length damper.

3. End panel.

4. End caps.

5. Inside and outside corners.

6. Valve access door.

7. Joiner pieces to snap together.

8. Enclosure Height: <Insert inches (mm)>.

9. Enclosure Depth: <Insert inches (mm)>.

10. Finish: Baked-enamel finish in manufacturer's [standard] [custom] color as selected by Architect.

11. Element Brackets: Primed and painted steel to support front panel and element.

2.3 ELECTRIC FINNED-TUBE RADIATION HEATERS

Copy this article and re-edit for each style of finned-tube radiation heater, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Berko; Marley Engineered Products.

2. Chromalox.

3. Indeeco.

4. Markel Products Company; TPI Corporation.

5. Marley Engineered Products.

6. Ouellet Canada Inc.

7. Qmark; Marley Engineered Products.

8. Trane Inc.

9. <Insert manufacturer's name>.

C. Description: Factory-packaged units constructed according to UL 499, UL 1030, and UL 2021.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Heating Elements: Nickel-chromium-wire heating element enclosed in metallic sheath mechanically bonded to fins, with high-temperature cutout and sensor running the full length of the element. Element supports shall eliminate thermal expansion noise.

Indicate length and total capacity on Drawings.

1. Volts: <Insert value>.

2. Phase: <Insert value>.

3. Hertz: <Insert value>.

4. Heat Output: <Insert W/ft. (W/m)>.

Retain "Front Panel" or "Rust-Resistant Front Panel" Paragraph below, or retain both and indicate location of each panel type on Drawings.

E. Front Panel: Minimum [0.0428-inch- (1.1-mm-)] [0.0528-inch- (1.35-mm-)] <Insert dimension> thick steel.

F. Rust-Resistant Front Panel: Minimum [0.052-inch- (1.3-mm-)] [0.064-inch- (1.6-mm-)] <Insert dimension> thick, ASTM A 653/A 653M, G60 (Z180) galvanized steel.

G. Wall-Mounted Back Panel: Minimum 0.0329-inch- (0.85-mm-) thick steel, full height, with full-length channel support for front panel without exposed fasteners.

H. Floor-Mounted Pedestals: Conceal conduit for power and control wiring at maximum 36-inch (914-mm) spacing. Pedestal-mounted back panel shall be solid panel matching front panel.

I. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.

J. Finish: Baked[-enamel][-epoxy] finish in manufacturer's [standard] [custom] color as selected by Architect.

K. Damper: Knob-operated internal damper at enclosure outlet.

L. Access Doors: Factory made, permanently hinged with tamper-resistant fastener, minimum size 6 by 7 inches (150 by 175 mm), integral with enclosure.

M. Enclosure Style: [Sloped] [Flat] top.

Retain features required for Project in subparagraphs below.

1. Front Inlet Grille: Punched louver; painted to match enclosure.

2. Front Inlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

3. [Top] [Front] Outlet Grille: Punched louver; painted to match enclosure.

4. [Top] [Front] Outlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

5. Enclosure Height: <Insert inches (mm)>.

6. Enclosure Depth: <Insert inches (mm)>.

Retain "Unit Controls" Paragraph below for integral control device; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

N. Unit Controls: Integral [line-voltage thermostat with minimum range of 60 to 90 deg F (15 to 32 deg C)] [low-voltage relay and control transformer for remote thermostat].

O. Accessories: Integral disconnect switch, filler sections, corners, relay sections, and splice plates all matching the enclosure and grille finishes.

2.4 HOT-WATER FINNED-TUBE RADIATION HEATERS

Copy this article and re-edit for each style of finned-tube radiation heater, or schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Embassy Industries, Inc.

2. Engineered Air.

3. Hydro-Air Components Inc.

4. Quincy Hydronic Technology Inc.

5. Rosemex.

6. Slant/Fin Corporation.

7. Sterling Hydronics; a Mestek company.

8. Trane Inc.

9. <Insert manufacturer's name>.

C. Performance Ratings: Rate finned-tube radiation heaters according to Hydronics Institute's "I=B=R Testing and Rating Standard for Finned-Tube (Commercial) Radiation."

Retain one of two "Heating Elements" paragraphs below.

D. Heating Elements: Copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins resting on element supports. One end of tube shall be belled.

If more than one configuration is required, delete eight subparagraphs below and schedule on Drawings.

1. Tube Diameter: [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] <Insert pipe size>.

2. Fin Size: [3 by 3 inches (76 by 76 mm)] [4 by 4 inches (102 by 102 mm)] <Insert dimensions>.

3. Fin Spacing: [40 per foot (131 per m)] [50 per foot (164 per m)] [58 per foot (190 per m)] <Insert value>.

4. Number of Tiers: <Insert number>.

5. Heat Output: <Insert Btu/h per ft. (W/m)>.

6. Entering-Air Temperature: [65 deg F (18 deg C)] <Insert temperature>.

7. Average Water Temperature: [180 deg F (82 deg C)] <Insert temperature>.

8. Minimum Water Velocity: [1/2 fps (0.15 m/s)] <Insert value>.

E. Heating Elements: Steel tubing mechanically expanded into flanged collars of evenly spaced steel fins resting on element supports. Tube ends shall be threaded.

If more than one configuration is required, delete eight subparagraphs below and schedule on Drawings.

1. Tube Diameter: [NPS 1-1/4 (DN 32)] <Insert pipe size>.

2. Fin Size: [4 by 4 inches (102 by 102 mm)] <Insert dimensions>.

3. Fin Spacing: [52 per foot (171 per m)] <Insert value>.

4. Number of Tiers: <Insert number>.

5. Heat Output: <Insert Btu/h per ft. (W/m)>.

6. Entering-Air Temperature: [65 deg F (18 deg C)] <Insert temperature>.

7. Average Water Temperature: [180 deg F (82 deg C)] <Insert temperature>.

8. Minimum Water Velocity: [1/2 fps (0.15 m/s)] <Insert value>.

F. Element Supports: Ball-bearing cradle type to permit longitudinal movement on enclosure brackets.

Retain "Front Panel" or "Rust-Resistant Front Panel" Paragraph below, or retain both and indicate location of each panel type on Drawings.

G. Front Panel: Minimum [0.0428-inch- (1.1-mm-)] [0.0528-inch- (1.35-mm-)] <Insert thickness> thick steel.

H. Rust-Resistant Front Panel: Minimum [0.052-inch- (1.3-mm-)] [0.064-inch- (1.6-mm-)] <Insert thickness> thick, ASTM A 653/A 653M, G60 (Z180) galvanized steel.

I. Wall-Mounted Back Panel: Minimum 0.0329-inch- (0.85-mm-) thick steel, full height, with full-length channel support for front panel without exposed fasteners.

J. Floor-Mounted Pedestals: Conceal insulated piping at maximum 36-inch (914-mm) spacing. Pedestal-mounted back panel shall be solid panel matching front panel. Provide stainless-steel escutcheon for floor openings at pedestals.

K. Support Brackets: Locate at maximum 36-inch (914-mm) spacing to support front panel and element.

L. Finish: Baked[-enamel][-epoxy] finish in manufacturer's [standard] [custom] color as selected by Architect.

M. Damper: Knob-operated internal damper at enclosure outlet.

N. Access Doors: Factory made, permanently hinged with tamper-resistant fastener, minimum size 6 by 7 inches (150 by 175 mm), integral with enclosure.

O. Enclosure Style: [Sloped] [Flat] top.

Retain features required for Project in subparagraphs below.

1. Front Inlet Grille: Punched louver; painted to match enclosure.

2. Front Inlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

3. [Top] [Front] Outlet Grille: Punched louver; painted to match enclosure.

4. [Top] [Front] Outlet Grille: Extruded-aluminum linear bar grille; pencil-proof bar spacing.

a. Mill-finish aluminum.

b. Anodized finish, color as selected by Architect from manufacturer's [standard] [custom] colors.

c. Painted to match enclosure.

5. Enclosure Height: <Insert inches (mm)>.

6. Enclosure Depth: <Insert inches (mm)>.

P. Accessories: Filler sections, corners, relay sections, and splice plates all matching the enclosure and grille finishes.

PART 3 -  EXECUTION

3.1 BASEBOARD RADIATION HEATER INSTALLATION

A. Install units level and plumb.

B. Install enclosure continuously around corners, using outside and inside corner fittings.

C. Join sections with splice plates and filler pieces to provide continuous enclosure.

D. Install access doors for access to valves.

E. Install enclosure continuously from wall to wall.

F. Terminate enclosures with manufacturer's end caps except where enclosures are indicated to extend to adjoining walls.

Retain three paragraphs below for hot-water units.

G. Install valves within reach of access door provided in enclosure.

H. Install air-seal gasket between wall and recessed flanges or front cover of fully recessed unit.

I. Install piping within pedestals for freestanding units.

3.2 FINNED-TUBE RADIATION HEATER INSTALLATION

A. Install units level and plumb.

B. Install enclosure continuously around corners, using outside and inside corner fittings.

C. Join sections with splice plates and filler pieces to provide continuous enclosure.

D. Install access doors for access to valves.

E. Install enclosure continuously from wall to wall.

F. Terminate enclosures with manufacturer's end caps except where enclosures are indicated to extend to adjoining walls.

Retain three paragraphs below for hot-water units.

G. Install valves within reach of access door provided in enclosure.

H. Install air-seal gasket between wall and recessed flanges or front cover of fully recessed unit.

I. Install piping within pedestals for freestanding units.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain first four paragraphs below for hot-water piping.

A. Piping installation requirements are specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect hot-water finned-tube radiation heaters and components to piping according to Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

1. Install shutoff valves on inlet and outlet, and balancing valve on outlet.

C. Install control valves as required by Section 230900 "Instrumentation and Control for HVAC."

D. Install piping adjacent to finned-tube radiation heaters to allow service and maintenance.

Retain two paragraphs below for electric finned-tube radiation heaters.

E. Ground electric finned-tube radiation heaters according to Section 260526 "Grounding and Bonding for Electrical Systems."

F. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections:

Retain "Leak Test" Subparagraph below for hot-water finned-tube radiation heaters.

1. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Retain "Operational Test" Subparagraph below for electric finned-tube radiation heaters.

2. Operational Test: After electrical circuitry has been energized, start units to confirm proper operation.

3. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Units will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 238236

	FINNED-TUBE RADIATION HEATERS
	238236 - 1



