Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238239.13 - CABINET UNIT HEATERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

This Section includes requirements for the LEED Rating System. However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits. Verify, with manufacturers, that the requirements for prerequisites and credits can be met. To achieve prerequisites and obtain credits, HVAC system designs that do not include cabinet unit heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes cabinet unit heaters with centrifugal fans and hot-water coils.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings:

1. Include plans, elevations, sections, and details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include location and size of each field connection.

4. Include details of anchorages and attachments to structure and to supported equipment.

5. Include equipment schedules to indicate rated capacities, operating characteristics, furnished specialties, and accessories.

6. Indicate location and arrangement of piping valves and specialties.

Retain first subparagraph below for cabinet unit heaters with integral controls; delete if control devices are specified in Section 230900 "Instrumentation and Control for HVAC."

7. Indicate location and arrangement of integral controls.

8. Wiring Diagrams: Power, signal, and control wiring.

D. Samples: For each exposed product and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Suspended ceiling components.

2. Structural members to which cabinet unit heaters will be attached.

3. Method of attaching hangers to building structure.

4. Size and location of initial access modules for acoustical tile.

5. Items penetrating finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. <Insert item>.

6. Perimeter moldings for exposed or partially exposed cabinets.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: Submit certification that cabinet unit heaters, accessories, and components will withstand seismic forces defined in Section 230548 "Vibration and Seismic Controls for HVAC."

C. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Airtherm; a Mestek company.
2. Berko; Marley Engineered Products.

3. Carrier Corporation; a UTC company.

4. Chromalox, Inc.

5. Dunham-Bush, Inc.

6. Engineered Air.

7. Indeeco.

8. International Environmental Corporation.

9. Markel Products Company; TPI Corporation.

10. Marley Engineered Products.

11. McQuay International.

12. Ouellet Canada Inc.

13. QMark; Marley Engineered Products.

14. Rosemex Products.

15. Trane Inc.

16. USA Coil & Air.

17. <Insert manufacturer's name>.

2.2 DESCRIPTION

A. Factory-assembled and -tested unit complying with AHRI 440.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.3 PERFORMANCE REQUIREMENTS

"ASHRAE Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

A. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

"ASHRAE/IESNA 90.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA 90.1 Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

C. Seismic Performance: Cabinet unit heaters shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2.4 COIL SECTION INSULATION

Flexible elastomeric insulation and mineral-fiber insulation with a foil face are available from some manufacturers to reduce the number of glass or mineral fibers circulating through the air-conditioned space.

Retain first "Insulation Materials" Paragraph below for duct-liner-type, glass-fiber insulation.

A. Insulation Materials: ASTM C 1071; surfaces exposed to airstream shall have [aluminum-foil facing] [erosion-resistant coating] to prevent erosion of glass fibers.

1. Thickness: [1/2 inch (13 mm)] [1 inch (25 mm)] [1-1/2 inches (38 mm)].

2. Thermal Conductivity (k-Value): 0.26 Btu x in./h x sq. ft. at 75 deg F (0.037 W/m x K at 24 deg C) mean temperature.

3. Fire-Hazard Classification: Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84.

4. Adhesive: Comply with ASTM C 916 and with NFPA 90A or NFPA 90B.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

5. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain "Insulation Materials" Paragraph below for flexible elastomeric insulation.

B. Insulation Materials: Comply with NFPA 90A or NFPA 90B. Unicellular polyethylene thermal plastic, preformed sheet insulation complying with ASTM C 534, Type II, except for density.

1. Thickness: [3/8 inch (9 mm)] [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)].

2. Thermal Conductivity (k-Value): 0.24 Btu x in./h x sq. ft. at 75 deg F (0.034 W/m x K at 24 deg C) mean temperature.

3. Fire-Hazard Classification: Maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM C 411.

4. Adhesive: As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

5. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

2.5 CABINETS

Retain "Material" Paragraph below for surface, semirecessed, and fully recessed units. Cabinet is not required for concealed units. Coordinate custom color requirements in paragraph below with Sample submittal requirements. Coordinate field painting with painting Sections.

A. Material: Steel with [factory prime coating, ready for field painting] [baked-enamel finish with manufacturer's standard paint, in color selected by Architect] [baked-enamel finish with manufacturer's custom paint, in color selected by Architect].

First option in "Vertical Unit, Exposed Front Panels" and "Horizontal Unit, Exposed Bottom Panels" subparagraphs below is the equivalent of 16-gage steel; second option is the equivalent of 14-gage steel.

1. Vertical Unit, Exposed Front Panels: Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] thick [galvanized ]sheet steel, removable panels with channel-formed edges secured with tamperproof cam fasteners.

2. Horizontal Unit, Exposed Bottom Panels: Minimum [0.0528-inch- (1.35-mm-)] [0.0677-inch- (1.7-mm-)] thick [galvanized ]sheet steel, removable panels secured with tamperproof cam fasteners and safety chain.

Retain "Recessed Flanges" Subparagraph below for units that are semirecessed or fully recessed in walls or ceilings.

3. Recessed Flanges: Steel, finished to match cabinet.

4. Control Access Door: Key operated.

Retain "Base" Subparagraph below for surface, vertical, wall-mounted units.

5. Base: Minimum 0.0528-inch- (1.35-mm-) thick steel, finished to match cabinet, [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension> high with leveling bolts.

6. Extended Piping Compartment: [8-inch- (200-mm-)] <Insert dimension> wide piping end pocket.

Accessories described in "False Back" and "Outdoor-Air Wall Box" subparagraphs below are furnished for vertical, wall-mounted units only.

7. False Back: Minimum 0.0428-inch- (1.1-mm-) thick steel, finished to match cabinet.

8. Outdoor-Air Wall Box: Minimum 0.1265-inch- (3.2-mm-) thick, aluminum, rain-resistant louver and box with integral eliminators and bird screen; aluminum louver with [anodized] [baked-enamel] finish in color selected by Architect from manufacturer's [standard] [custom] colors.

Retain second or third option in "Outdoor-Air Damper" Subparagraph below if applying for LEED certification. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, and Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

a. Outdoor-Air Damper: Galvanized-steel blades with edge and end seals and nylon bearings; with [manual] [electronic] [pneumatic], two-position actuators.

2.6 FILTERS

Verify available filter types with manufacturer. Indicate filter thickness in "Capacities and Characteristics" Article or in the Cabinet Unit-Heater Schedule on Drawings.

A. Minimum Arrestance: According to ASHRAE 52.1 and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or more of three subparagraphs below. If retaining more than one filter type, indicate type for each unit in the Cabinet Unit-Heater Schedule on Drawings.

1. Washable Foam: 70 percent arrestance and MERV 3.

2. Glass Fiber Treated with Adhesive: 80 percent arrestance and MERV 5.

3. Pleated: 90 percent arrestance and MERV 7.

2.7 COILS

A. Hot-Water Coil: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm) and rated for a minimum working pressure of 200 psig (1378 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Include manual air vent and drain.

2.8 CONTROLS

A. Fan and Motor Board: Removable.

1. Fan: Forward curved, [high static, ]double width, centrifugal, directly connected to motor; thermoplastic or painted-steel wheels and aluminum, painted-steel, or galvanized-steel fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

2. Motor: Permanently lubricated, multispeed; resiliently mounted on motor board. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

3. Wiring Terminations: Connect motor to chassis wiring with plug connection.

Retain "Factory, Hot-Water Piping Package" Paragraph below to require factory-piping package.

B. Factory, Hot-Water Piping Package: [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper tube with wrought-copper fittings and brazed joints. Label piping to indicate service, inlet, and outlet.

Retain one or more of first four subparagraphs below.

1. [Two] [Three]-way, [two-position] [modulating] control valve.[ Three-way valve packages shall include bypass line with manually adjustable balance device.]

2. Hose Kits: Minimum 400-psig (2758-kPa) working pressure, and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C). Tag hose kits to equipment designations.

a. Length: [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension>.

b. Minimum Diameter: Equal to cabinet unit-heater connection size.

3. Two-Piece, Ball Valves: Bronze body with full-port, chrome-plated bronze ball; PTFE or TFE seats; and 600-psig (4140-kPa) minimum CWP rating and blowout-proof stem.

4. Calibrated-Orifice Balancing Valves: Bronze body, ball type, 125-psig (860-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature; with calibrated orifice or venture, connection for portable differential pressure meter with integral seals, threaded ends, and equipped with a memory stop to retain set position.

5. Automatic Flow-Control Valve: Brass or ferrous-metal body, 300-psig (2068-kPa) working pressure at 250 deg F (121 deg C), with removable, corrosion-resistant, tamperproof, self-cleaning piston spring; factory set to maintain constant indicated flow within plus or minus 10 percent of differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

6. Y-Pattern, Hot-Water Strainers: Cast-iron body (ASTM A 126, Class B); 125-psig (860-kPa) minimum working pressure; with threaded connections, bolted cover, perforated stainless-steel basket, and bottom drain connection. Include minimum NPS 1/2 (DN 15) threaded pipe and full-port ball valve in strainer drain connection.

7. Wrought-Copper Unions: ASME B16.22.

Retain first paragraph below and delete "Basic Unit Controls" Paragraph below if controls are part of overall temperature-control system.

C. Control devices and operational sequences are specified in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence of Operations for HVAC Controls."

D. Basic Unit Controls:

1. Control voltage transformer.

Verify control features with manufacturer.

2. [Wall] [Unit]-mounted thermostat with the following features:

a. Heat-off switch.

b. Fan on-auto switch.

Retain first subparagraph below if multispeed motors are specified.

c. Manual fan-speed switch.

d. Adjustable deadband.

e. [Concealed] [Exposed] set point.

f. [Concealed] [Exposed] indication.

g. Deg F (Deg C) indication.

3. [Wall] [Unit]-mounted temperature sensor.

4. Unoccupied period override push button.

5. Data entry and access port.

a. Input data includes room temperature and occupied and unoccupied periods.

b. Output data includes room temperature, supply-air temperature, entering-water temperature, operating mode, and status.

Retain "(DDC )Terminal Controller" Paragraph below and coordinate with "Basic Unit Controls" Paragraph above or with control devices specified in Section 230900 "Instrumentation and Control for HVAC."

E. [DDC ]Terminal Controller:

1. Scheduled Operation: Occupied and unoccupied periods on seven-day clock with a minimum of four programmable periods per day.

2. Unoccupied Period Override: [Two] <Insert number> hours.

3. Unit Supply-Air Fan Operations:

a. Occupied Periods: Fan runs continuously.

b. Unoccupied Periods: Fan cycles to maintain setback room temperature.

4. Heating-Coil Operations:

a. Occupied Periods: [Open] [Modulate] control valve to provide heating if room temperature falls below thermostat set point.

b. Unoccupied Periods: Start fan and [open] [modulate] control valve if room temperature falls below setback temperature.

Retain "Outdoor-Air Damper Operation" Subparagraph below for automatic outdoor-air intake damper.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, and Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

5. Outdoor-Air Damper Operation:

a. Occupied Periods: Open dampers. Delay damper opening if room temperature is more than three degrees below set point.

b. Unoccupied Periods: Close damper.

6. Controller shall have volatile-memory backup.

F. BAS Interface Requirements:

1. Interface relay for scheduled operation.

2. Interface relay to provide indication of fault at central workstation.

3. Interface shall be [BAC-net] [or] [LonWorks] compatible for central BAS workstation and include the following functions:

a. Adjust set points.

b. Cabinet unit-heater start, stop, and operating status.

c. Data inquiry, including [outdoor-air damper position and ]supply-air and room-air temperature.

d. Occupied and unoccupied schedules.

G. Electrical Connection: Factory-wired motors and controls for a single field connection.

2.9 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of cabinet unit heater, delete this article and schedule cabinet unit heaters on Drawings.

A. Cabinet:

1. Vertical, Surface Mounted: Upflow.

a. Top: [Flat] [Sloped] [Flat or sloped].

b. Air Inlet: [Open bottom] [Front, punched louver] [Front, extruded-aluminum bar grille].

c. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

2. Vertical, Surface Mounted: Downflow.

a. Top: [Flat] [Sloped] [Flat or sloped].

b. Air Inlet: [Front] [Top] [Front or top], [punched louver] [extruded-aluminum bar grille].

c. Air Outlet: Front, [quad louver] [punched louver] [extruded-aluminum bar grille].

3. Vertical, Semirecessed: Upflow.

a. Air Inlet: [Open bottom] [Front, punched louver] [Front, extruded-aluminum bar grille].

b. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

4. Vertical, Semirecessed: Downflow.

a. Air Inlet: [Front] [Top] [Front or top], [punched louver] [extruded-aluminum bar grille].

b. Air Outlet: Front, [quad louver] [punched louver] [extruded-aluminum bar grille].

5. Vertical, Fully Recessed: [Upflow] [Downflow].

a. Air Inlet: [Front] [Duct connection], [punched louver] [extruded-aluminum bar grille].

b. Air Outlet: [Front] [Duct connection], [quad louver] [punched louver] [extruded-aluminum bar grille].

6. Horizontal, Surface Mounted:

a. Air Inlet: [Bottom] [Front] [Bottom or front], [punched louver] [extruded-aluminum bar grille].

b. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

7. Horizontal, Semirecessed:

a. Air Inlet: [Bottom] [Front] [Bottom or front], [punched louver] [extruded-aluminum bar grille].

b. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

8. Horizontal, Fully Recessed:

a. Air Inlet: [Front] [Duct connection], [punched louver] [extruded-aluminum bar grille].

b. Air Outlet: [Front] [Duct connection], [quad louver] [punched louver] [extruded-aluminum bar grille].

B. Concealed Unit Heater:

1. Vertical: [Upflow] [Downflow].

a. Air Inlet: [Open bottom] [Front, punched louver] [Front, extruded-aluminum bar grille].

b. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

2. Horizontal: Upflow.

a. Air Inlet: [Open bottom] [Front, punched louver] [Front, extruded-aluminum bar grille].

b. Air Outlet: [Front] [Top] [Front or top], [quad louver] [punched louver] [extruded-aluminum bar grille].

C. Fan:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Fan Speed: <Insert rpm>.

4. Motor Horsepower: <Insert value>.

D. Heating Capacity:

1. Output: <Insert Btu/h (kW)>.

2. Entering-Air Temperature: <Insert deg F (deg C)>.

3. Air-Temperature Rise: <Insert deg F (deg C)>.

E. Hot-Water Heating Coil:

1. Water Flow: <Insert gpm (L/s)>.

2. Water-Side Pressure Loss: <Insert feet wg (kPa)>.

3. Entering-Water Temperature: <Insert deg F (deg C)>.

F. Filters:

1. Face Area: <Insert sq. ft. (sq. m)>.

2. Thickness: [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert dimension>.

G. Electrical Characteristics for Single-Point Connection:

1. Volts: <Insert value>.

2. Phase: <Insert value>.

3. Hertz: <Insert value>.

4. Full-Load Amperes: <Insert value>.

5. Minimum Circuit Ampacity: <Insert value>.

6. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas to receive cabinet unit heaters for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

B. Examine roughing-in for [piping and ]electrical connections to verify actual locations before unit-heater installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain first paragraph below for vertical, wall-mounted cabinet unit heaters with wall boxes and outdoor-air intake louvers.

A. Install wall boxes in finished wall assembly; seal and weatherproof. Joint-sealant materials and applications are specified in Section 079200 "Joint Sealants."

B. Install cabinet unit heaters to comply with NFPA 90A.

C. Suspend cabinet unit heaters from structure with elastomeric hangers. Vibration isolators are specified in [Section 230548 "Vibration and Seismic Controls for HVAC."] [Section 230548.13 "Vibration Controls for HVAC."]

Retain first paragraph below if controls are provided by unit-heater manufacturer. To comply with requirements of the Americans with Disabilities Act, verify mounting height with authorities having jurisdiction.

D. Install wall-mounted thermostats and switch controls in electrical outlet boxes at heights to match lighting controls. Verify location of thermostats and other exposed control sensors with Drawings and room details before installation.

E. Install new filters in each fan-coil unit within two weeks of Substantial Completion.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Section 232113 "Hydronic Piping," Section 232116 Hydronic Piping Specialties," Section 232213 "Steam and Condensate Heating Piping," and Section 232216 Steam and Condensate Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Connect piping to cabinet unit heater's factory, hot-water piping package. Install the piping package if shipped loose.

Retain first paragraph below for concealed cabinet unit heaters. Coordinate duct installation requirements with Drawings and with requirements specified in Section 233113 "Metal Ducts," Section 233116 "Nonmetal Ducts," and Section 233300 "Air Duct Accessories."

D. Connect supply and return ducts to cabinet unit heaters with flexible duct connectors specified in Section 233300 "Air Duct Accessories."

E. Comply with safety requirements in UL 1995.

Retain first paragraph below for cabinet unit heaters if factory piping package is not required.

F. Unless otherwise indicated, install union and gate or ball valve on supply-water connection and union and calibrated balancing valve on return-water connection of cabinet unit heater. Hydronic specialties are specified in Section 232113 "Hydronic Piping" and Section 232116 Hydronic Piping Specialties."

G. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

H. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

2. Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Units will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 238239.13

	CABINET UNIT HEATERS
	238239.13 - 1



