Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238313 - RADIANT-HEATING ELECTRIC CABLES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes electric heating cables for ceiling or floor radiant heating, snow and ice melting on pavement, and freezer-floor frost-heave prevention with the following electric heating cables:

1. Plastic insulated, series resistance.

2. Self-regulating, parallel resistance.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 210533 "Heat Tracing for Fire-Suppression Piping."

2. Section 220533 "Heat Tracing for Plumbing Piping."

3. Section 230533 "Heat Tracing for HVAC Piping."

4. Section 238213 "Valance Heating and Cooling Units" for factory-fabricated electric heating panels for ceiling and wall applications.

5. Section 238323 "Radiant-Heating Electric Panels."

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For electric heating cable. Include plans, sections, details, and attachments to other work.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Reflected ceiling plans, drawn to scale, and coordinated with each other, using input from installers of the items involved.

B. Field quality-control reports.

C. Sample Warranty: For special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for electric heating cable.

1. Warranty Period: [10] [15] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 GENERAL REQUIREMENTS FOR ELECTRIC HEATING CABLES

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.2 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this article for ceiling and floor radiant heating, freezer-floor frost-heave prevention, and snow and ice melting on pavement. Some manufacturers limit use of this product to stone, ceramic tile, or concrete floors.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Delta-Therm Corporation.

2. Easy Heat; a division of EGS Electrical Group LLC.

3. Nuheat Industries Ltd.

4. Orbit Manufacturing.

5. Pyrotenax; a brand of Tyco Thermal Controls LLC.

6. Raychem; a brand of Tyco Thermal Controls LLC.

7. WarmlyYours Inc.

8. Watts Radiant, Inc.; a subsidiary of Watts Water Technologies, Inc.

9. <Insert manufacturer's name>.

C. Comply with UL 1673.

D. Heating Element: Single resistor wire. Terminate with waterproof, factory-assembled, nonheating leads with connectors at both ends.

E. Electrical Insulating Jacket: Minimum 4.0-mil (0.10-mm) Kapton with silicone or Tefzel.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: [Aluminum] [Stainless-steel] [Nickel] braid[ with silicone or Hylar outer jacket].

G. Maximum Operating Temperature: [300 deg F (150 deg C)] <Insert temperature>.

Retain "Cable-Heated Mats" Paragraph below for heating cables in factory-fabricated mats. Indicate length and spacing of cables on Drawings.

H. Cable-Heated Mats: Factory-fabricated cable and fiberglass or plastic mesh with uniform [1-1/2-inch (38-mm)] [3-inch (76-mm)] <Insert dimension> cable spacing, in [18-inch (457-mm)] [36-inch (914-mm)] <Insert dimension> widths.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for sample schedule.

I. Capacities and Characteristics:

Retain "Maximum Heat Output (Cable)" Subparagraph below for loose-laid heating cables.

1. Maximum Heat Output (Cable): [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert value>.

Retain "Maximum Heat Output (Mat)" Subparagraph below for heating cables in factory-fabricated mats. Heat output depends on spacing of the heating cables within the mat. Verify output capacities with manufacturer.

2. Maximum Heat Output (Mat): [12 W/sq. ft. (129 W/sq. m)] [16 W/sq. ft. (172 W/sq. m)] <Insert value>.

Retain "Spacing" Subparagraph below for cable-heated mats.

3. Spacing: <Insert inches (mm)>.

4. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages, phase, and heat-output ratings with manufacturer. Most manufacturers supply this product in single phase only.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain this article for ceiling and floor radiant heating, freezer-floor frost-heave prevention, and snow and ice melting on pavement.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. BriskHeat.

2. Chromalox.

3. Delta-Therm Corporation.

4. Easy Heat; a division of EGS Electrical Group LLC.

5. Nelson Heat Trace; a division of EGS Electrical Group LLC.

6. Pyrotenax; a brand of Tyco Thermal Controls LLC.

7. Raychem; a brand of Tyco Thermal Controls LLC.

8. Thermon Americas Inc.

9. Trasor Corp.

10. <Insert manufacturer's name>.

C. Comply with UL 1673.

D. Heating Element: Pair of parallel [No. 16] [No. 18] AWG, [tinned] [nickel-coated], stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length. Terminate with waterproof, factory-assembled, nonheating leads with connectors at one end, and seal the opposite end watertight. Cable shall be capable of crossing over itself once without overheating.

E. Electrical Insulating Jacket: Flame-retardant polyolefin.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: [Tinned-copper] [Stainless-steel] braid[ with polyolefin outer jacket with ultraviolet inhibitor].

G. Maximum Operating Temperature: [300 deg F (150 deg C)] <Insert temperature>.

Retain "Cable-Heated Mats" Paragraph below for heating cables in factory-fabricated mats. Indicate length and spacing of cables on Drawings.

H. Cable-Heated Mats: Factory-fabricated cable and fiberglass or plastic mesh with uniform [1-1/2-inch (38-mm)] [3-inch (76-mm)] <Insert dimension> cable spacing, in [18-inch (457-mm)] [36-inch (914-mm)] <Insert dimension> widths.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for sample schedule.

I. Capacities and Characteristics:

Retain "Maximum Heat Output (Cable)" Subparagraph below for loose-laid heating cables.

1. Maximum Heat Output (Cable): [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert value>.

Retain "Maximum Heat Output (Mat)" Subparagraph below for heating cables in factory-fabricated mats. Heat output depends on spacing of the heating cables within the mat. Verify output capacities with manufacturer.

2. Maximum Heat Output (Mat): [6 W/sq. ft. (65 W/sq. m)] [12 W/sq. ft. (129 W/sq. m)] [16 W/sq. ft. (172 W/sq. m)] [24 W/sq. ft. (260 W/sq. m)] <Insert value>.

Retain "Spacing" Subparagraph below for cable-heated mats.

3. Spacing: <Insert inches (mm)>.

4. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages, phase, and heat-output ratings with manufacturer. Most manufacturers supply this product in single phase only.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.4 CONTROLS

Retain first paragraph below and delete remainder of this article to specify temperature controls in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence of Operations for HVAC Controls." Delete first paragraph and retain remaining paragraphs to require controls integral to the radiant-heating electric cables to be provided by cable manufacturer.

A. Comply with requirements in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence of Operations for HVAC Controls" for control devices and sequence of operations for radiant-heating electric cables.

Retain "Wall-Mounted Thermostats for Ceiling and Floor Heating Cables" Paragraph below for room-temperature control of electric cables in ceilings and floors.

B. Wall-Mounted Thermostats for Ceiling and Floor Heating Cables:

1. Minimum temperature range from [50 to 90 deg F (10 to 32 deg C)] <Insert temperature range>.

2. Manually operated with on-off switch.

Retain "Precipitation and Temperature Sensor for Snow Melting on Pavement" Paragraph below to operate electric heating cable for snow melting on pavement.

C. Precipitation and Temperature Sensor for Snow Melting on Pavement:

1. [Microprocessor-based] [Automatic] control with manual on, automatic, and standby/reset switch.

2. Precipitation and temperature sensors shall sense the surface conditions of pavement and shall be programmed to energize the cable as follows:

Retain and revise features in "Temperature Span," "Adjustable Delay-Off Span," "Energize Cables," and "De-Energize Cables" subparagraphs below to suit Project. Verify available features with manufacturer.

a. Temperature Span: [34 to 44 deg F (1 to 7 deg C)] <Insert temperature range>.

b. Adjustable Delay-Off Span: [30 to 90] <Insert time> minutes.

c. Energize Cables: Following [two] <Insert time>-minute delay if ambient temperature is below set point and precipitation is detected.

d. De-Energize Cables: On detection of a dry surface plus time delay.

3. Corrosion-proof and waterproof enclosure suitable for outdoor mounting, for controls and precipitation and temperature sensors.

4. Minimum 30-A contactor to energize cable or close other contactors.

5. Provide relay with contacts to indicate operational status, on or off, for interface with central HVAC control-system workstation.

2.5 ACCESSORIES

A. Cable Installation Accessories: Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

B. Embedded Heating-Cable Identification:

Retain one of three subparagraphs below.

1. Flush-mounted cast-iron boxes with identification on lid according to NFPA 70.

2. Mechanically fastened [metal] [plastic] signage with identification according to NFPA 70 and complying with requirements in [Section 101416"Plaques."] [Section 101419 "Dimensional Letter Signage."] [Section 101423 "Panel Signage."]

3. Mechanically fastened [metal] [plastic] [concrete] post-mounted signage with identification according to NFPA 70 and complying with requirements in [Section 101416 "Plaques."] [Section 101419 "Dimensional Letter Signage."] [Section 101423 "Panel Signage."]

PART 3 -  EXECUTION

3.1 APPLICATIONS

Applications in this article are typical uses for each type of electric heating cable. Consult manufacturers for other applications.

A. Install the following types of electric heating cable for the applications described:

1. Ceiling Radiant Heating: [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

2. Floor Radiant Heating: [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

3. Snow and Ice Melting on Pavement: [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

4. Freezer-Floor Frost-Heave Prevention: [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

3.2 INSTALLATION

Indicate location of controls on Drawings.

A. Install electric heating cable or cable-heated mats across expansion, construction, and control joints according to manufacturer's written instructions; use cable-protection conduit and slack cable to allow movement without damage to cable.

B. Do not energize cables embedded in concrete or plaster until those assemblies are cured.

Coordinate "Electric Heating-Cable Installation for Ceiling Radiant Heating" Paragraph below with Drawings. Indicate details of how cable-heating array is installed in ceiling.

C. Electric Heating-Cable Installation for Ceiling Radiant Heating: Install heating cable or cable-heated mat with heat-conductive fill materials such as plaster to ensure direct contact with finished radiant surfaces.

Coordinate "Electric Heating-Cable Installation for Floor Radiant Heating" Paragraph below with Drawings. Indicate details of how cable-heating array is installed in floor.

D. Electric Heating-Cable Installation for Floor Radiant Heating: Install heating cable or cable-heated mat with heat-conductive fill materials such as concrete to ensure direct contact with finished radiant surfaces.

E. Electric Heating-Cable or Cable-Heated-Mat Installation for Snow and Ice Melting in Pavement:

1. Install heating cable or cable-heated mat with heat-conductive fill materials such as asphalt or concrete to ensure direct contact with finished radiant surfaces.

Retain first subparagraph below for asphalt paving.

2. Install cables or cable-heated mats after applying bituminous binder course to lower base; ensure that second bituminous binder course is applied to cables or mats before pouring finish topping.

Retain first subparagraph below to require a flush-mounted box to identify embedded heating array. Coordinate with paving Sections.

3. Install embedded electric heating-cable or cable-heated-mat identification box where indicated in pavement before pavement work is completed.

Retain first subparagraph below for cast-in-place concrete paving and to require embedded heating array to be identified by stamping.

4. Stamp concrete with embedded electric heating-cable or cable-heated-mat identification according to NFPA 70 and complying with requirements in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Consider pavement-mounted sensor for snow melting on pavement.

5. Mount precipitation sensor in pavement.

F. Electric Heating-Cable Installation for Freezer-Floor Frost-Heave Prevention: Install electric heating cable or cable-heated mat below insulation in subsoil.

Retain first subparagraph below to require a flush-mounted box to identify embedded heating array. Coordinate with finished floor work.

1. Install embedded electric heating-cable or cable-heated-mat identification box where indicated.

embedded electric heating-cable or cable-heated-mat identification

2. Install embedded electric heating-cable or cable-heated-mat identification according to NFPA 70 on adjacent structure and complying with requirements in [Section 101416 "Plaques."] [Section 101419 "Dimensional Letter Signage."] [Section 101423 "Panel Signage."]

3. Install embedded electric heating-cable or cable-heated-mat identification according to NFPA 70 on [metal] [wood] [concrete] post and complying with requirements in [Section 101416 "Plaques."] [Section 101419 "Dimensional Letter Signage."] [Section 101423 "Panel Signage."]

Retain subparagraph below to require embedded heating array to be identified by stamping.

4. Stamp concrete with embedded electric heating-cable or cable-heated-mat identification according to NFPA 70 and complying with requirements in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

G. Set field-adjustable switches and circuit-breaker trip ranges.

H. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

2. Test cables for electrical continuity and insulation integrity before energizing.

3. Test cables to verify rating and power input. Energize and measure voltage and current simultaneously.

B. Repeat tests for continuity, insulation resistance, and input power after applying finished surface on heating cables.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Radiant-heating electric cables will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

E. Remove and replace damaged radiant-heating electric cables and cable-heated mats.

END OF SECTION 238313

	RADIANT-HEATING ELECTRIC CABLES
	238313 - 1



