Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238323 - RADIANT-HEATING ELECTRIC PANELS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes prefabricated radiant-heating electric panels.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 238213 "Valance Heating and Cooling Units" for factory-fabricated electric heating panels for ceiling and wall applications.

2. Section 238313 "Radiant-Heating Electric Cables."

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For electric heating panels. Include plans, sections, details, and attachments to other work.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Reflected ceiling plans, drawn to scale, and coordinated with each other, using input from installers of the items involved.

B. Field quality-control reports.

C. Sample Warranty: For special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer agrees to repair or replace electric heating panels that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for radiant-heating electric panels.

1. Warranty Period: [Three] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 GENERAL REQUIREMENTS FOR RADIANT-HEATING ELECTRIC PANELS

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.2 PREFABRICATED RADIANT-HEATING ELECTRIC PANELS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Berko; c/o Marley Engineered Products.

2. QMark; c/o Marley Engineered Products.

3. SSHC, Inc.

4. <Insert manufacturer's name>.

C. Description: Sheet-metal-enclosed panel with heating element suitable for [lay-in installation flush with T-bar ceiling grid] [surface mounting] [recessed mounting]. Comply with UL 2021.

1. Panel: Minimum 0.0276-inch- (0.7-mm-) thick, galvanized sheet steel back panel riveted to minimum 0.0396-inch- (1.0-mm-) thick, galvanized sheet steel front panel with fused-on crystalline surface.

Retain one of two "Heating Element" subparagraphs below.

2. Heating Element: Powdered graphite sandwiched between sheets of electric insulation.

3. Heating Element: Insulated resistive wires.

4. Electrical Connections: Nonheating, high-temperature, insulated-copper leads, factory connected to heating element.

Retain one of three "Exposed-Side Panel Finish" subparagraphs or "Surface-Mounted Trim" Subparagraph below. If more than one type of finish is required, indicate each type in a schedule on Drawings.

5. Exposed-Side Panel Finish: Apply silk-screened finish to match appearance of Architect-selected acoustical ceiling tiles.

6. Exposed-Side Panel Finish: Factory prime coated, ready for field painting.

7. Exposed-Side Panel Finish: Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain "Surface-Mounted Trim" Subparagraph below for surface-mounted panels.

8. Surface-Mounted Trim: Sheet metal with baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

D. Wall Thermostat: Bimetal, sensing elements calibrated from 55 to 90 deg F (13 to 32 deg C); with contacts suitable for [low] [line]-voltage circuit, and manually operated on-off switch with contactors, relays, and control transformers.

If Project has more than one type or configuration of prefabricated radiant-heating electric panel, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for sample schedule.

E. Capacities and Characteristics:

1. Nominal Panel Size: [24 by 24 inches (600 by 600 mm)] [24 by 36 inches (600 by 900 mm)] [24 by 48 inches (600 by 1200 mm)] [24 by 60 inches (600 by 1500 mm)] <Insert custom size>.

2. Heating Capacity: [250] [375] [500] [570] [625] [750] [950] <Insert value> W.

3. Electrical Characteristics for Single-Point Connection:

a. Volts: <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 INSTALLATION

Indicate location of controls on Drawings.

A. Install radiant-heating panels level and plumb.

B. Support for Radiant-Heating Panels in or on Grid-Type Suspended Ceilings: Use grid as a support element.

1. Install a minimum of four ceiling-support-system rods or wires for each panel. Locate not more than 6 inches (150 mm) from panel corners.

2. Support Clips: Fasten to panel and to ceiling grid members at or near each panel corner with clips designed for the application.

3. Panels of Sizes Less Than Ceiling Grid: Install as indicated on reflected ceiling plans or center in acoustical panel, and support panels independently with at least two 3/4-inch (19-mm) metal channels spanning and secured to ceiling tees.

Retain subparagraph below if Project is in a seismic area.

4. Install at least one independent support rod or wire from structure to a tab on panel. Wire or rod shall have breaking strength of the weight of the panel at a safety factor of 3.

To comply with requirements of the Americans with Disabilities Act, verify mounting height in first paragraph below with authorities having jurisdiction.

C. Verify locations of thermostats with Drawings and room details before installation. Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

D. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

E. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.2 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Operate electric-heating elements through each stage to verify proper operation and electrical connections.

2. Test and adjust controls and safeties.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Radiant-heating electric panels will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

D. Remove and replace damaged radiant-heating electric panels.

END OF SECTION 238323

	RADIANT-HEATING ELECTRIC PANELS
	238323 - 1



