Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260923 - LIGHTING CONTROL DEVICES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. ASHRAE/IESNA 90.1, Section 9, "Lighting," sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.

Local switches, occupancy sensors, and daylight-harvesting controls can be used to comply with the requirements of LEED-NC, LEED-CI, and LEED for Schools Credit EQ 6.1. However, use of task lighting may also be required, depending on the type of lighting system used on Project.

Occupancy sensors and daylight-harvesting controls can be combined with other energy-conserving measures to comply with the requirements of LEED-NC, LEED-CS, and LEED for Schools Credit EA 1 or with LEED-CI Credit EA 1.2.

Time switches and occupancy sensors can be combined to comply with the requirements of LEED-NC, LEED-CS, and LEED for Schools Credit SS 8 or with LEED-CI Credit SS 1, Option 1F.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Time switches.

2. Photoelectric switches.

3. [Indoor occupancy] [switchbox-mounted occupancy] [and] [outdoor motion] sensors.

B. Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 262726 "Wiring Devices" for wall-box dimmers, wall-switch occupancy sensors, and manual light switches.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 TIME SWITCHES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper Industries, Inc.

2. Intermatic, Inc.

3. Invensys Controls.

4. Leviton Manufacturing Co., Inc.

5. NSi Industries LLC; TORK Products.

6. Tyco Electronics; ALR Brand.

7. <Insert manufacturer's name>.

Retain "Electronic Time Switches" or "Electromechanical-Dial Time Switches" Paragraph below.

C. Electronic Time Switches: Solid state, programmable, with alphanumeric display; complying with UL 917.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain "Contact Configuration" Subparagraph below if configuration is not indicated on Drawings.

2. Contact Configuration: [SPST] [DPST] [DPDT] <Insert configuration>.

3. Contact Rating: [30-A inductive or resistive, 240-V ac] [20-A ballast load, 120-/240-V ac] <Insert rating>.

Retain one of eight "Programs" subparagraphs below.

4. Programs: Eight on-off set points on a 24-hour schedule[ and an annual holiday schedule that overrides the weekly operation on holidays].

5. Programs: Two on-off set points on a 24-hour schedule, allowing different set points for each day of the week[ and an annual holiday schedule that overrides the weekly operation on holidays].

6. Programs: <Insert number> channels; each channel is individually programmable with eight on-off set points on a 24-hour schedule.

7. Programs: <Insert number> channels; each channel is individually programmable with two on-off set points on a 24-hour schedule with a skip-a-day weekly schedule.

8. Programs: <Insert number> channels; each channel is individually programmable with two on-off set points on a 24-hour schedule, allowing different set points for each day of the week.

9. Programs: <Insert number> channels; each channel is individually programmable with 40 on-off operations per week and an annual holiday schedule that overrides the weekly operation on holidays.

10. Programs: <Insert number> channels; each channel is individually programmable with 40 on-off operations per week, plus four seasonal schedules that modify the basic program, and an annual holiday schedule that overrides the weekly operation on holidays.

11. Programs: <Insert configuration>[ and an annual holiday schedule that overrides the weekly operation on holidays].

12. Circuitry: Allow connection of a photoelectric relay as substitute for on-off function of a program[ on selected channels].

13. Astronomic Time: [All] [Selected] channels.

If retaining first subparagraph below, the timer will change the time at 2:00 a.m. on the second Sunday in March and on the first Sunday in November.

14. Automatic daylight savings time changeover.

15. Battery Backup: Not less than seven days reserve, to maintain schedules and time clock.

D. Electromechanical-Dial Time Switches: Comply with UL 917.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain "Contact Configuration" Subparagraph below if configuration is indicated on Drawings.

2. Contact Configuration: [SPST] [DPST] [SPDT] [DPDT] <Insert configuration>.

3. Contact Rating: [30-A inductive or resistive, 240-V ac] [20-A ballast load, 120-/240-V ac] <Insert rating>.

Five subparagraphs below describe optional features.

4. Circuitry: Allows connection of a photoelectric relay as a substitute for the on-off function of a program.

Retain first subparagraph below to make time switches self-adjust for seasonal changes and automatically adjust on-off times as days grow shorter or longer.

5. Astronomic time dial.

6. Eight-Day Program: Uniquely programmable for each weekday and holidays.

7. Skip-a-day mode.

8. Wound-spring reserve carryover mechanism to keep time during power failures, minimum of [16] <Insert number> hours.

2.2 OUTDOOR PHOTOELECTRIC SWITCHES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper Industries, Inc.

2. Intermatic, Inc.

3. NSi Industries LLC; TORK Products.

4. Tyco Electronics; ALR Brand.

5. <Insert manufacturer's name>.

"Description" Paragraph below describes a device with less-effective surge protection, having a fixed load-breaking contact capacity. Its main application is control of a single lighting fixture. It is designed for mounting on a fixture.

C. Description: Solid state, with [SPST] [DPST] dry contacts rated for 1800 VA, to operate connected load, complying with UL 773.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Light-Level Monitoring Range: 1.5 to 10 fc (16.14 to 108 lux), with an adjustment for turn-on and turn-off levels within that range.

3. Time Delay: Thirty-second minimum, to prevent false operation.

4. Lightning Arrester: Air-gap type.

5. Mounting: Twist lock complying with NEMA C136.10, with base.

2.3 INDOOR OCCUPANCY SENSORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bryant Electric.

2. Cooper Industries, Inc.

3. Hubbell Building Automation, Inc.

4. Leviton Manufacturing Co., Inc.

5. Lightolier Controls.

6. Lithonia Lighting; Acuity Brands Lighting, Inc.

7. Lutron Electronics Co., Inc.

8. NSi Industries LLC; TORK Products.

9. RAB Lighting.

10. Sensor Switch, Inc.

11. Square D.

12. Watt Stopper.

13. <Insert manufacturer's name>.

C. General Requirements for Sensors: Wall- or ceiling-mounted, solid-state indoor occupancy sensors with a separate power pack.

Retain subparagraphs below to specify various types of units required for Project.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Operation: Unless otherwise indicated, turn lights on when coverage area is occupied, and turn them off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

3. Sensor Output: Contacts rated to operate the connected relay, complying with UL 773A. Sensor is powered from the power pack.

4. Power Pack: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Sensor has 24-V dc, 150-mA, Class 2 power source, as defined by NFPA 70.

5. Mounting:

a. Sensor: Suitable for mounting in any position on a standard outlet box.

b. Relay: Externally mounted through a 1/2-inch (13-mm) knockout in a standard electrical enclosure.

c. Time-Delay and Sensitivity Adjustments: Recessed and concealed behind hinged door.

6. Indicator: Digital display, to show when motion is detected during testing and normal operation of sensor.

7. Bypass Switch: Override the "on" function in case of sensor failure.

8. Automatic Light-Level Sensor: Adjustable from 2 to 200 fc (21.5 to 2152 lux); turn lights off when selected lighting level is present.

Retain one or more of "PIR Type," "Ultrasonic Type," and "Dual-Technology Type" paragraphs below. Revise coverage area of detectors and add detectors with different coverage patterns and features to suit Project.

D. PIR Type: Ceiling mounted; detect occupants in coverage area by their heat and movement.

1. Detector Sensitivity: Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm).

2. Detection Coverage (Room): Detect occupancy anywhere in a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

3. Detection Coverage (Corridor): Detect occupancy within 90 feet (27.4 m) when mounted on a 10-foot- (3-m-) high ceiling.

E. Ultrasonic Type: Ceiling mounted; detect occupants in coverage area through pattern changes of reflected ultrasonic energy.

1. Detector Sensitivity: Detect a person of average size and weight moving not less than 12 inches (305 mm) in either a horizontal or a vertical manner at an approximate speed of 12 inches/s (305 mm/s).

Areas listed in detection coverage subparagraphs below are typical.

2. Detection Coverage (Small Room): Detect occupancy anywhere within a circular area of 600 sq. ft. (56 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

3. Detection Coverage (Standard Room): Detect occupancy anywhere within a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

4. Detection Coverage (Large Room): Detect occupancy anywhere within a circular area of 2000 sq. ft. (186 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

5. Detection Coverage (Corridor): Detect occupancy anywhere within 90 feet (27.4 m) when mounted on a 10-foot- (3-m-) high ceiling in a corridor not wider than 14 feet (4.3 m).

F. Dual-Technology Type: Ceiling mounted; detect occupants in coverage area using PIR and ultrasonic detection methods. The particular technology or combination of technologies that control on-off functions is selectable in the field by operating controls on unit.

1. Sensitivity Adjustment: Separate for each sensing technology.

2. Detector Sensitivity: Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm), and detect a person of average size and weight moving not less than 12 inches (305 mm) in either a horizontal or a vertical manner at an approximate speed of 12 inches/s (305 mm/s).

3. Detection Coverage (Standard Room): Detect occupancy anywhere within a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

2.4 SWITCHBOX-MOUNTED OCCUPANCY SENSORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bryant Electric.

2. Cooper Industries, Inc.

3. Hubbell Building Automation, Inc.

4. Leviton Manufacturing Co., Inc.

5. Lightolier Controls.

6. Lithonia Lighting; Acuity Brands Lighting, Inc.

7. Lutron Electronics Co., Inc.

8. NSi Industries LLC; TORK Products.

9. RAB Lighting.

10. Sensor Switch, Inc.

11. Square D.

12. Watt Stopper.

13. <Insert manufacturer's name>.

Each manufacturer's switch rating is different; however, rated design values are generally not less than those stated in "General Requirements for Sensors" Paragraph below.

C. General Requirements for Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application[, and shall comply with California Title 24].

2. Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F (0 to 49 deg C).

3. Switch Rating: Not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent.

"WS1" and "WS2" in "Wall-Switch Sensor Tag WS1" and "Wall-Switch Sensor Tag WS2" paragraphs below are a suggested marking system on Drawings when detectors with different sensor characteristics are required.

D. Wall-Switch Sensor Tag WS1:

1. Standard Range: 180-degree field of view, field adjustable from 180 to 40 degrees; with a minimum coverage area of [900 sq. ft. (84 sq. m)] [2100 sq. ft (196 sq. m)].

2. Sensing Technology: [PIR] [Dual technology - PIR and ultrasonic].

3. Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."] [SP, field selectable automatic "on," or manual "on" automatic "off."]

4. Voltage: [Match the circuit voltage] [120 V] [277 V] [Dual voltage, 120 and 277 V]; [passive-infrared] [dual-technology] type.

5. Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc (108 to 1600 lux). The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

6. Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

7. Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

8. Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and helps eliminate false "off" switching.

"Wall-Switch Sensor Tag WS2" Paragraph below is typical for square and near-square rectangular rooms.

E. Wall-Switch Sensor Tag WS2:

1. Standard Range: 210-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

2. Sensing Technology: PIR.

3. Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."] [SP, field selectable automatic "on," or manual "on" automatic "off."]

4. Voltage: [Match the circuit voltage] [120 V] [277 V] [Dual voltage, 120 and 277 V]; [passive-infrared] [dual-technology] type.

5. Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc (108 to 1600 lux). The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

6. Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

7. Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

8. Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and helps eliminate false "off" switching.

2.5 OUTDOOR MOTION SENSORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bryant Electric.

2. Cooper Industries, Inc.

3. Hubbell Building Automation, Inc.

4. Leviton Manufacturing Co., Inc.

5. Lithonia Lighting; Acuity Brands Lighting, Inc.

6. NSi Industries LLC; TORK Products.

7. RAB Lighting.

8. Sensor Switch, Inc.

9. Watt Stopper.

10. <Insert manufacturer's name>.

C. General Requirements for Sensors: Solid-state outdoor motion sensors.

Retain features in subparagraphs below applicable to motion sensors for Project.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application[, and shall comply with California Title 24].

2. [PIR] [Dual-technology (PIR and infrared)] type, weatherproof. Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm). Comply with UL 773A.

3. Switch Rating:

a. Lighting-Fixture-Mounted Sensor: [1000-W incandescent, 500-VA fluorescent] <Insert rating>.

b. Separately Mounted Sensor: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Sensor has 24-V dc, 150-mA, Class 2 power source, as defined by NFPA 70.

4. Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."][SP, field selectable automatic "on," or manual "on" automatic "off."][ With bypass switch to override the "on" function in case of sensor failure.]

5. Voltage: [Match the circuit voltage] [120-V] [277-V] [Dual voltage, 120- and 277-V] type.

6. Detector Coverage:

a. Standard Range: 210-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

b. Long Range: 180-degree field of view and 110-foot (34-m) detection range.

c. <Insert coverage area>.

7. Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc (108 to 1600 lux). The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

8. Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

9. Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

10. Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and helps eliminate false "off" switching.

11. Operating Ambient Conditions: Suitable for operation in ambient temperatures ranging from minus 40 to plus 130 deg F (minus 40 to plus 54 deg C), rated as "raintight" according to UL 773A.

2.6 LIGHTING CONTACTORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Allen-Bradley/Rockwell Automation.

2. ASCO Power Technologies, LP.

3. Eaton Corporation.

4. General Electric Company; GE Consumer &amp;amp; Industrial - Electrical Distribution; Total Lighting Control.

5. Square D.

6. <Insert manufacturer's name>.

C. Description: Electrically operated and [mechanically] [electrically] held, combination-type lighting contactors with [fusible switch] [nonfused disconnect], complying with NEMA ICS 2 and UL 508.

Revise subparagraphs below, if required, for specific ratings; or indicate on Drawings. Coordinate control voltage with lighting control system if used. See Evaluations for suggested options to be indicated on Drawings.

1. Current Rating for Switching: Listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballast with 15 percent or less total harmonic distortion of normal load current).

2. Fault Current Withstand Rating: Equal to or exceeding the available fault current at the point of installation.

3. Enclosure: Comply with NEMA 250.

4. Provide with control and pilot devices as [indicated on Drawings] [scheduled], matching the NEMA type specified for the enclosure.

2.7 CONDUCTORS AND CABLES

A. Power Wiring to Supply Side of Remote-Control Power Sources: Not smaller than No. 12 AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

B. Classes 2 and 3 Control Cable: Multiconductor cable with stranded-copper conductors not smaller than [No. 18] [No. 22] [No. 24] AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

C. Class 1 Control Cable: Multiconductor cable with stranded-copper conductors not smaller than [No. 14] [No. 16] [No. 18] AWG. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated. Do not exceed coverage limits specified in manufacturer's written instructions.

B. Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting sensors to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

1. For occupancy and motion sensors, verify operation at outer limits of detector range. Set time delay to suit Owner's operations.

C. Mount electrically held lighting contactors with elastomeric isolator pads to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

D. Wiring Method: Comply with Section 260519 "Low-Voltage Electrical Power Conductors and Cables." Minimum conduit size is 1/2 inch (13 mm).

E. Identify components and power and control wiring according to Section 260553 "Identification for Electrical Systems."

3.2 FIELD QUALITY CONTROL

Retain "Testing Agency" and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph or if retaining "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to evaluate lighting control devices and perform tests and inspections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

B. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Operational Test: After installing time switches and sensors, and after electrical circuitry has been energized, start units to confirm proper unit operation.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Lighting control devices will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

END OF SECTION 260923

	LIGHTING CONTROL DEVICES
	260923 - 1



