Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262500 - ENCLOSED BUS ASSEMBLIES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Feeder-bus assemblies.

2. Plug-in bus assemblies.

3. Bus plug-in devices.

1.2 ACTION SUBMITTALS

A. Shop Drawings: For each type of [bus assembly] [and plug-in device].

1. Show fabrication and installation details for enclosed bus assemblies.

Retain first subparagraph below if Project requires fire-stop or weather barriers.

2. Show fittings, materials, fabrication, and installation methods for [listed fire-stop barriers] [and] [weather barriers].

3. Wiring Diagrams: Power[ and signal] [ and control] [, signal, and control] wiring.

Retain subparagraph and associated subparagraphs below if products are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify products' compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

4. Seismic-Restraint Details: Signed and sealed by a qualified professional engineer.

a. Design Calculations: Calculate requirements for selecting seismic restraints.

b. Detail fabrication, including anchorages and attachments to structure and to supported equipment.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

A. Manufacturer Seismic Qualification Certification: Submit certification that enclosed bus assemblies,[ plug-in devices,] accessories, and components will withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

B. Field quality-control test reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NEMA BU 1, "Busways."

C. Comply with NFPA 70.

1.6 PROJECT CONDITIONS

A. Derate enclosed bus assemblies for continuous operation at indicated ampere ratings for ambient temperature not exceeding [122 deg F (50 deg C)] [140 deg F (60 deg C)] <Insert ambient temperature>.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of two paragraphs and list of manufacturers in this Article. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1. Calvert Company (The).

2. Eaton Electrical Inc.; Cutler-Hammer Products.

3. General Electric Company; Electrical Distribution & Control Division.

4. Siemens Energy & Automation, Inc.

5. Square D; Schneider Electric.

6. <Insert manufacturer's name.>

2.2 ENCLOSED BUS ASSEMBLIES

A. Feeder-Bus Assemblies: NEMA BU 1, low-impedance bus assemblies in nonventilated housing; single-bolt joints; ratings as indicated.

Retain subparagraph below for projects in seismic areas. Coordinate with "Informational Submittals" Article for submittal of manufacturer's seismic qualification certification.

1. Seismic Fabrication Requirements: Fabricate mounting provisions and attachments for feeder-bus assemblies with reinforcement strong enough to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems" when mounting provisions and attachments are anchored to building structure

Select from options in first subparagraph below and revise to suit Project. Consider 200 percent neutral on 4-wire systems if a significant portion of load is nonlinear (e.g., computers, fluorescent or high-intensity-discharge lighting, variable-frequency drives, etc.) and harmonic cancellation on the neutral conductor is unlikely. If busways with different voltages and neutral capacities are required, delete subparagraph and include a schedule on Drawings. See sample schedule in the Evaluations.

2. Voltage: [120/208] [240] [480] [277/480] V; 3 phase; [100] [200] [percent neutral capacity].

3. Temperature Rise: 55 deg C above 40 deg C ambient maximum for continuous rated current.

4. Bus Materials: Current-carrying [copper] [aluminum] conductors, fully insulated with Class 130C insulation except at joints; plated surface at joints.

5. Ground:

Retain one or more of three subparagraphs below.

a. 50 percent capacity integral with housing.

b. 50 percent capacity internal bus bars of material matching bus material.

c. 50 percent capacity isolated, internal bus bar of material matching bus material.

If busways with different ground or enclosure types are required, delete "Ground" Subparagraph and associated subparagraphs above or "Enclosure" Subparagraph below, or both, and include a schedule on Drawings. See sample schedule in the Evaluations.

6. Enclosure: [Steel with manufacturer's standard finish] [Aluminum with manufacturer's standard finish] [Weatherproof, steel or aluminum with manufacturer's standard finish, sealed seams, drains, and removable closures].

7. Fittings and Accessories: Manufacturer's standard.

8. Mounting: Arranged flat, edgewise, or vertically without derating.

B. Plug-in Bus Assemblies: NEMA BU 1, low-impedance bus assemblies in nonventilated housing; single-bolt joints; ratings as indicated.

Retain subparagraph below for projects in seismic areas. Coordinate with "Informational Submittals" Article for submittal of manufacturer's seismic qualification certification.

1. Seismic Fabrication Requirements: Fabricate mounting provisions and attachments for switchboards with reinforcement strong enough to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems" when mounting provisions and attachments are anchored to building structure.

Select from options in first subparagraph below and revise to suit Project. Consider 200 percent neutral on 4-wire systems if a significant portion of load is nonlinear (e.g., computers, fluorescent or high-intensity-discharge lighting, variable-frequency drives, etc.) and harmonic cancellation on the neutral conductor is unlikely. If busways with different voltages and neutral capacities are required, delete subparagraph and include a schedule on Drawings. See sample schedule in the Evaluations.

2. Voltage: [120/208] [240] [480] [277/480] V; 3 phase; [100] [200] [percent neutral capacity].

3. Temperature Rise: 55 deg C above 40 deg C ambient maximum for continuous rated current.

4. Bus Materials: Current-carrying [copper] [aluminum] conductors, fully insulated with Class 130C insulation except at stabs and joints; plated surface at stabs and joints.

5. Ground:

Retain one or more of three subparagraphs below.

a. 50 percent capacity integral with housing.

b. 50 percent capacity internal bus bar of material matching bus material.

c. 50 percent capacity isolated, internal bus bar of material matching bus material.

If busways with different ground or enclosure types are required, delete "Ground" Subparagraph and associated subparagraphs above or "Enclosure" Subparagraph below, or both, and include a schedule on Drawings. See sample schedule in the Evaluations.

6. Enclosure: [Steel, with manufacturer's standard finish, plug-in openings 24 inches (610 mm) o.c., and hinged covers over unused openings] [Aluminum, with manufacturer's standard finish, plug-in openings 24 inches (610 mm) o.c., and hinged covers over unused openings].

7. Fittings and Accessories: Manufacturer's standard.

8. Mounting: Arranged flat, edgewise, or vertically without derating.

2.3 PLUG-IN DEVICES

Chain-operable handles are available for plug-in devices.

For fusible-switch plug-in devices, R-type rejection fuse clips and J-type fuse clips are available in sizes from 30 to 600 A, rated 600 V. L-type, bolt-on fuse clips are available in 800 to 1600 A, 600-V fusible switches. Coordinate options selected in paragraph below with Section 262813 "Fuses."

A. Fusible Switches: NEMA KS 1, heavy duty; with [R-type rejection] [J-type] [L-type] fuse clips to accommodate specified fuses; hookstick-operated handle, lockable with two padlocks, and interlocked with cover in closed position. See Section 262813 "Fuses" for fuses and fuse installation requirements.

Indicate in schedule or diagrams on Drawings the frame size, trip rating, number of poles, interrupting-capacity rating, and auxiliary devices.

B. Molded-Case Circuit Breakers: NEMA AB 1; hookstick-operated handle, lockable with two padlocks, and interlocked with cover in closed position.

Retain paragraph below if required.

C. Accessories: Hookstick operator, adjustable to maximum extension of [14 feet (4.3 m)] <Insert dimension>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Support bus assemblies independent of supports for other elements such as equipment enclosures at connections to panelboards and switchboards, pipes, conduits, ceilings, and ducts.

1. Design each fastener and support to carry load indicated by seismic requirements and to comply with seismic-restraint details according to Section 260548.16 "Seismic Controls for Electrical Systems."

Retain subparagraph above if requirements for seismic control are included in Part 1. Retain four subparagraphs below if seismic restraint is not required. Revise to suit Project.

2. Design each fastener and support to carry 200 lb (90 kg) or 4 times the weight of bus assembly, whichever is greater.

3. Support bus assembly to prevent twisting from eccentric loading.

4. Support bus assembly with not less than 3/8-inch (10-mm) steel rods. Install side bracing to prevent swaying or movement of bus assembly. Modify supports after completion to eliminate strains and stresses on bus bars and housings.

5. Fasten supports securely to building structure according to Section 260529 "Hangers and Supports for Electrical Systems."

B. Install expansion fittings at locations where bus assemblies cross building expansion joints. Install at other locations so distance between expansion fittings does not exceed manufacturer's recommended distance between fittings.

C. Construct rated fire-stop assemblies where bus assemblies penetrate fire-rated elements such as walls, floors, and ceilings. Seal around penetrations according to Section 078413 "Penetration Firestopping."

D. Install weatherseal fittings and flanges where bus assemblies penetrate exterior elements such as walls or roofs. Seal around openings to make weathertight. See Section 079200 "Joint Sealants" for materials and application.

Coordinate floor penetrations with Structural Drawings.

E. Install a concrete curb at least 4 inches (100 mm) high around bus-assembly floor penetrations.

F. Coordinate bus-assembly terminations to equipment enclosures to ensure proper phasing, connection, and closure.

G. Tighten bus-assembly joints with torque wrench or similar tool recommended by bus-assembly manufacturer. Tighten joints again after bus assemblies have been energized for 30 days.

H. Install bus-assembly, plug-in units. Support connecting conduit independent of plug-in unit.

I. Set field-adjustable, circuit-breaker trip ranges[ and overload relay trip settings] as indicated.

3.2 FIELD QUALITY CONTROL

A. Perform tests and inspections.

B. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Infrared Scanning: Two months after Substantial Completion, perform an infrared scan of bus assembly including joints and plug-in units.

a. Use an infrared-scanning device designed to measure temperature or detect significant deviations from normal values. Provide documentation of device calibration.

b. Perform 2 follow-up infrared scans of bus assembly, one at 4 months and the other at 11 months after Substantial Completion.

c. Prepare a certified report identifying bus assembly checked and describing results of scanning. Include notation of deficiencies detected, remedial action taken, and scanning observations after remedial action.

END OF SECTION 262500

	ENCLOSED BUS ASSEMBLIES
	262500 - 1



