Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 265600 - EXTERIOR LIGHTING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. ASHRAE/IESNA 90.1, Section 9 - "Lighting," sets maximum interior and exterior lighting power densities and minimum requirements for lighting controls. The selection of the lamp and ballast as a system is an important design decision to optimize energy efficiency of the lighting system.

A reduction in lighting energy usage can be combined with other energy-conserving measures to meet the requirements of LEED-NC, LEED-CS, and LEED for Schools Credit EA 1.

LEED-NC, LEED-CS, and LEED for Schools Credit SS 8 requires that exterior lights be provided as needed for "safety and comfort" with the lighting power densities for the exterior areas and the building facade and landscape at a minimum of 20 and 50% less than ASHRAE/IESNA 90.1, respectively. In addition, the lighting design must eliminate or minimize any "light trespass" from the site and reduce "sky glow," depending on the zone classification of the site according to IESNA RP-33 requirements. Consider selecting the proper light fixtures, such as low-intensity shielded fixtures, the aiming of the fixtures, and using automatic controllers to turn off nonessential site lighting after a specific hour as defined by this credit. Credit SS 8 also sets requirements for interior lighting. See Section 265100 "Interior Lighting."

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Exterior luminaires with lamps and ballasts.

2. Luminaire-mounted photoelectric relays.

3. Poles and accessories.

1.2 STRUCTURAL ANALYSIS CRITERIA FOR POLE SELECTION

Retain this article if manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4-M. Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in the Exterior Lighting Device Schedule or in details on Drawings. See Editing Instruction No. 1 in the Evaluations.

A. Dead Load: Weight of luminaire and its horizontal and vertical supports, lowering devices, and supporting structure, applied as stated in AASHTO LTS-4-M.

Retain "Live Load" Paragraph below if Project includes pole-mounted walkways.

B. Live Load: Single load of 500 lbf (2224 N), distributed as stated in AASHTO LTS-4-M.

Retain "Ice Load" Paragraph below if Project is inside the area shown in the Ice Load Map, Figure 3-1.

C. Ice Load: Load of 3 lbf/sq. ft. (145 Pa), applied as stated in AASHTO LTS-4-M Ice Load Map.

See Editing Instruction No. 2 in the Evaluations for discussion of wind-load calculations.

D. Wind Load: Pressure of wind on pole and luminaire and banners and banner arms, calculated and applied as stated in AASHTO LTS-4-M.

1. Basic wind speed for calculating wind load for poles exceeding 49.2 feet (15 m) in height is [100 mph (45 m/s)] [90 mph (40 m/s)] <Insert value from AASHTO LTS-4-M>.

a. Wind Importance Factor: [1.0] <Insert value from Table 3-2>.

b. Minimum Design Life: [50 years] <Insert value from Table 3-3>.

c. Velocity Conversion Factors: [1.0] <Insert value from Table 3-2>.

2. Basic wind speed for calculating wind load for poles 50 feet (15 m) high or less is [100 mph (45 m/s)] [90 mph (40 m/s)] <Insert value from AASHTO LTS-4-M for this Project>.

a. Wind Importance Factor: [1.0] <Insert value from Table 3-2>.

b. Minimum Design Life: [25 years] <Insert value from Table 3-3>.

c. Velocity Conversion Factors: [1.0] <Insert value from Table 3-2>.

1.3 ACTION SUBMITTALS

A. Product Data: For each luminaire, pole, and support component, arranged in order of lighting unit designation. Include data on features, accessories, and finishes.

B. Shop Drawings: Anchor-bolt templates keyed to specific poles and certified by manufacturer.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with IEEE C2, "National Electrical Safety Code."

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

In "Products" Paragraph below, retain first option when only one manufacturer and product designation is indicated on Drawings and Contractor must use named product; retain second option when more than one manufacturer and product is indicated on Drawings, providing choices for Contractor among those listed; retain third option if one or more manufacturers and products are indicated and Contractor may propose products from other manufacturers. Delete this article if no manufacturers and product designations are indicated. See Section 016000 "Product Requirements."

A. Products: Subject to compliance with requirements, [provide product indicated on Drawings] [provide one of the products indicated on Drawings] [available products that may be incorporated into the Work include, but are not limited to, product(s) indicated on Drawings].

2.2 GENERAL REQUIREMENTS FOR LUMINAIRES

A. Luminaires shall comply with UL 1598 and be listed and labeled for installation in wet locations by an NRTL acceptable to authorities having jurisdiction.

See Editing Instruction No. 6 in the Evaluations for discussion of LER.

1. LER Tests Incandescent Fixtures: Where LER is specified, test according to NEMA LE 5A.

2. LER Tests HID Fixtures: Where LER is specified, test according to NEMA LE 5B.

Retain "Lateral Light Distribution Patterns" Paragraph below if some lighting units or luminaires are indicated to have Type I, II, III, IV, or V distribution pattern in the Exterior Lighting Device Schedule or in details on Drawings.

B. Lateral Light Distribution Patterns: Comply with IESNA RP-8 for parameters of lateral light distribution patterns indicated for luminaires.

C. Metal Parts: Free of burrs and sharp corners and edges.

D. Sheet Metal Components: Corrosion-resistant aluminum unless otherwise indicated. Form and support to prevent warping and sagging.

E. Housings: Rigidly formed, weather- and light-tight enclosures that will not warp, sag, or deform in use. Provide filter/breather for enclosed luminaires.

F. Doors, Frames, and Other Internal Access: Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools. Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position. Doors shall be removable for cleaning or replacing lenses. Designed to disconnect ballast when door opens.

G. Exposed Hardware Material: Stainless steel.

H. Plastic Parts: High resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

Retain "Light Shields" Paragraph below if one or more luminaires require partial shielding of light output to avoid light trespass or to meet other requirements. Coordinate with the Exterior Lighting Device Schedule on Drawings.

I. Light Shields: Metal baffles, factory installed and field adjustable, arranged to block light distribution to indicated portion of normally illuminated area or field.

J. Reflecting surfaces shall have minimum reflectance as follows unless otherwise indicated:

1. White Surfaces: 85 percent.

2. Specular Surfaces: 83 percent.

3. Diffusing Specular Surfaces: 75 percent.

K. Lenses and Refractors Gaskets: Use heat- and aging-resistant resilient gaskets to seal and cushion lenses and refractors in luminaire doors.

Revise "Luminaire Finish" Paragraph below to include custom colors. Coordinate custom-color requirements for luminaires with those for poles and other luminaire support requirements.

L. Luminaire Finish: Manufacturer's standard paint applied to factory-assembled and -tested luminaire before shipping. Where indicated, match finish process and color of pole or support materials.

Retain "Factory-Applied Finish for Steel Luminaires" Paragraph below when luminaire material is steel that is not to be field painted and is not required to match finish of pole or support materials.

M. Factory-Applied Finish for Steel Luminaires: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Surface Preparation: Clean surfaces to comply with SSPC-SP 1, "Solvent Cleaning," to remove dirt, oil, grease, and other contaminants that could impair paint bond. Grind welds and polish surfaces to a smooth, even finish. Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1, "White Metal Blast Cleaning," or SSPC-SP 8, "Pickling."

2. Exterior Surfaces: Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

Retain one of three "Color" subparagraphs below.

a. Color: As selected from manufacturer's standard catalog of colors.

b. Color: Match Architect's sample of [manufacturer's standard] [custom] color.

c. Color: As selected by Architect from manufacturer's full range.

Retain "Factory-Applied Finish for Aluminum Luminaires" Paragraph below when luminaire material is aluminum that is not to be field painted and is not required to match finish of pole or support materials.

N. Factory-Applied Finish for Aluminum Luminaires: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain one of three finish subparagraphs below or revise to suit Project.

2. Natural Satin Finish: Provide fine, directional, medium satin polish (AA-M32); buff complying with AA-M20; and seal aluminum surfaces with clear, hard-coat wax.

3. Class I, Clear Anodic Finish: AA-M32C22A41 (Mechanical Finish: medium satin; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

4. Class I, Color Anodic Finish: AA-M32C22A42/A44 (Mechanical Finish: medium satin; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker) complying with AAMA 611.

a. Color: [Light bronze] [Medium bronze] [Dark bronze] [Black].

See Editing Instruction No. 7 in the Evaluations for discussion of luminaire labeling.

O. Factory-Applied Labels: Comply with UL 1598. Include recommended lamps and ballasts. Labels shall be located where they will be readily visible to service personnel, but not seen from normal viewing angles when lamps are in place.

1. Label shall include the following lamp and ballast characteristics:

a. "USES ONLY" and include specific lamp type.

b. Lamp tube configuration (twin, quad, triple), base type, and nominal wattage for compact fluorescent luminaires.

c. Lamp type, wattage, bulb type (ED17, BD56, etc.) and coating (clear or coated) for HID luminaires.

d. Start type (preheat, rapid start, instant start) compact fluorescent luminaires.

e. ANSI ballast type (M98, M57, etc.) for HID luminaires.

f. CCT and CRI for all luminaires.

2.3 LUMINAIRE-MOUNTED PHOTOELECTRIC RELAYS

A. Comply with UL 773 or UL 773A.

B. Contact Relays: Factory mounted, single throw, designed to fail in the on position, and factory set to turn light unit on at 1.5 to 3 fc (16 to 32 lx) and off at 4.5 to 10 fc (48 to 108 lx) with 15-second minimum time delay.[ Relay shall have directional lens in front of photocell to prevent artificial light sources from causing false turnoff.]

1. Relay with locking-type receptacle shall comply with ANSI C136.10.

2. Adjustable window slide for adjusting on-off set points.

2.4 FLUORESCENT BALLASTS AND LAMPS

See Editing Instruction No. 4 in the Evaluations for discussion of low-temperature application of fluorescent luminaires, lamps, and ballasts.

A. Ballasts for Low-Temperature Environments:

Retain "electromagnetic" option in first subparagraph below if lamp starting and operating temperature near 0 deg F (minus 17 deg C) is a critical requirement. Verify, with manufacturers, the compatibility of ballasts with indicated lamps for low-temperature operation.

1. Temperatures 0 Deg F (Minus 17 Deg C) and Higher: [Electronic] [or] [electromagnetic] type rated for 0 deg F (minus 17 deg C) starting and operating temperature with indicated lamp types.

2. Temperatures Minus 20 Deg F (Minus 29 Deg C) and Higher: Electromagnetic type designed for use with indicated lamp types.

B. Ballast Characteristics:

1. Power Factor: 90 percent, minimum.

2. Sound Rating: Class A.

See Evaluations for discussion of harmonic distortion in first subparagraph below.

3. Total Harmonic Distortion Rating: Less than [10] [20] percent.

4. Electromagnetic Ballasts: Comply with ANSI C82.1, energy-saving, high power factor, Class P, automatic-reset thermal protection.

5. Case Temperature for Compact Lamp Ballasts: 65 deg C, maximum.

6. Transient-Voltage Protection: Comply with IEEE C62.41.1 and IEEE C62.41.2, Category A or better.

Coordinate "Low-Temperature Lamp Capability" Paragraph below with Drawings, and indicate lamp type for each fluorescent luminaire in the Exterior Lighting Device Schedule on Drawings or in description in this Section. Where color rendition or color uniformity is important and several types of fluorescent lamps are used, provide consistent manufacturer designations or ANSI lamp designations to define requirements.

For applications at low temperatures, verify that lamp, ballast, and luminaire combinations indicated will start reliably and provide required light output throughout the range of temperatures that may be encountered.

C. Low-Temperature Lamp Capability: Rated for reliable starting and operation with ballast provided at temperatures [0 deg F (minus 18 deg C)] [minus 20 deg F (minus 29 deg C)] and higher.

2.5 BALLASTS FOR HID LAMPS

A. Comply with ANSI C82.4 and UL 1029 and capable of open-circuit operation without reduction of average lamp life. Include the following features unless otherwise indicated:

1. Ballast Circuit: Constant-wattage autotransformer or regulating high-power-factor type.

2. Minimum Starting Temperature: Minus 22 deg F (Minus 30 deg C).

3. Normal Ambient Operating Temperature: 104 deg F (40 deg C).

Retain "Ballast Fuses" Subparagraph below if ballasts are required to be fused. See Editing Instruction No. 3 in the Evaluations for discussion of ballast fusing.

4. Ballast Fuses: One in each ungrounded power supply conductor. Voltage and current ratings as recommended by ballast manufacturer.

B. High-Pressure Sodium Ballasts: Electromagnetic type with solid-state igniter/starter and capable of open-circuit operation without reduction of average lamp life. Igniter/starter shall have an average life in pulsing mode of 10,000 hours at an igniter/starter-case temperature of 90 deg C.

2.6 HID LAMPS

Coordinate this article with Drawings. Where color rendition or color uniformity is important and several types of HID lamps are used, provide consistent manufacturer designations or ANSI designations to define lamp types.

A. High-Pressure Sodium Lamps: ANSI C78.42, CRI 21 (minimum), CCT color temperature [1900] <Insert value> K, and average rated life of 24,000 hours, minimum.

Consider retaining "Dual-Arc Tube Lamp" Subparagraph below if extinguishing of high-pressure sodium lamps caused by momentary power interruptions is unacceptable for safety, security, or other reasons. Verify, with manufacturers, availability of individual ratings before scheduling or specifying.

1. Dual-Arc Tube Lamp: Arranged so only one of two arc tubes is lighted at one time and, when power is restored after an outage, the cooler arc tube, with lower internal pressure, lights instantly, providing an immediate 8 to 15 percent of normal light output.

B. Low-Pressure Sodium Lamps: ANSI C78.43.

ANSI has a separate standard for each conventional metal-halide lamp, unlike standards for low- and high-pressure sodium lamps. Consider including the standard number in the Exterior Lighting Device Schedule on Drawings. Wattage and mean lumen output ratings for each lamp may be included in the Exterior Lighting Device Schedule on Drawings.

C. Metal-Halide Lamps: ANSI C78.43, with minimum CRI [65] <Insert value>, and CCT color temperature [4000] <Insert value> K.

Pulse-start, metal-halide lamps in first paragraph below are available in ratings from 30 to 1000 W and provide higher lumen maintenance and reduced color-shift throughout the life of the lamp, compared with basic metal-halide lamps. This may permit use of lower-wattage lamps to provide the same maintained illumination level provided by an equal number of conventional metal-halide lamps. Consult manufacturers to verify compatibility of lamps with ballasts and luminaires.

D. Pulse-Start, Metal-Halide Lamps: Minimum CRI 65, and CCT color temperature [4000] <Insert value> K.

Ceramic, pulse-start, metal-halide lamps in paragraph below are available in ratings from about 40 to 250 W. Besides advantages inherent in pulse-start technology, these lamps have an improved CRI, between 80 and 94, with higher initial and maintained lumen output.

E. Ceramic, Pulse-Start, Metal-Halide Lamps: Minimum CRI [80] <Insert value>, and CCT color temperature [4000] <Insert value> K.

2.7 GENERAL REQUIREMENTS FOR POLES AND SUPPORT COMPONENTS

A. Structural Characteristics: Comply with AASHTO LTS-4-M.

Retain two subparagraphs below if retaining "Structural Analysis Criteria for Pole Selection" Article and manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4-M. Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in the Exterior Lighting Device Schedule or details on Drawings. See Editing Instruction No. 1 in the Evaluations.

1. Wind-Load Strength of Poles: Adequate at indicated heights above grade without failure, permanent deflection, or whipping in steady winds of speed indicated in "Structural Analysis Criteria for Pole Selection" Article.

Retain "Strength Analysis" Subparagraph below to help ensure that poles are stiff enough to avoid excessive flexure and vibration. Alternatively, add requirements for minimum pole wall thickness and other parameters. See Editing Instruction No. 5 in the Evaluations.

2. Strength Analysis: For each pole, multiply the actual equivalent projected area of luminaires and brackets by a factor of [1.1] <Insert number> to obtain the equivalent projected area to be used in pole selection strength analysis.

B. Luminaire Attachment Provisions: Comply with luminaire manufacturers' mounting requirements. Use stainless-steel fasteners and mounting bolts unless otherwise indicated.

Coordinate "Mountings, Fasteners, and Appurtenances" Paragraph below with Drawings.

C. Mountings, Fasteners, and Appurtenances: Corrosion-resistant items compatible with support components.

1. Materials: Shall not cause galvanic action at contact points.

2. Anchor Bolts, Leveling Nuts, Bolt Caps, and Washers: Hot-dip galvanized after fabrication unless otherwise indicated.

3. Anchor-Bolt Template: Plywood or steel.

Coordinate "Handhole" Paragraph below with Drawings for indication of concrete foundations suitable for soil conditions and loads imposed by pole, luminaire, and support components.

D. Handhole: Oval-shaped, with minimum clear opening of 2-1/2 by 5 inches (65 by 130 mm), with cover secured by stainless-steel captive screws.[ Provide on all, except wood poles.]

E. Concrete Pole Foundations: Cast in place, with anchor bolts to match pole-base flange. Concrete, reinforcement, and formwork are specified in Section 033000 "Cast-in-Place Concrete."

Coordinate two paragraphs below with Drawings.

F. Power-Installed Screw Foundations: Factory fabricated by pole manufacturer, with structural steel complying with ASTM A 36/A 36M and hot-dip galvanized according to ASTM A 123/A 123M; and with top-plate and mounting bolts to match pole base flange and strength required to support pole, luminaire, and accessories.

On Drawings, identify poles that require breakaway supports described in paragraph below. Add description if specific type of breakaway support is required.

G. Breakaway Supports: Frangible breakaway supports, tested by an independent testing agency acceptable to authorities having jurisdiction, according to AASHTO LTS-4-M.

If using support structures other than poles, insert an article here to specify structure materials.

2.8 STEEL POLES

See Editing Instruction No. 5 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles: Comply with ASTM A 500, Grade B, carbon steel with a minimum yield of 46,000 psig (317 MPa); one-piece construction up to 40 feet (12 m) in height with access handhole in pole wall.

1. Shape: [Round, tapered] [Round, straight] [Square, tapered] [Square, straight].

Coordinate "Mounting Provisions" Subparagraph below with Drawings.

2. Mounting Provisions: Butt flange for bolted mounting on foundation or breakaway support.

Indicate on Drawings the span and rise of mast arms in "Steel Mast Arms" Paragraph below. Delete paragraph if mast arms are adequately described in the Exterior Lighting Device Schedule or in details on Drawings.

B. Steel Mast Arms: [Single-arm] [Truss] [Davit] type, continuously welded to pole attachment plate. Material and finish same as pole.

Indicate on Drawings the span and rise of luminaire brackets in "Brackets for Luminaires" Paragraph below. Delete paragraph if luminaire brackets are adequately described in the Exterior Lighting Device Schedule or in details on Drawings.

C. Brackets for Luminaires: Detachable, cantilever, without underbrace.

1. Adapter fitting welded to pole, allowing the bracket to be bolted to the pole mounted adapter, then bolted together with [stainless] [galvanized]-steel bolts.

2. Cross Section: Tapered oval, with straight tubular end section to accommodate luminaire.

3. Match pole material and finish.

D. Pole-Top Tenons: Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

E. Steps: Fixed steel, with nonslip treads, positioned for 15-inch (381-mm) vertical spacing, alternating on opposite sides of pole; first step at elevation 10 feet (3 m) above finished grade.

F. Grounding and Bonding Lugs: Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Section 260526 "Grounding and Bonding for Electrical Systems," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

G. Cable Support Grip: Wire-mesh type with rotating attachment eye, sized for diameter of cable and rated for a minimum load equal to weight of supported cable times a 5.0 safety factor.

Retain any combination of three paragraphs below that applies to steel poles or other steel support components for this Project. Specify field-painting requirements in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting." Verify compatibility of factory finishes with field-applied coats.

H. Prime-Coat Finish: Manufacturer's standard prime-coat finish ready for field painting.

I. Galvanized Finish: After fabrication, hot-dip galvanize complying with ASTM A 123/A 123M.

Retain "Galvanized Finish" Paragraph above for plain galvanized finish; retain "Factory-Painted Finish" Paragraph below for factory-painted finish.

J. Factory-Painted Finish: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Surface Preparation: Clean surfaces to comply with SSPC-SP 1, "Solvent Cleaning," to remove dirt, oil, grease, and other contaminants that could impair paint bond. Grind welds and polish surfaces to a smooth, even finish. Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1, "White Metal Blast Cleaning," or with SSPC-SP 8, "Pickling."

2. Interior Surfaces of Pole: One coat of bituminous paint, or otherwise treat for equal corrosion protection.

3. Exterior Surfaces: Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

a. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

2.9 ALUMINUM POLES

See Editing Instruction No. 5 in the Evaluations for discussion of pole flexure and vibration resistance.

Retain one of two "Poles" paragraphs below. Retain second paragraph for aluminum poles up to 40 feet (12 m) in nominal mounting height and if higher strength or resistance to vibration is required.

A. Poles: Seamless, extruded structural tube complying with ASTM B 429/B 429M, Alloy 6063-T6 with access handhole in pole wall.

B. Poles: ASTM B 209 (ASTM B 209M), 5052-H34 marine sheet alloy with access handhole in pole wall.

1. Shape: [Round, tapered] [Round, straight] [Square, tapered] [Square, straight].

2. Mounting Provisions: Butt flange for bolted mounting on foundation or breakaway support.

C. Pole-Top Tenons: Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

D. Grounding and Bonding Lugs: Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Section 260526 "Grounding and Bonding for Electrical Systems," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

Revise "Brackets for Luminaires" Paragraph below to suit Project or delete if items are adequately described in the Exterior Lighting Device Schedule or in details on Drawings. Indicate span and rise of luminaire brackets on Drawings.

E. Brackets for Luminaires: Detachable, with pole and adapter fittings of cast aluminum. Adapter fitting welded to pole and bracket, then bolted together with stainless-steel bolts.

1. Tapered oval cross section, with straight tubular end section to accommodate luminaire.

2. Finish: Same as [pole] [luminaire].

Retain one of two "finish" paragraphs below. Specify field-painting requirements in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting." Verify compatibility of factory finishes with field-applied coats.

F. Prime-Coat Finish: Manufacturer's standard prime-coat finish ready for field painting.

G. Aluminum Finish: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain one of four subparagraphs below or revise to suit Project.

2. Natural Satin Finish: Provide fine, directional, medium satin polish (AA-M32); buff complying with AA-M20; and seal aluminum surfaces with clear, hard-coat wax.

3. Class I, Clear Anodic Finish: AA-M32C22A41 (Mechanical Finish: medium satin; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

4. Class I, Color Anodic Finish: AA-M32C22A42/A44 (Mechanical Finish: medium satin; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker) complying with AAMA 611.

5. <Insert finish>.

Retain one color in subparagraph below with any subparagraph above.

a. Color: [Light bronze] [Medium bronze] [Dark bronze] [Black] [As selected by Architect from manufacturer's full range].

2.10 WOOD POLES

See Editing Instruction No. 5 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles: [Douglas fir] [Southern yellow pine], [machine trimmed by turning,] complying with ANSI O5.1 and with AWPA UC4 for wood species used; and bored, roofed, and gained before treatment.

1. Mounting Provisions: Embedded.

B. Preservative Treatment: Pressure treat poles with [creosote] [pentachlorophenol] [ammoniacal copper arsenate] according to AWPA UC4.

Indicate rise and span of luminaire brackets in paragraph below on Drawings.

C. Luminaire Brackets: Comply with ANSI C136.13. Fasteners shall be compatible with chemicals used in preservative treatment.
2.11 POLE ACCESSORIES

Revise this article to suit Project, safety codes, and luminaire servicing methods. Add requirement for removable steps if necessary. Coordinate with the Exterior Lighting Device Schedule on Drawings.

A. Duplex Receptacle: 120 V, 20 A in a weatherproof assembly complying with Section 262726 "Wiring Devices" for ground-fault circuit-interrupter type.

1. [Surface mounted] [Recessed], [12 inches (300 mm)] <Insert dimension> above finished grade.

2. Nonmetallic polycarbonate plastic or reinforced fiberglass, weatherproof in use, cover, <Insert color to match pole,> that when mounted results in NEMA 250, [Type 3R] [Type 4X] enclosure.

3. With cord opening.

4. With lockable hasp and latch that complies with OSHA lockout and tag-out requirements.

B. Minimum 1800-W transformer, protected by replaceable fuses, mounted behind access cover.

Coordinate two "base" paragraphs below with "Breakaway Supports" Paragraph in "General Requirements for Poles and Support Components" Article.

C. Base Covers: Manufacturers' standard metal units, arranged to cover pole's mounting bolts and nuts. Finish same as pole.

D. Transformer Type Base: Same material and color as pole. Coordinate dimensions to suit pole's base flange and accept [ballast(s)] [indicated accessories].

Verify availability of decorative accessories with specified pole manufacturers.

E. Decorative accessories, supplied by decorative pole manufacturer, include the following:

1. Banner Arms: <Insert material>.

2. Flag Holders: <Insert material>.

3. Ladder Rests: <Insert material>.

PART 3 -  EXECUTION

3.1 LUMINAIRE INSTALLATION

A. Install lamps in each luminaire.

B. Fasten luminaire to indicated structural supports.

Retain subparagraph below if seismic restraint is required by local code or authorities having jurisdiction. See Evaluations.

1. Use fastening methods and materials selected to resist seismic forces defined for the application and approved by manufacturer.

C. Adjust luminaires that require field adjustment or aiming.[ Include adjustment of photoelectric device to prevent false operation of relay by artificial light sources, favoring a north orientation.]

3.2 POLE INSTALLATION

Retain "Alignment" Paragraph below if luminaire alignment for desired light distribution depends on alignment of pole.

A. Alignment: Align pole foundations and poles for optimum directional alignment of luminaires and their mounting provisions on the pole.

Coordinate "Clearances" Paragraph below with Drawings and revise to suit Project.

B. Clearances: Maintain the following minimum horizontal distances of poles from surface and underground features unless otherwise indicated on Drawings:

1. Fire Hydrants and Storm Drainage Piping: [60 inches (1520 mm)] <Insert dimension>.

2. Water, Gas, Electric, Communication, and Sewer Lines: [10 feet (3 m)] <Insert dimension>.

3. Trees: [15 feet (5 m)] <Insert dimension> from tree trunk.

4. <Insert features and clearance dimensions>.

Coordinate first five paragraphs below with Drawings. See Evaluations for structural- and soil- engineering coordination.

C. Concrete Pole Foundations: Set anchor bolts according to anchor-bolt templates furnished by pole manufacturer. Concrete materials, installation, and finishing requirements are specified in Section 033000 "Cast-in-Place Concrete."

D. Foundation-Mounted Poles: Mount pole with leveling nuts, and tighten top nuts to torque level recommended by pole manufacturer.

Retain first subparagraph below if seismic restraint is required by local code or authorities having jurisdiction. See Evaluations.

1. Use anchor bolts and nuts selected to resist seismic forces defined for the application and approved by manufacturer.

2. Grout void between pole base and foundation. Use nonshrink or expanding concrete grout firmly packed to fill space.

3. Install base covers unless otherwise indicated.

4. Use a short piece of 1/2-inch- (13-mm-) diameter pipe to make a drain hole through grout. Arrange to drain condensation from interior of pole.

Retain one of first two paragraphs below for embedded poles and coordinate with Drawings.

E. Embedded Poles with Tamped Earth Backfill: Set poles to depth below finished grade indicated on Drawings, but not less than one-sixth of pole height.

1. Dig holes large enough to permit use of tampers in the full depth of hole.

2. Backfill in 6-inch (150-mm) layers and thoroughly tamp each layer so compaction of backfill is equal to or greater than that of undisturbed earth.

F. Embedded Poles with Concrete Backfill: Set poles in augered holes to depth below finished grade indicated on Drawings, but not less than one-sixth of pole height.

1. Make holes 6 inches (150 mm) in diameter larger than pole diameter.

2. Fill augered hole around pole with air-entrained concrete having a minimum compressive strength of 3000 psi (20 MPa) at 28 days, and finish in a dome above finished grade.

3. Use a short piece of 1/2-inch- (13-mm-) diameter pipe to make a drain hole through concrete dome. Arrange to drain condensation from interior of pole.

4. Cure concrete a minimum of 72 hours before performing work on pole.

For projects in seismic areas, retain first paragraph below to minimize possible concentration of horizontal forces during seismic events where poles or pole foundations meet the finished grade.

G. Poles and Pole Foundations Set in Concrete Paved Areas: Install poles with minimum of 6-inch- (150-mm-) wide, unpaved gap between the pole or pole foundation and the edge of adjacent concrete slab. Fill unpaved ring with [pea gravel] <Insert material> to a level 1 inch (25 mm) below top of concrete slab.

H. Raise and set poles using web fabric slings (not chain or cable).

3.3 BOLLARD LUMINAIRE INSTALLATION

A. Align units for optimum directional alignment of light distribution.

Retain paragraph below if bollards require protection from damage at base due to landscaping maintenance or snow removal operations. Coordinate with Drawings.

B. Install on concrete base with top [4 inches (100 mm)] <Insert dimension> above finished grade or surface at bollard location. Cast conduit into base, and shape base to match shape of bollard base. Finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Section 033000 "Cast-in-Place Concrete."

3.4 INSTALLATION OF INDIVIDUAL GROUND-MOUNTING LUMINAIRES

Coordinate this article with Drawings. Delete if installation is detailed on Drawings.

A. Install on concrete base with top [4 inches (100 mm)] <Insert dimension> above finished grade or surface at luminaire location. Cast conduit into base, and finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Section 033000 "Cast-in-Place Concrete."

3.5 CORROSION PREVENTION

A. Aluminum: Do not use in contact with earth or concrete. When in direct contact with a dissimilar metal, protect aluminum by insulating fittings or treatment.

B. Steel Conduits: Comply with Section 260533 "Raceways and Boxes for Electrical Systems." In concrete foundations, wrap conduit with 0.010-inch- (0.254-mm-) thick, pipe-wrapping plastic tape applied with a 50 percent overlap.

3.6 GROUNDING

Coordinate first paragraph below with Drawings.

A. Ground metal poles and support structures according to Section 260526 "Grounding and Bonding for Electrical Systems."

1. Install grounding electrode for each pole unless otherwise indicated.

2. Install grounding conductor pigtail in the base for connecting luminaire to grounding system.

B. Ground nonmetallic poles and support structures according to Section 260526 "Grounding and Bonding for Electrical Systems."

Retain first subparagraph below if lightning damage is of concern.

1. Install grounding electrode for each pole.

2. Install grounding conductor and conductor protector.

3. Ground metallic components of pole accessories and foundations.

END OF SECTION 265600

	EXTERIOR LIGHTING
	265600 - 8



