Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 270528 - PATHWAYS FOR COMMUNICATIONS SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Metal conduits and fittings.

2. Nonmetallic conduits and fittings.

3. Optical-fiber-cable pathways and fittings.

4. Surface pathways.

5. Boxes, enclosures, and cabinets.

6. Handholes and boxes for exterior underground cabling.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 260533 "Raceways and Boxes for Electrical Systems" for conduits, wireways, surface raceways, boxes, enclosures, cabinets, handholes, and faceplate adapters serving electrical systems.

2. Section 280528 "Pathways for Electronic Safety and Security" for conduits, surface pathways, innerduct, boxes, and faceplate adapters serving electronic safety and security.

1.2 ACTION SUBMITTALS

A. Product Data: For surface pathways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

B. LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for solvent cements and adhesive primers.

1. Product Data for Credit IEQ 4.1: For solvent cements and adhesive primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

2. Laboratory Test Reports for Credit IEQ 4: For solvent cements and adhesive primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Retain "Shop Drawings" Paragraph below for custom enclosures only.

C. Shop Drawings: For custom enclosures and cabinets.

1.3 INFORMATIONAL SUBMITTALS

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For pathway racks, enclosures, cabinets, equipment racks and their mounting provisions, including those for internal components, from manufacturer.

PART 2 -  PRODUCTS

2.1 METAL CONDUITS AND FITTINGS

A. General Requirements for Metal Conduits and Fittings:

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Comply with TIA-569-B.

B. GRC: Comply with ANSI C80.1 and UL 6.

Retain "ARC" Paragraph below for corrosion resistance and other special conditions.

C. ARC: Comply with ANSI C80.5 and UL 6A.

D. EMT: Comply with ANSI C80.3 and UL 797.

E. Fittings for Metal Conduit: Comply with NEMA FB 1 and UL 514B.

Coordinate "Conduit Fittings for Hazardous (Classified) Locations" Subparagraph below with Drawings.

1. Conduit Fittings for Hazardous (Classified) Locations: Comply with UL 886 and NFPA 70.

2. Fittings for EMT:

a. Material: [Steel] [or] [die cast].

b. Type: [Setscrew] [or] [compression].

3. Expansion Fittings: PVC or steel to match conduit type, complying with UL-467, rated for environmental conditions where installed, and including flexible external bonding jumper.

Retain "Joint Compound for GRC or ARC" Paragraph below to require some threaded joints of GRC, ARC, or their fittings, to be treated with joint compound for improved conductivity, resistance to oxidation, or ease of assembly and disassembly.

F. Joint Compound for GRC or ARC: Approved, as defined in NFPA 70, by authorities having jurisdiction for use in conduit assemblies, and compounded for use to lubricate and protect threaded conduit joints from corrosion and to enhance their conductivity.

2.2 NONMETALLIC CONDUITS AND FITTINGS

A. General Requirements for Nonmetallic Conduits and Fittings:

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Comply with TIA-569-B.

See Evaluations for descriptions of nonmetallic conduit types.

B. RNC: Type EPC-40-PVC, complying with NEMA TC 2 and UL 651 unless otherwise indicated.

C. Continuous HDPE: Comply with UL 651B.

D. Fittings for RNC: Comply with NEMA TC 3; match to conduit or tubing type and material.

Retain first paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1. VOC limit is that for PVC welding compounds and adhesive primers for plastic.

E. Solvent cements and adhesive primers shall have a VOC content of 510 and 550 g/L or less, respectively, when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain paragraph below if required for LEED for Schools Credit IEQ 4.

F. Solvent cements and adhesive primers shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

2.3 OPTICAL-FIBER-CABLE PATHWAYS AND FITTINGS

Retain this article to specify special-purpose, flexible, nonmetallic pathways permitted by NFPA 70 in its "Optical Fiber Cables and Raceways" and "Communications Circuits" articles. See Evaluations.

In "Description" Paragraph below, if retaining more than one type of pathway, indicate extent and location of each type on Drawings.

A. Description: Comply with UL 2024; flexible-type pathway, approved for [plenum] [riser] [or] [general-use] installation unless otherwise indicated.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Comply with TIA-569-B.

2.4 SURFACE PATHWAYS

A. General Requirements for Surface Pathways:

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Comply with TIA-569-B.

Insert requirements for finish-coat paint color, if applicable, in "Surface Metal Pathways" Paragraph below. See Section 099123 "Interior Painting" for optional field-finish coats.

B. Surface Metal Pathways: Galvanized steel with snap-on covers complying with UL 5. Manufacturer's standard enamel finish.

C. Surface Nonmetallic Pathways: Two- or three-piece construction, complying with UL 5A, and manufactured of rigid PVC with texture and color selected by Architect from manufacturer's standard colors. Product shall comply with UL-94 V-0 requirements for self-extinguishing characteristics.

D. Tele-Power Poles:

1. Material: [Galvanized steel with baked-enamel finish] [Aluminum with clear anodized finish].

2. Fittings and Accessories: Dividers, end caps, covers, cutouts, wiring harnesses, devices, mounting materials, and other fittings shall match and mate with tele-power pole as required for complete system.

2.5 BOXES, ENCLOSURES, AND CABINETS

A. General Requirements for Boxes, Enclosures, and Cabinets:

1. Comply with TIA-569-B.

2. Boxes, enclosures and cabinets installed in wet locations shall be listed for use in wet locations.

B. Sheet-Metal Outlet and Device Boxes: Comply with NEMA OS 1 and UL 514A.

In "Cast-Metal Outlet and Device Boxes" Paragraph below, aluminum boxes are suitable for use with steel pathways in most environments. Type FD is a device box with extra depth. Many other configurations are available.

C. Cast-Metal Outlet and Device Boxes: Comply with NEMA FB 1, [ferrous alloy] [aluminum], Type FD, with gasketed cover.

D. Box extensions used to accommodate new building finishes shall be of same material as recessed box.

See Editing Instruction No. 2 in the Evaluations for a discussion of floor boxes.

E. Metal Floor Boxes:

1. Material: [Cast metal] [or] [sheet metal].

2. Type: [Fully adjustable] [Semi-adjustable].

3. Listing and Labeling: Metal floor boxes shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

F. Nonmetallic Floor Boxes: Nonadjustable, [round] [rectangular].

1. Listing and Labeling: Nonmetallic floor boxes shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

G. Small Sheet Metal Pull and Junction Boxes: NEMA OS 1.

H. Cast-Metal Access, Pull, and Junction Boxes: Comply with NEMA FB 1 and UL 1773, [cast aluminum] [galvanized, cast iron] with gasketed cover.

I. Device Box Dimensions: [4 inches square by 2-1/8 inches deep (100 mm square by 60 mm deep)] [4 inches by 2-1/8 inches by 2-1/8 inches deep (100 mm by 60 mm by 60 mm deep)] <Insert other dimension>.

J. Gangable boxes are prohibited.

K. Nonmetallic Outlet and Device Boxes: Comply with NEMA OS 2 and UL 514C.

Coordinate "Hinged-Cover Enclosures" Paragraph below with Drawings if hinged cover enclosures other than NEMA 250, Type 1 are required, such as for very dusty areas; or if consideration should be given to use of NEMA 250, Type 3R or Type 12 enclosures.

L. Hinged-Cover Enclosures: Comply with UL 50 and NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12] <Insert type> with continuous-hinge cover with flush latch unless otherwise indicated.

1. Metal Enclosures: Steel, finished inside and out with manufacturer's standard enamel.

2. Nonmetallic Enclosures: Plastic or fiberglass[ finished inside with radio-frequency-resistant paint].

3. Interior Panels: Steel; all sides finished with manufacturer's standard enamel.

M. Cabinets:

1. NEMA 250, [Type 1] [Type 3R] [Type 12] <Insert type>, galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

2. Hinged door in front cover with flush latch and concealed hinge.

3. Key latch to match panelboards.

4. Metal barriers to separate wiring of different systems and voltage.

5. Accessory feet where required for freestanding equipment.

6. Nonmetallic cabinets shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.6 HANDHOLES AND BOXES FOR EXTERIOR UNDERGROUND CABLING

See Editing Instruction No. 3 in the Evaluations. Verify with manufacturers that units of types specified are available in sizes required. Indicate the size of each enclosure on Drawings, and use a symbol or other notation to differentiate between handholes and pull boxes.

A. General Requirements for Handholes and Boxes:

1. Boxes and handholes for use in underground systems shall be designed and identified as defined in NFPA 70, for intended location and application.

2. Boxes installed in wet areas shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

3. Comply with TIA-569-B.

Retain one or more of three paragraphs below to select enclosure type(s) for areas not subject to traffic by vehicles. Indicate location of each type in "Pathway Application" Article. For enclosures with cover options, verify that selected cover is available with load rating specified in "Pathway Application" Article. If retaining more than one type of box and cover combination, indicate location of each type on Drawings.

B. Polymer-Concrete Handholes and Boxes with Polymer-Concrete Cover: Molded of sand and aggregate, bound together with polymer resin, and reinforced with steel, fiberglass, or a combination of the two.

1. Standard: Comply with SCTE 77.

First option in "Configuration" Subparagraph below facilitates bottom conduit entry. Second option may be provided by a separate slab placed in the excavation under an open-bottom enclosure; third option is obtained by molding or fabricating the bottom integrally with the body of unit.

2. Configuration: Designed for flush burial with [open] [closed] [integral closed] bottom unless otherwise indicated.

3. Cover: Weatherproof, secured by tamper-resistant locking devices and having structural load rating consistent with enclosure and handhole location.

4. Cover Finish: Nonskid finish shall have a minimum coefficient of friction of 0.50.

5. Cover Legend: Molded lettering, ["COMMUNICATIONS."] <Insert legend>.

C. Fiberglass Handholes and Boxes: Molded of fiberglass-reinforced polyester resin, with frame and covers of [polymer concrete] [reinforced concrete] [cast iron] [hot-dip galvanized-steel diamond plate] [fiberglass].

1. Standard: Comply with SCTE 77.

Retain "Color of Frame and Cover" Subparagraph below if choosing a metal frame and cover; otherwise, delete.

2. Color of Frame and Cover: [Gray] [Green].

First option in "Configuration" Subparagraph below facilitates bottom conduit entry. Second option may be provided by a separate slab placed in the excavation under an open-bottom enclosure; third option is obtained by molding or fabricating the bottom integrally with the body of unit.

3. Configuration: Designed for flush burial with [open] [closed] [integral closed] bottom unless otherwise indicated.

4. Cover: Weatherproof, secured by tamper-resistant locking devices and having structural load rating consistent with enclosure and handhole location.

5. Cover Finish: Nonskid finish shall have a minimum coefficient of friction of 0.50.

6. Cover Legend: Molded lettering, ["COMMUNICATIONS."] <Insert legend>.

PART 3 -  EXECUTION

3.1 PATHWAY APPLICATION

Retain this article to specify the type of pathway to be installed. Coordinate with cabling methods specified in Section 271300 "Communications Backbone Cabling" and Section 271500 "Communications Horizontal Cabling" and in other Sections. See "Writing Guide" Article in the Evaluations for instructions on revising this article.

A. Outdoors: Apply pathway products as specified below unless otherwise indicated:

1. Exposed Conduit: [GRC] [RNC, Type EPC-40-PVC] [RNC, Type EPC-80-PVC].

2. Concealed Conduit, Aboveground: [GRC] [EMT] [RNC, Type EPC-40-PVC].

3. Underground Conduit: RNC, [Type EPC-40-PVC] [Type EPC-80-PVC], [direct buried] [concrete encased].

4. Boxes and Enclosures, Aboveground: NEMA 250, [Type 3R] [Type 4].

B. Indoors: Apply pathway products as specified below unless otherwise indicated:

1. Exposed, Not Subject to Physical Damage: [EMT] [or] [RNC].

2. Exposed, Not Subject to Severe Physical Damage: [EMT] [RNC identified for such use].

3. Exposed and Subject to Severe Physical Damage: GRC.

4. Concealed in Ceilings and Interior Walls and Partitions: [EMT] [RNC, Type EPC-40-PVC] [or] [innerduct].

5. Damp or Wet Locations: GRC.

6. Pathways for Optical-Fiber or Communications Cable in Spaces Used for Environmental Air: [Plenum-type, optical-fiber-cable pathway] [Plenum-type, communications-cable pathway] [EMT] <Insert pathway type>.

7. Pathways for Optical-Fiber or Communications-Cable Risers in Vertical Shafts: [Riser-type, optical-fiber-cable pathway] [Riser-type, communications-cable pathway] [EMT] <Insert pathway type>.

8. Pathways for Concealed General-Purpose Distribution of Optical-Fiber or Communications Cable: [General-use, optical-fiber-cable pathway] [Riser-type, optical-fiber-cable pathway] [Plenum-type, optical-fiber-cable pathway] [General-use, communications-cable pathway] [Riser-type, communications-cable pathway] [Plenum-type, communications-cable pathway] [EMT] <Insert pathway type>.

9. Boxes and Enclosures: NEMA 250 Type 1, except use NEMA 250 Type 4 [stainless steel] [nonmetallic] in institutional and commercial kitchens and damp or wet locations.

C. Minimum Pathway Size: 3/4-inch (21-mm) trade size. Minimum size for optical-fiber cables is 1 inch (27 mm).

D. Pathway Fittings: Compatible with pathways and suitable for use and location.

1. Rigid Steel Conduit: Use threaded rigid steel conduit fittings unless otherwise indicated. Comply with NEMA FB 2.10.

2. EMT: Use [setscrew] [or] [compression], [steel] [cast-metal] fittings. Comply with NEMA FB 2.10.

E. Do not install aluminum conduits, boxes, or fittings in contact with concrete or earth.

Coordinate first paragraph below with Drawings.

F. Install surface pathways only where indicated on Drawings.

G. Do not install nonmetallic conduit where ambient temperature exceeds [120 deg F (49 deg C)] <Insert temperature>.

3.2 INSTALLATION

A. Comply with NECA 1, NECA 101, and TIA-569-B for installation requirements except where requirements on Drawings or in this article are stricter. Comply with NECA 102 for aluminum pathways. Comply with NFPA 70 limitations for types of pathways allowed in specific occupancies and number of floors.

B. Keep pathways at least 6 inches (150 mm) away from parallel runs of flues and steam or hot-water pipes. Install horizontal pathway runs above water and steam piping.

C. Comply with requirements in Section 260529 "Hangers and Supports for Electrical Systems" for hangers and supports.

D. Arrange stub-ups so curved portions of bends are not visible above finished slab.

First paragraph below is more restrictive than NFPA 70, which permits up to four quarter bends in a conduit run. Retain paragraph for more conservative design, in compliance with TIA-569-B, with less stress being placed on conductors being pulled in.

E. Install no more than the equivalent of two 90-degree bends in any pathway run. Support within 12 inches (300 mm) of changes in direction. Utilize long radius ells for all optical-fiber cables.

F. Conceal conduit and EMT within finished walls, ceilings, and floors unless otherwise indicated. Install conduits parallel or perpendicular to building lines.

G. Pathways Embedded in Slabs:

1. Run conduit larger than 1-inch (27-mm) trade size, parallel or at right angles to main reinforcement. Where at right angles to reinforcement, place conduit close to slab support. Secure pathways to reinforcement at maximum 10-foot (3-m) intervals.

2. Arrange pathways to cross building expansion joints at right angles with expansion fittings.

3. Arrange pathways to keep a minimum of [1 inch (25 mm)] [2 inches (50 mm)] <Insert dimension> of concrete cover in all directions.

4. Do not embed threadless fittings in concrete unless specifically approved by Architect for each specific location.

H. Stub-ups to Above Recessed Ceilings:

1. Use a conduit bushing or insulated fitting to terminate stub-ups not terminated in hubs or in an enclosure.

I. Coat field-cut threads on PVC-coated pathway with a corrosion-preventing conductive compound prior to assembly.

Retain one of first two paragraphs below to exceed NFPA 70 requirements. NFPA 70 does not require insulated bushings for communications cables, but TIA-569-B does.

J. Terminate threaded conduits into threaded hubs or with locknuts on inside and outside of boxes or cabinets. Install insulated bushings on conduits terminated with locknuts.

K. Install pathways square to the enclosure and terminate at enclosures with locknuts. Install locknuts hand tight plus 1/4 turn more.

L. Do not rely on locknuts to penetrate nonconductive coatings on enclosures. Remove coatings in the locknut area prior to assembling conduit to enclosure to assure a continuous ground path.

M. Spare Pathways: Install pull wires in empty pathways. Cap underground pathways designated as spare above grade alongside pathways in use.

Retain "Surface Pathways" Paragraph below if applicable.

N. Surface Pathways:

1. Install surface pathway for surface telecommunications outlet boxes only where indicated on Drawings.

"Pathways for Optical-Fiber and Communications Cable" Paragraph below is applicable for EMT, RMC, RNC, and optical-fiber and communications-cable pathways.

O. Pathways for Optical-Fiber and Communications Cable: Install pathways as follows:

1. 3/4-Inch (21-mm) Trade Size and Smaller: Install pathways in maximum lengths of 50 feet (15 m).

2. 1-Inch (27-mm) Trade Size and Larger: Install pathways in maximum lengths of 75 feet (23 m).

3. Install with a maximum of two 90-degree bends or equivalent for each length of pathway unless Drawings show stricter requirements.

P. Install pathway sealing fittings at accessible locations according to NFPA 70 and fill them with listed sealing compound.

See Evaluations for discussion of types of and locations for pathway seals.

Q. Locate seals so no fittings or boxes are between the seal and the following changes of environments. Seal the interior of all pathways at the following points:

1. Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

2. Where an underground service pathway enters a building or structure.

3. Where otherwise required by NFPA 70.

Retain "Expansion-Joint Fittings" Paragraph below unless locations for expansion fittings for PVC conduits are indicated on Drawings. See Evaluations.

R. Expansion-Joint Fittings:

1. Install in each run of aboveground RNC that is located where environmental temperature change may exceed 30 deg F (17 deg C), and that has straight-run length that exceeds 25 feet (7.6 m). Install in each run of aboveground RMC[ and EMT] conduit that is located where environmental temperature change may exceed 100 deg F (55 deg C) and that has straight-run length that exceeds 100 feet (30 m).

2. Install type and quantity of fittings that accommodate temperature change listed for each of the following locations:

Revise list below to include all locations in Project with environmental conditions that require considering expansion-joint fittings in conduit runs. For each Project, consider only locations with PVC conduit with straight-run length exceeding 25 feet (7.6 m) or metal conduit in lengths over 100 feet (30 m). Also revise temperature change for each location so it safely represents conditions anticipated. Temperature-change figures below are examples of maximum total swings from the lowest to the highest environmental temperatures at the indicated types of locations and must be revised to represent temperature swings or changes that may occur at Project locations.

a. Outdoor Locations Not Exposed to Direct Sunlight: [125 deg F (70 deg C)] <Insert temperature> temperature change.

b. Outdoor Locations Exposed to Direct Sunlight: [155 deg F (86 deg C)] <Insert temperature> temperature change.

c. Indoor Spaces Connected with Outdoors without Physical Separation: [125 deg F (70 deg C)] <Insert temperature> temperature change.

d. Attics: [135 deg F (75 deg C)] <Insert temperature> temperature change.

e. <Insert location and corresponding temperature change>.

Formula in first subparagraph below provides about 15 percent safety factor (extra expansion-contraction capability).

3. Install fitting(s) that provide expansion and contraction for at least 0.00041 inch per foot of length of straight run per deg F (0.06 mm per meter of length of straight run per deg C) of temperature change for PVC conduits. Install fitting(s) that provide expansion and contraction for at least 0.000078 inch per foot of length of straight run per deg F (0.0115 mm per meter of length of straight run per deg C) of temperature change for metal conduits.

4. Install expansion fittings at all locations where conduits cross building or structure expansion joints.

5. Install each expansion-joint fitting with position, mounting, and piston setting selected according to manufacturer's written instructions for conditions at specific location at time of installation. Install conduit supports to allow for expansion movement.

S. Mount boxes at heights indicated on Drawings in accordance with ADA requirements. Install boxes with height measured to [center] [top] [bottom] of box unless otherwise indicated.

T. Horizontally separate boxes mounted on opposite sides of walls so they are not in the same vertical channel.

3.3 INSTALLATION OF UNDERGROUND CONDUIT

Retain this article if Project includes small amounts of exterior underground cabling 600 V and less. Delete if Section 260543 "Underground Ducts and Raceways for Electrical Systems" is included in the Project Manual.

A. Direct-Buried Conduit:

1. Excavate trench bottom to provide firm and uniform support for conduit. Prepare trench bottom as specified in Section 312000 "Earth Moving" for pipe less than 6 inches (150 mm) in nominal diameter.

2. Install backfill as specified in Section 312000 "Earth Moving."

3. After installing conduit, backfill and compact. After placing controlled backfill to within 12 inches (300 mm) of finished grade, make final conduit connection at end of run and complete backfilling with normal compaction as specified in Section 312000 "Earth Moving."

4. Install manufactured rigid steel conduit elbows for stub-ups at poles and equipment and at building entrances through floor.

a. Couple steel conduits to ducts with adapters designed for this purpose, and encase coupling with 3 inches (75 mm) of concrete for a minimum of 12 inches (300 mm) on each side of the coupling.

b. For stub-ups at equipment mounted on outdoor concrete bases and where conduits penetrate building foundations, extend steel conduit horizontally a minimum of 60 inches (1500 mm) from edge of foundation or equipment base. Install insulated grounding bushings on terminations at equipment.

5. Underground Warning Tape: Comply with requirements in Section 260553 "Identification for Electrical Systems."

3.4 INSTALLATION OF UNDERGROUND HANDHOLES AND BOXES

Retain this article if Project includes small amounts of exterior underground cabling 600 V and less. Delete if Section 260543 "Underground Ducts and Raceways for Electrical Systems" is included in the Project Manual. See Editing Instruction No. 3 in the Evaluations.

A. Install handholes and boxes level and plumb and with orientation and depth coordinated with connecting conduits to minimize bends and deflections required for proper entrances.

B. Elevation: In paved areas, set so cover surface will be flush with finished grade. Set covers of other enclosures 1 inch (25 mm) above finished grade.

C. Install handholes with bottom below frost line, <Insert depth of frost line below grade at Project site> below grade.

Delete paragraph below if conduits enter enclosure through open bottom.

D. Field cut openings for conduits according to enclosure manufacturer's written instructions.

3.5 SLEEVE AND SLEEVE-SEAL INSTALLATION FOR COMMUNICATIONS PENETRATIONS

A. Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 270544 "Sleeves and Sleeve Seals for Communications Pathways and Cabling."

3.6 FIRESTOPPING

A. Install firestopping at penetrations of fire-rated floor and wall assemblies. Comply with requirements in Section 078413 "Penetration Firestopping."

3.7 PROTECTION

A. Protect coatings, finishes, and cabinets from damage or deterioration.

END OF SECTION 270528

	PATHWAYS FOR COMMUNICATIONS SYSTEMS
	270528 - 1



