Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 271100 - COMMUNICATIONS EQUIPMENT ROOM FITTINGS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Telecommunications mounting elements.

2. Backboards.

3. Telecommunications equipment racks and cabinets.

4. Grounding.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 270536 "Cable Trays for Communications Systems" for cable trays and accessories.

2. Section 271300 "Communications Backbone Cabling" for voice and data cabling associated with system panels and devices.

3. Section 271500 "Communications Horizontal Cabling" for voice and data cabling associated with system panels and devices.

4. Section 280513 "Conductors and Cables for Electronic Safety and Security" for voice and data cabling associated with system panels and devices.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For communications equipment room fittings. Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

3. Grounding: Indicate location of grounding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

1.3 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For [Installer, ]qualified layout technician, installation supervisor, and field inspector.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying telecommunications equipment supports and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For equipment frames from manufacturer.

1.4 QUALITY ASSURANCE

BICSI is an industry trade association. See Editing Instruction No. 2 in the Evaluations for summaries of qualifications for registration.

A. Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

1. Layout Responsibility: Preparation of Shop Drawings shall be under the direct supervision of [RCDD] [RCDD/NTS] [Commercial Installer, Level 2].

2. Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

3. Field Inspector: Currently registered by BICSI as [RCDD] [Commercial Installer, Level 2] to perform the on-site inspection.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

A. Seismic Performance: Equipment frames shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2.2 BACKBOARDS

A. Backboards: Plywood, [fire-retardant treated, ]3/4 by 48 by 96 inches (19 by 1220 by 2440 mm). Comply with requirements for plywood backing panels specified in Section 061000 "Rough Carpentry."

2.3 EQUIPMENT FRAMES

Delete this article if all cross-connects and patch panels are mounted on backboards.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. ADC.

2. Belden Inc.

3. Cooper B-Line.

4. Emerson Network Power Connectivity Solutions.

5. Hubbell Premise Wiring.

6. Leviton Commercial Networks Division.

7. Middle Atlantic Products, Inc.

8. Ortronics, Inc.

9. Panduit Corp.

10. Siemon Co. (The).

11. Tyco Electronics Corporation; AMP Products.

12. <Insert manufacturer's name>.

C. General Frame Requirements:

1. Distribution Frames: Freestanding and wall-mounting, modular-steel units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

2. Module Dimension: Width compatible with EIA 310-D standard, 19-inch (480-mm) panel mounting.

3. Finish: Manufacturer's standard, baked-polyester powder coat.

D. Floor-Mounted Racks: Modular-type, [steel] [or] [aluminum] construction.

1. Vertical and horizontal cable management channels, top and bottom cable troughs, grounding lug[, and a power strip].

2. Baked-polyester powder coat finish.

E. Modular Freestanding Cabinets:

1. Removable and lockable side panels.

2. Hinged and lockable front and rear doors.

3. Adjustable feet for leveling.

4. Screened ventilation openings in the roof and rear door.

5. Cable access provisions in the roof and base.

6. Grounding bus bar.

7. [Rack] [Roof]-mounted, 550-cfm (260-L/s) fan with filter.

8. Power strip.

9. Baked-polyester powder coat finish.

10. All cabinets keyed alike.

F. Modular Wall Cabinets:

1. Wall mounting.

2. [Steel] [Aluminum] [Steel or aluminum] construction.

3. Treated to resist corrosion.

4. Lockable front[ and rear] doors.

5. Louvered side panels.

6. Cable access provisions top and bottom.

7. Grounding lug.

8. [Rack] [Roof]-mounted, 250-cfm (118-L/s) fan.

9. Power strip.

10. All cabinets keyed alike.

G. Cable Management for Equipment Frames:

1. Metal, with integral wire retaining fingers.

2. Baked-polyester powder coat finish.

3. Vertical cable management panels shall have front and rear channels, with covers.

4. Provide horizontal crossover cable manager at the top of each relay rack, with a minimum height of two rack units each.

2.4 POWER STRIPS

A. Power Strips: Comply with UL 1363.

1. Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2. Rack mounting.

3. [Six] <Insert number>, [15-A, 120-V ac, NEMA WD 6, Configuration 5-15R] [20-A, 120-V ac, NEMA WD 6, Configuration 5-20R] receptacles.

4. LED indicator lights for power and protection status.

5. LED indicator lights for reverse polarity and open outlet ground.

Retain one of first two subparagraphs below.

6. Circuit Breaker and Thermal Fusing: When protection is lost, circuit opens and cannot be reset.

7. Circuit Breaker and Thermal Fusing: Unit continues to supply power if protection is lost.

8. [Close-coupled, direct plug-in] [Cord connected with 15-foot (4.5-m)] line cord.

9. Rocker-type on-off switch, illuminated when in on position.

Retain two subparagraphs below if power strips contain surge protection. In first subparagraph, retain 33 kA for high exposure and cost, 26 kA for medium exposure and cost, and 13 kA for low exposure and cost.

10. Peak Single-Impulse Surge Current Rating: [33] [26] [13] kA per phase.

11. Protection modes shall be line to neutral, line to ground, and neutral to ground. UL 1449 clamping voltage for all three modes shall be not more than [330 V] <Insert value>.

2.5 GROUNDING

A. Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems" for grounding conductors and connectors.

B. Telecommunications Main Bus Bar:

1. Connectors: Mechanical type, cast silicon bronze, solderless [compression] [exothermic]-type wire terminals, and long-barrel, two-bolt connection to ground bus bar.

2. Ground Bus Bar: Copper, minimum 1/4 inch thick by 4 inches wide (6 mm thick by 100 mm wide) with 9/32-inch (7.14-mm) holes spaced 1-1/8 inches (28 mm) apart.

3. Stand-Off Insulators: Comply with UL 891 for use in switchboards, 600 V. Lexan or PVC, impulse tested at 5000 V.

C. Comply with J-STD-607-A.

2.6 LABELING

A. Comply with TIA/EIA-606-A and UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

PART 3 -  EXECUTION

3.1 ENTRANCE FACILITIES

Retain first paragraph below if demarcation point and service entrance cabling are by telecommunications service provider.

A. Contact telecommunications service provider and arrange for installation of demarcation point, protected entrance terminals, and a housing when so directed by service provider.

B. Comply with requirements in Section 270528 "Pathways for Communications Systems" for materials and installation requirements for [underground] [buried] [aerial] pathways.

3.2 INSTALLATION

A. Comply with NECA 1.

B. Comply with BICSI TDMM for layout and installation of communications equipment rooms.

C. Bundle, lace, and train conductors and cables to terminal points without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

Revise two paragraphs below to specify coordination with other parties involved in finalizing communications equipment room work. See Editing Instruction No. 3 in the Evaluations.

D. Coordinate layout and installation of communications equipment with Owner's telecommunications and LAN equipment and service suppliers. Coordinate service entrance arrangement with local exchange carrier.

1. Meet jointly with telecommunications and LAN equipment suppliers, local exchange carrier representatives, and Owner to exchange information and agree on details of equipment arrangements and installation interfaces.

2. Record agreements reached in meetings and distribute them to other participants.

3. Adjust arrangements and locations of distribution frames, cross-connects, and patch panels in equipment rooms to accommodate and optimize arrangement and space requirements of telephone switch and LAN equipment.

4. Adjust arrangements and locations of equipment with distribution frames, cross-connects, and patch panels of cabling systems of other communications, electronic safety and security, and related systems that share space in the equipment room.

E. Coordinate location of power raceways and receptacles with locations of communications equipment requiring electrical power to operate.

3.3 SLEEVE AND SLEEVE SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 270544 "Sleeves and Sleeve Seals for Communications Pathways and Cabling."

3.4 FIRESTOPPING

A. Comply with requirements in Section 078413 "Penetration Firestopping."

B. Comply with TIA-569-B, Annex A, "Firestopping."

C. Comply with BICSI TDMM, "Firestopping Systems" Article.

3.5 GROUNDING

A. Install grounding according to BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

B. Comply with J-STD-607-A.

C. Locate grounding bus bar to minimize the length of bonding conductors. Fasten to wall allowing at least 2-inch (50-mm) clearance behind the grounding bus bar. Connect grounding bus bar with a minimum No. 4 AWG grounding electrode conductor from grounding bus bar to suitable electrical building ground.

D. Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

Retain subparagraph below if screened twisted-pair cables and coaxial cables are in communications equipment rooms.

1. Bond the shield of shielded cable to the grounding bus bar in communications rooms and spaces.

3.6 IDENTIFICATION

A. Identify system components, wiring, and cabling complying with TIA/EIA-606-A. Comply with requirements in Division 26 Section "Identification for Electrical Systems."

B. Comply with requirements in Division 09 Section "Interior Painting" for painting backboards. For fire-resistant plywood, do not paint over manufacturer's label.

See Division 27 Section "Communications Horizontal Cabling" for additional identification requirements. See Evaluations for discussion of TIA/EIA standard as it applies to this Section.

C. Paint and label colors for equipment identification shall comply with TIA/EIA-606-A for [Class 2] [Class 3] [Class 4] level of administration[ including optional identification requirements of this standard].

D. Labels shall be preprinted or computer-printed type.

END OF SECTION 271100

	COMMUNICATIONS EQUIPMENT ROOM FITTINGS
	271100 - 1



