Copyright 2010 AIA
MasterSpec Professional
12/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 271500 - COMMUNICATIONS HORIZONTAL CABLING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. UTP cabling.

2. Multiuser telecommunications outlet assemblies.

3. Cable connecting hardware, patch panels, and cross-connects.

4. Telecommunications outlet/connectors.

5. Cabling system identification products.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 271300 "Communications Backbone Cabling" for voice and data cabling associated with system panels and devices.

2. Section 280513 "Conductors and Cables for Electronic Safety and Security" for voice and data cabling associated with system panels and devices.

1.2 ADMINISTRATIVE REQUIREMENTS

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work. See Editing Instruction No. 3 in the Evaluations.

A. Coordinate layout and installation of telecommunications cabling with Owner's telecommunications and LAN equipment and service suppliers.

B. Coordinate telecommunications outlet/connector locations with location of power receptacles at each work area.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings:

1. System Labeling Schedules: Electronic copy of labeling schedules that are part of the cabling and asset identification system of the software.

2. Wiring diagrams to show typical wiring schematics, including the following:

a. Cross-connects.

b. Patch panels.

c. Patch cords.

3. Cross-connects and patch panels. Detail mounting assemblies, and show elevations and physical relationship between the installed components.

1.4 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For [Installer, ]qualified layout technician, installation supervisor, and field inspector.

B. Source quality-control reports.

C. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Maintenance data.

1.6 QUALITY ASSURANCE

BICSI is an industry trade association. See Editing Instruction No. 2 in the Evaluations for summaries of qualifications for registration.

A. Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

1. Layout Responsibility: Preparation of Shop Drawings[ and Cabling Administration Drawings][, Cabling Administration Drawings, and field testing program development] by an RCDD.

2. Installation Supervision: Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

1.7 DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, cables should be tested upon receipt.

A. Test cables upon receipt at Project site. Test each pair of UTP cable for open and short circuits.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 HORIZONTAL CABLING DESCRIPTION

A. Horizontal cable and its connecting hardware provide the means of transporting signals between the telecommunications outlet/connector and the horizontal cross-connect located in the communications equipment room. This cabling and its connecting hardware are called a "permanent link," a term that is used in the testing protocols.

1. TIA/EIA-568-B.1 requires that a minimum of two telecommunications outlet/connectors be installed for each work area.

2. Horizontal cabling shall contain no more than one transition point or consolidation point between the horizontal cross-connect and the telecommunications outlet/connector.

3. Bridged taps and splices shall not be installed in the horizontal cabling.

2.2 PERFORMANCE REQUIREMENTS

A. General Performance: Horizontal cabling system shall comply with transmission standards in TIA/EIA-568-B.1 when tested according to test procedures of this standard.

B. Surface-Burning Characteristics: Comply with ASTM E 84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

1. Flame-Spread Index: [25] <Insert value> or less.

2. Smoke-Developed Index: [50] [450] <Insert value> or less.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Grounding: Comply with J-STD-607-A.

2.3 BACKBOARDS

A. Backboards: Plywood, [fire-retardant treated, ]3/4 by 48 by 96 inches (19 by 1220 by 2440 mm). Comply with requirements in Section 061000 "Rough Carpentry" for plywood backing panels.

2.4 UTP CABLE

Copy this article and re-edit for each product.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. ADC.

2. Belden Inc.

3. Berk-Tek; a Nexans company.

4. CommScope, Inc.
5. Draka Cableteq USA.

6. Genesis Cable Products; Honeywell International, Inc.

7. Mohawk; a division of Belden Networking, Inc.

8. Superior Essex Inc.

9. SYSTIMAX Solutions; a CommScope, Inc. brand.

10. 3M Communication Markets Division.

11. Tyco Electronics Corporation; AMP Products.

12. <Insert manufacturer's name>.

C. Description: 100-ohm, four-pair UTP, formed into 25-pair, binder groups covered with a blue thermoplastic jacket.

1. Comply with ICEA S-90-661 for mechanical properties.

2. Comply with TIA/EIA-568-B.1 for performance specifications.

3. Comply with TIA/EIA-568-B.2, [Category 5e] [Category 6].

4. Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project. Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

a. Communications, General Purpose: Type CM or CMG[; or MPP, CMP, MPR, CMR, MP, or MPG].

b. Communications, Plenum Rated: Type CMP[ or MPP], complying with NFPA 262.

c. Communications, Riser Rated: Type CMR[; or MPP, CMP, or MPR], complying with UL 1666.

d. Communications, Limited Purpose: Type CMX[; or MPP, CMP, MPR, CMR, MP, MPG, CM, or CMG].

e. Multipurpose: Type MP or MPG[; or MPP or MPR].

f. Multipurpose, Plenum Rated: Type MPP, complying with NFPA 262.

g. Multipurpose, Riser Rated: Type MPR[ or MPP], complying with UL 1666.

2.5 UTP CABLE HARDWARE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. ADC.

2. American Technology Systems Industries, Inc.

3. Belden Inc.

4. Dynacom Inc.

5. Hubbell Premise Wiring.

6. Leviton Commercial Networks Division.

7. Molex Premise Networks; a division of Molex, Inc.

8. Panduit Corp.

9. Siemon Co. (The).

10. Tyco Electronics Corporation; AMP Products.

11. <Insert manufacturer's name>.

See Editing Instruction No. 4 in the Evaluations for discussion about 110-style IDC connectors and connector blocks.

C. General Requirements for Cable Connecting Hardware: Comply with TIA/EIA-568-B.2, IDC type, with modules designed for punch-down caps or tools. Cables shall be terminated with connecting hardware of same category or higher.

D. Connecting Blocks: [110-style IDC for Category 5e] [110-style IDC for Category 6] [66-style IDC for Category 5e]. Provide blocks for the number of cables terminated on the block, plus [25] <Insert number> percent spare. Integral with connector bodies, including plugs and jacks where indicated.

Delete "Cross-Connect" Paragraph below if cross-connection is accomplished exclusively on patch panels.

E. Cross-Connect: Modular array of connecting blocks arranged to terminate building cables and permit interconnection between cables.

Coordinate "Number of Terminals per Field" Subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field: [One] <Insert number> for each conductor in assigned cables.

F. Patch Panel: Modular panels housing multiple-numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Coordinate "Number of Jacks per Field" Subparagraph below with Drawings for quantity of fields.

1. Number of Jacks per Field: [One] <Insert number> for each four-pair [UTP cable indicated] [conductor group of indicated cables, plus spares and blank positions adequate to suit specified expansion criteria].

G. Jacks and Jack Assemblies: Modular, color-coded, eight-position modular receptacle units with integral IDC-type terminals.

Cords are generally available in lengths to 20 feet (6 m) and longer in 24-inch (600-mm) increments.

H. Patch Cords: Factory-made, four-pair cables in [36-inch (900 mm)] [48-inch1200-mm] <Insert length> lengths; terminated with eight-position modular plug at each end.

Retain one of two subparagraphs below; retain first for Category 6, second for Category 5e patch cords.

1. Patch cords shall have bend-relief-compliant boots and color-coded icons to ensure Category 6 performance. Patch cords shall have latch guards to protect against snagging.

2. Patch cords shall have color-coded boots for circuit identification.

2.6 CONSOLIDATION POINTS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Technology Systems Industries, Inc.

2. Belden Inc.

3. Chatsworth Products, Inc.

4. Dynacom Inc.

5. Hubbell Premise Wiring.

6. Molex Premise Networks; a division of Molex, Inc.

7. Ortronics, Inc.; a subsidiary of Legrand Group.

8. Panduit Corp.

9. Siemon Co. (The).

10. <Insert manufacturer's name>.

C. Description: Consolidation points shall comply with requirements for cable connecting hardware.

Coordinate "Number of Terminals per Field" Subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field: [One] <Insert number> for each conductor in assigned cables.

Coordinate "Number of Connectors per Field" Subparagraph below with Drawings for quantity of connectors.

2. Number of Connectors per Field:

a. [One] <Insert number> for each four-pair UTP cable indicated.

b. [One] <Insert number> for each four-pair conductor group of indicated cables, plus [25] <Insert number> percent spare positions.

3. Mounting: [Recessed in ceiling] [Wall] [Desk] [Furniture].

4. NRTL listed as complying with UL 50 and UL 1863.

5. When installed in plenums used for environmental air, NRTL listed as complying with UL 2043.

2.7 MULTIUSER TELECOMMUNICATIONS OUTLET ASSEMBLY (MUTOA)

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Belden Inc.

2. Chatsworth Products, Inc.

3. Hubbell Premise Wiring.

4. Molex Premise Networks; a division of Molex, Inc.

5. Ortronics, Inc.; a subsidiary of Legrand Group.

6. Panduit Corp.

7. Siemon Co. (The).

8. <Insert manufacturer's name>.

C. Description: MUTOAs shall meet the requirements for cable connecting hardware.

Coordinate "Number of Terminals per Field" Subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field: [One] <Insert number> for each conductor in assigned cables.

Coordinate "Number of Connectors per Field" Subparagraph below with Drawings for quantity of connectors.

2. Number of Connectors per Field:

a. [One] <Insert number> for each four-pair UTP cable indicated.

b. [One] <Insert number> for each four-pair conductor group of indicated cables, plus [25] <Insert number> percent spare positions.

3. Mounting: [Recessed in ceiling] [Wall] [Desk] [Furniture].

4. NRTL listed as complying with UL 50 and UL 1863.

5. Label shall include maximum length of work area cords, based on TIA/EIA-568-B.1.

6. When installed in plenums used for environmental air, NRTL listed as complying with UL 2043.

2.8 TELECOMMUNICATIONS OUTLET/CONNECTORS

A. Jacks: 100-ohm, balanced, twisted-pair connector; four-pair, eight-position modular. Comply with TIA/EIA-568-B.1.

Coordinate "Workstation Outlets" Paragraph below with other items specified to be mounted in workstation faceplates. Revise paragraph if faceplate elevations are on Drawings.

B. Workstation Outlets: [Two][Four]<Insert number of ports>-port-connector assemblies mounted in [single] [or] [multigang] faceplate.

Retain "Plastic Faceplate" or "Metal Faceplate" Subparagraph below, or retain both as required to match Section 262726 "Wiring Devices."

1. Plastic Faceplate: High-impact plastic. Coordinate color with Section 262726 "Wiring Devices."

2. Metal Faceplate: [Stainless steel] [Brass] <Insert description>, complying with requirements in Section 262726 "Wiring Devices."

3. For use with snap-in jacks accommodating any combination of UTP work area cords.

a. Flush mounting jacks, positioning the cord at a 45-degree angle.

Retain one of three "Legend" subparagraphs below; retain first for metal faceplates.

4. Legend: Factory labeled by silk-screening or engraving [for] [stainless steel] [brass] <Insert description> [faceplates].

5. Legend: Machine printed, in the field, using adhesive-tape label.

6. Legend: Snap-in, clear-label covers and machine-printed paper inserts.

2.9 GROUNDING

A. Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems" for grounding conductors and connectors.

B. Comply with J-STD-607-A.

2.10 IDENTIFICATION PRODUCTS

A. Comply with TIA/EIA-606-A and UL 969 for labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

B. Comply with requirements in Section 260553 "Identification for Electrical Systems."

2.11 SOURCE QUALITY CONTROL

Retain "Testing Agency" Paragraph below if required. Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

A. Testing Agency: Engage a qualified testing agency to evaluate cables.

B. Factory test UTP cables on reels according to TIA/EIA-568-B.1.

C. Factory test UTP cables according to TIA/EIA-568-B.2.

D. Cable will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 ENTRANCE FACILITIES

Retain this article if service entrance cabling and demarcation point are provided by communications service provider and horizontal cabling connects to the demarcation point. Normally, unless this is for a small single-story facility, communications horizontal cable interfaces with backbone cabling in communications rooms or spaces at cross-connects and patch panels.

A. Coordinate backbone cabling with the protectors and demarcation point provided by communications service provider.

3.2 WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings.

A. Install cables in pathways and cable trays except within consoles, cabinets, desks, and counters[ and except in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used]. Conceal pathways and cables except in unfinished spaces.

Retain first subparagraph below if retaining unenclosed wiring method option in paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements in Section 270528 "Pathways for Communications Systems."

3. Comply with requirements in Section 270536 "Cable Trays for Communications Systems."

B. Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

C. Wiring within Enclosures:

1. Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.

2. Install lacing bars and distribution spools.

3. Install conductors parallel with or at right angles to sides and back of enclosure.

3.3 INSTALLATION OF CABLES

A. Comply with NECA 1.

B. General Requirements for Cabling:

1. Comply with TIA/EIA-568-B.1.

2. Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

3. Install 110-style IDC termination hardware unless otherwise indicated.

4. MUTOA shall not be used as a cross-connect point.

5. Consolidation points may be used only for making a direct connection to telecommunications outlet/connectors:

a. Do not use consolidation point as a cross-connect point, as a patch connection, or for direct connection to workstation equipment.

b. Locate consolidation points for UTP at least 49 feet (15 m) from communications equipment room.

6. Terminate conductors; no cable shall contain unterminated elements. Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

7. Cables may not be spliced. Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

8. Install lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

9. Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter. Install lacing bars and distribution spools.

10. Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points. Remove and discard cable if damaged during installation and replace it with new cable.

11. Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used for heating.

12. In the communications equipment room, install a 10-foot- (3-m-) long service loop on each end of cable.

13. Pulling Cable: Comply with BICSI ITSIM, Ch. 4, "Pulling Cable." Monitor cable pull tensions.

C. UTP Cable Installation:

1. Comply with TIA/EIA-568-B.2.

2. Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

D. Open-Cable Installation:

1. Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

2. Suspend UTP cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceilings by cable supports not more than [60 inches (1524 mm)] <Insert dimension> apart.

3. Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

E. Installation of Cable Routed Exposed under Raised Floors:

1. Install plenum-rated cable only.

2. Install cabling after the flooring system has been installed in raised floor areas.

3. Coil cable [6 feet (1800 mm)] <Insert size> long not less than [12 inches (300 mm)] <Insert size> in diameter below each feed point.

F. Group connecting hardware for cables into separate logical fields.

See Editing Instruction No. 5 in the Evaluations for discussion about EMI.

G. Separation from EMI Sources:

1. Comply with BICSI TDMM and TIA-569-B for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

2. Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA: A minimum of 5 inches (127 mm).

b. Electrical Equipment Rating between 2 and 5 kVA: A minimum of 12 inches (300 mm).

c. Electrical Equipment Rating More Than 5 kVA: A minimum of 24 inches (610 mm).

3. Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA: A minimum of 2-1/2 inches (64 mm).

b. Electrical Equipment Rating between 2 and 5 kVA: A minimum of 6 inches (150 mm).

c. Electrical Equipment Rating More Than 5 kVA: A minimum of 12 inches (300 mm).

4. Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA: No requirement.

b. Electrical Equipment Rating between 2 and 5 kVA: A minimum of 3 inches (76 mm).

c. Electrical Equipment Rating More Than 5 kVA: A minimum of 6 inches (150 mm).

5. Separation between Communications Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger: A minimum of 48 inches (1200 mm).

6. Separation between Communications Cables and Fluorescent Fixtures: A minimum of 5 inches (127 mm).

3.4 FIRESTOPPING

A. Comply with requirements in Section 078413 "Penetration Firestopping."

B. Comply with TIA-569-B, Annex A, "Firestopping."

C. Comply with BICSI TDMM, "Firestopping Systems" Article.

3.5 GROUNDING

A. Install grounding according to BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

B. Comply with J-STD-607-A.

C. Locate grounding bus bar to minimize the length of bonding conductors. Fasten to wall allowing at least 2-inch (50-mm) clearance behind the grounding bus bar. Connect grounding bus bar with a minimum No. 4 AWG grounding electrode conductor from grounding bus bar to suitable electrical building ground.

D. Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

3.6 IDENTIFICATION

Retain one of first two paragraphs below.

A. Identify system components, wiring, and cabling complying with TIA/EIA-606-A. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

See Evaluations for discussion about designating the class of cabling plant administration and color-coding of cross-connect fields.

1. Administration Class: [1] [2] [3] [4].

2. Color-code cross-connect fields. Apply colors to voice and data service backboards, connections, covers, and labels.

B. Comply with requirements in Section 099123 "Interior Painting" for painting backboards. For fire-resistant plywood, do not paint over manufacturer's label.

See Evaluations for discussion about TIA/EIA standard as it applies to this Section.

C. Paint and label colors for equipment identification shall comply with TIA/EIA-606-A for [Class 2] [Class 3] [Class 4] level of administration[, including optional identification requirements of this standard].

D. Cable Schedule: Post in prominent location in each equipment room and wiring closet. List incoming and outgoing cables and their designations, origins, and destinations. Protect with rigid frame and clear plastic cover. Furnish an electronic copy of final comprehensive schedules for Project.

E. Cabling Administration Drawings: Show building floor plans with cabling administration-point labeling. Identify labeling convention and show labels for telecommunications closets, [backbone pathways and cables,] [entrance pathways and cables,] terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors. Follow convention of TIA/EIA-606-A. Furnish electronic record of all drawings, in software and format selected by Owner.

F. Cable and Wire Identification:

1. Label each cable within 4 inches (100 mm) of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

2. Each wire connected to building-mounted devices is not required to be numbered at device if color of wire is consistent with associated wire connected and numbered within panel or cabinet.

3. Exposed Cables and Cables in Cable Trays and Wire Troughs: Label each cable at intervals not exceeding 15 feet (4.5 m).

4. Label each terminal strip and screw terminal in each cabinet, rack, or panel.

a. Individually number wiring conductors connected to terminal strips, and identify each cable or wiring group being extended from a panel or cabinet to a building-mounted device shall be identified with name and number of particular device as shown.

b. Label each unit and field within distribution racks and frames.

5. Identification within Connector Fields in Equipment Rooms and Wiring Closets: Label each connector and each discrete unit of cable-terminating and connecting hardware. Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

6. Uniquely identify and label work area cables extending from the MUTOA to the work area. These cables may not exceed the length stated on the MUTOA label.

G. Labels shall be preprinted or computer-printed type with printing area and font color that contrasts with cable jacket color but still complies with requirements in TIA/EIA-606-A.

1. Cables use flexible vinyl or polyester that flex as cables are bent.

3.7 FIELD QUALITY CONTROL

A. Perform the following tests and inspections:

1. Visually inspect UTP jacket materials for NRTL certification markings. Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with TIA/EIA-568-B.1.

2. Visually confirm [Category 5e,] [Category 6,] marking of outlets, cover plates, outlet/connectors, and patch panels.

3. Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

4. Test UTP backbone copper cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors. Test operation of shorting bars in connection blocks. Test cables after termination but not cross-connection.

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2. Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex. Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

5. UTP Performance Tests:

a. Test for each outlet and MUTOA. Perform the following tests according to TIA/EIA-568-B.1 and TIA/EIA-568-B.2:

1) Wire map.

2) Length (physical vs. electrical, and length requirements).

3) Insertion loss.

4) Near-end crosstalk (NEXT) loss.

5) Power sum near-end crosstalk (PSNEXT) loss.

6) Equal-level far-end crosstalk (ELFEXT).

7) Power sum equal-level far-end crosstalk (PSELFEXT).

8) Return loss.

9) Propagation delay.

10) Delay skew.

Retain "Final Verification Tests" Subparagraph below if Owner intends to use Contractor in final testing after its personnel have assumed the operation of communications system.

6. Final Verification Tests: Perform verification tests for UTP systems after the complete communications cabling and workstation outlet/connectors are installed.

a. Voice Tests: These tests assume that dial tone service has been installed. Connect to the network interface device at the demarcation point. Go off-hook and listen and receive a dial tone. If a test number is available, make and receive a local, long distance, and digital subscription line telephone call.

b. Data Tests: These tests assume the Information Technology Staff has a network installed and is available to assist with testing. Connect to the network interface device at the demarcation point. Log onto the network to ensure proper connection to the network.

B. Document data for each measurement. Data for submittals shall be printed in a summary report that is formatted similar to Table 10.1 in BICSI TDMM, or transferred from the instrument to the computer, saved as text files, and printed and submitted.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. End-to-end cabling will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

3.8 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel in cable-plant management operations, including changing signal pathways for different workstations, rerouting signals in failed cables, and keeping records of cabling assignments and revisions when extending wiring to establish new workstation outlets.

END OF SECTION 271500

	COMMUNICATIONS HORIZONTAL CABLING
	271500 - 1



