Copyright 2010 AIA
MasterSpec Professional
12/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 274133 - MASTER ANTENNA TELEVISION SYSTEM
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. MATV equipment using [cable television service] [direct broadcast satellite service] [an off-air antenna system] [CCTV cameras and video recorders] as the signal source.

2. Off-air antennas.

3. MATV head-end components.

4. Distribution components.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 271300 "Communications Backbone Cabling" for coaxial, UTP, and fiber-optic cables and connectors.

2. Section 271500 "Communications Horizontal Cabling" for coaxial, UTP, and fiber-optic cables and connectors.

3. Section 282300 "Video Surveillance" for cameras, monitors, computers, and cabling for video surveillance systems.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. dBmV: Decibels relative to 1 mV across 75 ohms. Zero dBmV is defined as 1 mV across 75 ohms. dBmV = 20 log 10(V1/V2) where V1 is the measurement of voltage at a point having identical impedance to V2 (0.001 V across 75 ohms).

B. User Interface: End point of Contractor's responsibility for Work of this Section. User interfaces are the [terminal blocks to which the end user may connect coaxial cabling] [75-ohm terminals on device plates] <Define user-interface points>.

1.3 PERFORMANCE REQUIREMENTS

A. Minimum acceptable performance of distribution system at all user-interface points shall be as follows:

1. RF Video-Carrier Level: Between 3 and 12 dBmV.

2. Relative Video-Carrier Level: Within 3 dB to adjacent channel.

3. Carrier Level Stability, Short Term: Level shall not change more than 0.5 dB during a 60-minute period.

4. Carrier Level Stability, Long Term: Level shall not change more than 2 dB during a 24-hour period.

5. Channel Frequency Response: Across any 6-MHz channel in the 54- to 220-MHz frequency range, referenced to video; signal amplitude shall be plus or minus 1 dB, maximum.

6. Carrier-to-Noise Ratio: 45 dB or more.

7. RF Visual Signal-to-Noise Ratio: 43 dB or more.

8. Antenna Combiner Insertion Loss: 40 dB maximum.

9. Signal Power Splitter and Isolation Tap Return Loss: 17 dB maximum.

10. Cable Connectors Attenuation: Less than 0.1 dB.

Retain three subparagraphs below if capability for FM reception is required.

11. RF FM Carrier Level: 13 to 17 dB below video-carrier level.

12. FM Frequency Response: More than in the 88- to 108-MHz frequency range; signal amplitude is plus or minus 0.75 dB, maximum.

13. FM Carrier-to-Noise Ratio: More than 24 dB.

1.4 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For headend and distribution system. Include plans, elevations, sections, details, and attachments to other work.

1. Show fabrication and installation details for television equipment.

2. Wiring Diagrams: For power, signal, and control wiring. For UTP or fiber-optic cable, include cross connects, patch panels, and patch cords.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if design responsibilities have been delegated to Contractor. Delete below if signal attenuation budget and losses are indicated on Drawings or if signal strength to user interfaces is indicated.

C. Design Calculations: Calculate signal attenuation budget and show calculated line and equipment losses for the system based on the functional block diagram, to show that proposed system layout can be expected to perform up to specification. Calculate signal strength from sources to headend input points for each antenna, satellite dish, and CATV grouping. Allowable losses between components and user interface shall be used to determine size and type of coaxial cable.

1.5 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

PART 2 -  PRODUCTS

2.1 SYSTEMS REQUIREMENTS

A. Components: Plug-in, modular, heavy-duty, industrial- or commercial-grade units.

B. Equipment: Silicon-based, solid-state, integrated circuit devices.

C. Power Supply Characteristics: Devices shall be within specified parameters for ac supply voltages within the range of 105 to 130 V.

D. Protect signal cables and connected components against transient-voltage surges by suppressors and absorbers designed specifically for that purpose. Comply with requirements in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

E. Provide ac-powered equipment with integral surge suppressors complying with UL 1449.

F. RF and Video Impedance Matching: Signal-handling components, including connecting cable, shall have end-to-end impedance-matched signal paths. Match and balance devices used at connections where it is impossible to avoid impedance mismatch or mismatch of balanced circuits to unbalanced circuits.

2.2 MATV EQUIPMENT

A. Description: Signal-source components, signal-processing and amplifying equipment, distribution components, and interconnecting wiring. System shall receive, amplify, process, and distribute signals to outlets for receiving sets. Equipment shall translate UHF channels to VHF channels before distribution to outlets.

Coordinate first paragraph below with Drawings. Clear descriptions of signal sources used and programs distributed are critical to obtaining meaningful Contractor response to MATV system requirements.

B. Identification of Signal Sources Distributed:

Include FM stations in subparagraph below if needed.

1. <Insert signal sources and basic service selection>.

C. MATV System Qualitative and Quantitative Performance Requirements: Reception quality of color-television program transmissions at each system outlet from each service and source shall be equal to or superior than that obtained with performance checks specified in "Field Quality Control" Article, using standard, commercial, cable-ready, multiple A/V input color-television receivers.

2.3 OFF-AIR ANTENNAS

A. Antennas shall be tested, marked, and packaged, according to CEA-774-A, CEA-2028, and CEA-2032. Antennas shall be labeled according to CEA antenna mapping program.

B. Off-Air, Mast-Mounted Antennas: Weatherproof single-channel or broadband type, constructed of high-strength anodized aluminum and rated to survive in a [100-mph (160-km/h)] <Insert speed> wind, minimum.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Channel Master; Part of Andrew Corporation.

b. RadioShack Corporation.

c. TERK by Audiovox; a subsidiary of Audiovox Corporation.

d. Winegard Company.

e. <Insert manufacturer's name>.

3. Elements: Internally dampened against mechanical vibration that may occur in service.

4. Ends of Crossarms and Elements: Sealed.

5. Mounting and Connecting Hardware: Corrosion proof.

6. Frequency Range: Matched to source frequencies.

Retain first subparagraph below if reception patterns are not scheduled on Drawings. See Editing Instruction No. 3 in the Evaluations for discussion of CEA antenna reception patterns and scheduling.

7. CEA Reception Patterns: <Insert reception pattern and number of antennas>.

Retain subparagraph below if FM distribution is specified or if FM signal is not obtained from a broadband antenna.

8. FM Antenna: Separate from the broadband antenna and the [omnidirectional] [directional] antenna, with 2-dB minimum gain.

Coordinate paragraph below with Drawings.

C. Antenna-Supporting Structures: Prefabricated, hot-dip galvanized-steel units.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Channel Master; Part of Andrew Corporation.

b. RadioShack Corporation.

c. TERK by Audiovox; a subsidiary of Audiovox Corporation.

d. Winegard Company.

e. <Insert manufacturer's name>.

3. Strength of Structure and Attachments: Adequate to withstand [100-mph (160-km/h)] <Insert speed> winds while supporting installed antennas.

4. Comply with 47 CFR 17 and TIA 222-G.

Retain obstruction lighting requirements in subparagraph below if applicable.

5. Comply with FAA AC 70/7460-1K.

2.4 MATV HEADEND COMPONENTS

A. Headend Equipment: [Channel mixers] [Processors] [Broadband amplifier] [Single-channel amplifiers] [FM module] [Combining networks] for receiving off-air television and FM signals and outputting the signals to cable distribution system. Equip coaxial down-leads of the off-air antennas with preamplifiers to send signals at strength required by headend. Headend component performance specified in this article is minimum acceptable; better performance may be required to comply with minimum acceptable system performance standard in "Performance Requirements" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Blonder Tongue Laboratories, Inc.

b. Canare Corp.

c. Channel Master; Part of Andrew Corporation.

d. Leviton Manufacturing Co., Inc.; Leviton Voice & Data Division.

e. Motorola, Inc.; Connected Home Solutions.

f. Quality RF Services, Inc.; a member company of ATX Networks.

g. Scientific-Atlanta, Inc.; a subsidiary of Cisco Systems, Inc.

h. <Insert manufacturer's name>.

3. House units in standard 19-inch (483-mm) electronic equipment cabinet complying with EIA 310.

B. Antenna Combiner: Directional coupler design network, combining up to eight antenna signals into a single output. Frequency response of the device shall be 5 to 400 MHz, and the insertion loss between input ports shall be not less than 40 dB.

C. Down-Lead Preamplifiers: Antenna mast-mounted preamplifier, designed to boost antenna signal and contained in weatherproof housing; single-channel or broadband type. Install power supplies indoors at headend equipment, connected through power inserters to provide power to preamplifiers through the coaxial down-lead cable.

1. Frequency Response: Plus or minus 0.75 dB.

2. Minimum Input: Minus 20 dBmV.

3. Return Loss: 14 dB.

4. I/O Impedance: 75 ohms.

D. Channel Mixers: Use for nonadjacent channels only.

1. Insertion Loss (Maximum 54 to 216 MHz): 2.5 dB.

2. Return Loss: 14 dB.

3. Out-of-Band Rejection: 12 dB.

4. I/O Impedance: 75 ohms.

E. Processors: One for each channel to be translated.

1. Bandwidth: 6 MHz.

2. Return Loss: 16 dB, within the 6-MHz bandwidth.

3. Noise: Not more than 10 dB at maximum gain.

4. Input Level Range, VHF: Minus 20 to plus 30 dBmV.

5. Input Level Range, UHF: Minus 20 to plus 25 dBmV.

6. Output Level Range: 50 to 60 dBmV.

7. Carrier-to-Noise Ratio: Minus 57 dB at plus 10-dBmV input.

8. Automatic Gain Control: Plus or minus 1-dB output variation for rated input level range variation.

9. Frequency Stability: Plus or minus 10 kHz over the operational temperature range.

10. Spurious Output: 60 dB below the video carrier with video-carrier output level at plus 60 dBmV and audio-carrier level at plus 45 dBmV.

11. Adjacent Channel Rejection: Not less than 60 dB.

12. I/O Impedance: 75 ohms.

F. Broadband Amplifier:

1. Frequency Range: [54 to 108, 174 to 220] [54 to 220] MHz.

2. Frequency Response: Plus or minus 1.0 dB across passband.

3. Maximum Noise: 10 dB.

4. Minimum Return Loss: 16 dB.

5. I/O Impedance: 75 ohms.

G. Single-Channel Amplifiers:

1. Frequency: 6 MHz for specified channel.

2. Frequency Response: Plus or minus 0.5 dB.

3. Maximum Noise: 10 dB.

4. Minimum Return Loss: 14 dB.

5. Automatic Gain Control: Plus or minus 1-dB output variation for rated input level range variation.

6. Skirt Rejection: Minus 26 dB at plus or minus 5 MHz from channel center.

7. Sound Trap: Adjustable to 10 VdB of attenuation of the sound carrier.

8. I/O Impedance: 75 ohms.

Retain first paragraph below if single-station FM receiver modules are required.

H. FM Module: One RF processor module for each station listed.

1. Frequency Range: Between 88 and 108 MHz.

2. Output Level: 52 dBmV.

3. Output Level Control: Plus or minus 10 dB.

4. Stability: 0.005 percent, crystal controlled.

5. Sensitivity: 3 mV for 30-dB quieting.

6. Input Level: 60 mV, stereo.

7. Image Rejection: 901 dB.

8. Passband: 200 kHz.

9. Selectivity: Plus or minus 150 kHz or less, at 30 dB down. Plus or minus 250 kHz or less, at 50 dB down.

I. Combining Network (Mixer): Combines the off-air television [FM] [CCTV] [and] [CATV] signals into a single-broadband output. An output test point, a 75-ohm television jack, a mixer output step attenuator dual-pilot insertion network, and a removable mixer-to-trunk jumper are included.

1. Passband: As required by system performance.

2. Distortion: Not more than plus or minus 0.1 dB over any 6-MHz segment.

3. Distortion: Not more than plus or minus 0.5 dB over the 54- to 216-MHz frequency range.

4. Nominal Insertion Loss:

a. 15 dB maximum, channel input to single-system output.

b. 13 dB maximum, channel input to mixer output.

c. 20 dB maximum at test point, e.g., loss from trunk output.

5. Isolation between any Two Inputs: 30 dB.

6. I/O Impedance: 70 ohms.

2.5 DISTRIBUTION COMPONENTS

A. Signal Power Splitters and Isolation Taps: Metal-enclosed directional couplers with brass connector parts. Where installed in signal circuits used to supply cable-powered amplifiers, power throughput capacity shall exceed load by at least 25 percent.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Canare Corp.

b. Leviton Manufacturing Co., Inc.; Leviton Voice & Data Division.

c. Motorola, Inc.; Connected Home Solutions.

d. Quality RF Services, Inc.; a member company of ATX Networks.

e. Scientific-Atlanta, Inc.; a subsidiary of Cisco Systems, Inc.

f. <Insert manufacturer's name>.

3. Return Loss: 17 dB.

4. RFI Shielding: 100 dB.

5. Isolation: 25 dB.

6. I/O Impedance: 75 ohms.

B. Distribution System Amplifiers: Powered by coaxial cable system and equipped with surge protection device and external test points to allow convenient signal monitoring.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Canare Corp.

b. Leviton Manufacturing Co., Inc.; Leviton Voice & Data Division.

c. Motorola, Inc.; Connected Home Solutions.

d. Quality RF Services, Inc.; a member company of ATX Networks.

e. Scientific-Atlanta, Inc.; a subsidiary of Cisco Systems, Inc.

f. <Insert manufacturer's name>.

C. Cable System Power Supplies: Plug-in, modular construction, with surge, short-circuit, and overload protection.

D. Signal Traps: Packaged filters tuned to interference frequencies encountered in Project.

E. Attenuators: Passive, of fixed value, and used to balance signal levels.

F. Terminating Resistors: Enclosed units rated 0.5 W and matched for coaxial impedance.

Coordinate paragraph below with Drawings.

G. User-Interface Device: Flush, female-type outlets, designed to mimic power duplex outlet; for mounting in standard outlet box; with metallic parts of anodized brass, beryllium copper, or phosphor bronze. Cable connector mounting shall be semirecessed so its protrusion is flush with the plane of device plate.[ Feed-through-type cable connection shall not be used] [except in area housing a single tenant] [except within a single-dwelling unit].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Canare Corp.

b. Leviton Manufacturing Co., Inc.; Leviton Voice & Data Division.

c. Motorola, Inc.; Connected Home Solutions.

d. Quality RF Services, Inc.; a member company of ATX Networks.

e. Scientific-Atlanta, Inc.; a subsidiary of Cisco Systems, Inc.

f. <Insert manufacturer's name>.

3. Cable Connector: Female, Type F.

4. Wall Plates: Match materials and finish of power outlets in same space.

5. Attenuation: Less than 0.1 dB.

6. Voltage Standing-Wave Ratio: Less than 1.15 to 1.

2.6 ENCLOSURES

A. Enclosures for Interior, Controlled Environments: NEMA 250, Type 1.

B. Enclosures for Interior, Uncontrolled Environments: NEMA 250, [Type 3R] [Type 4] [Type 12] [Type 12K].

C. Enclosures for Exterior Environments: NEMA 250, [Type 3] [Type 3R] [Type 3S] [Type 4] [Type 4X].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install signal line surge suppressors on coaxial cables entering headend equipment space and at antenna-mounted amplifiers. Comply with requirements in Section 264313 "Transient-Voltage Suppression for Low-Voltage Electrical Power Circuits."

Coordinate paragraph below with Drawings and verify that Drawings properly indicate mounting heights.

B. Install antenna towers, masts, and mountings on concrete bases. Comply with requirements for concrete bases specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

2. Install anchor bolts to elevations required for proper attachment to supported equipment.

3.2 ANTENNA AND HEADEND INSTALLATION

Coordinate this article with Drawings.

A. Mount headend equipment in electronic-equipment cabinets recommended by manufacturer. Group related items in methodical sequence.

B. Arrange equipment to facilitate access for maintenance and to preserve headroom and passage space. Parts that require periodic service or maintenance shall be readily accessible. Headend components that require tuning adjustments shall be accessible from the front of equipment cabinets.

C. Align antenna elements to achieve maximum signal level and quality.

D. Antenna-Supporting Structure: Increase antenna height as required to obtain signal strength needed for specified system performance.

Retain one or both of first two subparagraphs below. Delete both if Drawings detail attachment. Revise bolt sizes as recommended by structural engineer.

1. Attachment to Building: Use 0.375-inch- (10-mm-) minimum expansion anchors for masonry, and place anchors clear of grout or mortar joints.

2. Attachment to Building: Use 0.375-inch- (10-mm-) minimum lag bolts for attachment to wood.

3. Lightning Protection: Comply with requirements in Section 264113 "Lightning Protection for Structures."

E. Antenna Cable Entrance: Use weatherproof entrance fittings, and seal at penetrations of the building envelope.

3.3 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Inspection: Verify that units and controls are properly installed, connected, and labeled, and that interconnecting wires and terminals are identified.

C. Tests and Inspections:

1. Align and adjust system and pretest components, wiring, and functions to verify that they comply with specified requirements.

2. Replace malfunctioning or damaged items.

3. Retest until satisfactory performance and conditions are achieved.

4. Prepare television equipment for acceptance and operational testing.

5. Use an agile receiver and signal strength meter or spectrum analyzer for testing.

6. Off-Air, Mast-Mounted Antenna Sources: Connect receiver to the down-lead of a 10-element, single-channel antenna, tuned and oriented to optimize reception for the channel and placed at system antenna's location. Alternatively, connect receiver to a single-channel video amplifier connected to the down-lead of the above single-channel antenna.

7. CATV Sources: Connect receiver to an agile demodulator or CATV set-top converter at CATV service entrance to the facility.

8. Satellite Earth-Station System Sources: Adapt receiver to the output of satellite-television receiver.

9. CCTV Sources: Connect receiver to the output of each CCTV signal source or the distribution amplifier associated with it.

10. Test Schedule: Schedule tests after pretesting has successfully been completed and system has been in normal functional operation for at least 14 days. Provide a minimum of 10 days' notice of test schedule.

11. Operational Tests: Perform tests of operational system to verify that system complies with Specifications. Include all modes of system operation. Test equipment for proper operation in all functional modes.

12. Distribution System Acceptance Tests:

a. Field-Strength Instrument: Rated for minus 40-dBmV measuring sensitivity and a frequency range of 54 to 812 MHz, minimum. Provide documentation of recent calibration against recognized standards.

b. Signal Level and Picture Quality: Use a field-strength meter or spectrum analyzer, and a standard television receiver to measure signal levels and check picture quality at [all] [25 percent of] <Insert number or percentage> user-interface outlets.

1) Test the signal strength in dBmV at 55[, 151, 547,] and 750 MHz.

2) Minimum acceptable signal level is 0 dBmV (1000 mV).

3) Maximum acceptable signal level over the entire bandwidth is 15 dBmV.

4) Television receiver shall show no evidence of cross-channel intermodulation, ghost images, or beat interference.

13. Signal-to-Noise-Ratio Test: Use a field-strength meter to make a sequence of measurements at the output of the last distribution amplifier or of another agreed-on location in system. With system operating at normal levels, tune meter to the picture carrier frequency of each of the designated channels in turn and record the level. With signal removed and input to corresponding headend amplifier terminated at 75 ohms, measure the level of noise at same tuning settings. With meter correction factor added to last readings, differences from first set must not be less than 45 dB.

14. Qualitative and Quantitative Performance Tests: Demonstrate reception quality of color-television program transmissions at each user interface from each designated channel and source. Quality shall be equal to or superior than that obtained with performance checks specified below, using a standard, commercial, cable-ready, color-television receiver. Level and quality of signal at each outlet and from each service and source shall comply with the following Specifications when tested according to 47 CFR 76:

a. RF video-carrier level.

b. Relative video-carrier level.

c. Carrier level stability, during 60-minute and 24-hour periods.

d. Broadband frequency response.

e. Channel frequency response.

f. Carrier-to-noise ratio.

g. RF visual signal-to-noise ratio.

h. Antenna combiner insertion loss.

i. Signal power splitter loss.

j. Cable connector attenuation.

Retain subparagraphs below if capability for FM reception is required.

k. RF FM carrier level.

l. FM frequency response.

m. FM carrier-to-noise ratio.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Headend and distribution system will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

F. For fiber-optic- and UTP-cable performance test, see Section 271500 "Communications Horizontal Cabling."

G. Cap all unused connectors and seal weathertight.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain MATV equipment.

1. Train Owner's maintenance personnel on procedures and schedules for troubleshooting, servicing, and maintaining equipment.

2. Demonstrate methods of determining optimum alignment and adjustment of components and settings for system controls.

3. Demonstrate programming and tuning of satellite receivers.

END OF SECTION 274133

	MASTER ANTENNA TELEVISION SYSTEM
	274133 - 1



