Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 275123.50 - EDUCATIONAL INTERCOMMUNICATIONS AND PROGRAM SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes: Manually switched intercommunications and program systems with the following components:

1. Master stations.

2. Speaker-microphone stations.

3. Call-switch unit.

4. All-call amplifier.

5. Intercommunication amplifier.

6. Paging amplifier.

7. Loudspeakers/speaker microphones.

8. Conductors and cables.

9. Raceways.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For educational intercommunications and program systems. Include plans, elevations, sections, details, and attachments to other work.

1. Wiring Diagrams: For power, signal, and control wiring.

a. Identify terminals to facilitate installation, operation, and maintenance.

b. Single-line diagram showing interconnection of components.

c. Cabling diagram showing cable routing.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Installer Qualifications: Manufacturer's authorized representative who is trained and approved for installation of units required for this Project.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for location and application.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Bogen Communications, Inc.

2. Dukane Communication Systems; part of GE Infrastructure, Security.

3. Jeron Electronic Systems, Inc.

4. Rauland-Borg Corporation.

5. <Insert manufacturer's name>.

2.2 FUNCTIONAL DESCRIPTION OF SYSTEMS

A. Master Station:

Six subparagraphs below are examples of typical functions.

1. Communicating selectively with other master and speaker-microphone stations by actuating selector switches.

If retaining first subparagraph below, retain "All-Call Amplifier" Article.

2. Communicating simultaneously with all other stations by actuating a single all-call switch.

3. Communicating with individual stations in privacy.

4. Including other master-station connections in a multiple-station conference call.

5. Accessing separate paging speakers or groups of paging speakers by actuating selector switches.

6. Overriding any conversation by a designated master station.

B. Speaker-Microphone Station:

Five subparagraphs below are examples of typical functions. Revise first subparagraph to indicate privacy features required. Coordinate with Drawings.

1. Having privacy from remote monitoring without a warning tone signal at monitored station. Designated speaker-microphone stations have a privacy switch to prevent another station from listening and to permit incoming calls.

2. Communicating hands free.

3. Calling master station by actuating call switch.

4. Returning a busy signal to indicate that station is already in use.

5. Being free of noise and distortion during operation and when in standby mode.

C. Speakers: Free of noise and distortion during operation and when in standby mode.

2.3 GENERAL REQUIREMENTS FOR EQUIPMENT AND MATERIALS

A. Coordinate features and select components to form an integrated system. Match components and interconnections for optimum performance of specified functions.

B. Expansion Capability: Increase number of stations in the future by [25] <Insert number> percent above those indicated without adding any internal or external components or main trunk cable conductors.

C. Equipment: Modular type using solid-state components, fully rated for continuous duty unless otherwise indicated. Select equipment for normal operation on input power usually supplied at 110 to 130 V, 60 Hz. Comply with UL 813.

D. Weather-Resistant Equipment: Listed and labeled by an NRTL for duty outdoors or in damp locations.

2.4 MASTER STATION

A. Station-Selector and Talk-Listen Switches: Heavy-duty type with gold-plated contacts rated for five million operations.

B. Volume Control: Regulates incoming-call volume.

C. LED Annunciation: Identifies calling stations and stations in use. LED remains on until call is answered.

D. Tone Annunciation: Momentary audible tone signal announces incoming calls.

E. Speaker Microphone: Transmits and receives calls.

1. Minimum Speaker Sensitivity: 91 dB at one meter, with 1-W input.

Coordinate first paragraph below with Drawings.

F. Handset with Hook Switch: Telephone type with 18-inch- (450-mm-) long, permanently coiled cord. Arrange to disconnect speaker when handset is lifted.

G. Central-Equipment Cabinet: Comply with TIA/EIA-310-D. Lockable, ventilated metal cabinet houses terminal strips, power supplies, amplifiers, system volume control, and auxiliary equipment.

2.5 SPEAKER-MICROPHONE STATIONS

Paragraphs below are examples of typical products and components.

A. Mounting: Flush unless otherwise indicated, and suitable for mounting conditions indicated.

B. Faceplate: Stainless steel or anodized aluminum with tamperproof mounting screws.

C. Back Box: Two-gang galvanized steel with 2-1/2-inch (64-mm) minimum depth.

D. Speaker: Minimum axial sensitivity shall be 91 dB at one meter, with 1-W input. Voice coil shall be not less than 3 inches (76 mm), 2.3 oz. (65 g) minimum; permanent magnet.

E. Tone Annunciation: Recurring momentary tone indicates incoming calls.

F. Call Switch: Mount on faceplate. Permits calls to master station.

G. Privacy Switch: Mount on faceplate. When in on position, switch prevents transmission of sound from remote station to system; when in off position, without further switch manipulation, response can be made to incoming calls.

2.6 CALL-SWITCH UNIT

A. Enclosure: Single-gang box with stainless-steel faceplate.

B. Call Switch: Momentary contact signals system that a call has been placed.

C. Privacy Switch: Prevents transmission of sound signals from station to system.

D. Volume Control: Operated by screwdriver blade through a hole in faceplate to adjust output level of associated speaker.

2.7 ALL-CALL AMPLIFIER

A. Output Power: 70-V balanced line. [80 percent of the sum of wattage settings of connected] <Insert wattage> for each station and speaker connected in all-call mode of operation, plus an allowance for future stations.

B. Total Harmonic Distortion: Less than 5 percent at rated output power with load equivalent to quantity of stations connected in all-call mode of operation.

C. Minimum Signal-to-Noise Ratio: 60 dB, at rated output.

D. Frequency Response: Within plus or minus 2 dB from 50 to 12,000 Hz.

E. Output Regulation: Maintains output level within 2 dB from full to no load.

F. Input Sensitivity: Compatible with master stations and central equipment so amplifier delivers full-rated output with sound-pressure level of less than 10 dynes/sq. cm impinging on master stations, speaker microphones, or handset transmitters.

G. Amplifier Protection: Prevents damage from shorted or open output.

2.8 INTERCOMMUNICATION AMPLIFIER

A. Minimum Output Power: 15 W; adequate for all functions.

B. Total Harmonic Distortion: Less than 5 percent at rated output power with load equivalent to one station connected to output terminals.

C. Minimum Signal-to-Noise Ratio: 50 dB, at rated output.

D. Frequency Response: Within plus or minus 3 dB from 70 to 10,000 Hz.

E. Output Regulation: Maintains output level within 2 dB from full to no load.

F. Input Sensitivity: Matched to input circuit and to provide full-rated output with sound-pressure level of less than 10 dynes/sq-m impinging on microphones in master stations, speaker microphones, or handset transmitters.

G. Amplifier Protection: Prevents damage from shorted or open output.

2.9 PAGING AMPLIFIER

Retain this article if Project requires paging over speakers separate from those associated with intercommunication stations.

A. Input Voltage: 120-V ac, 60 Hz.

B. Frequency Response: Within plus or minus 3 dB from 60 to 10,000 Hz.

C. Minimum Signal-to-Noise Ratio: 60 dB, at rated output.

D. Total Harmonic Distortion: Less than 3 percent at rated output power from 70 to 12,000 Hz.

E. Output Regulation: Less than 2 dB from full to no load.

F. Controls: On-off, input levels, and low-cut filter.

G. Input Sensitivity: Matched to input circuit and to provide full-rated output with sound-pressure level of less than 10 dynes/sq. cm impinging on speaker microphones or handset transmitters.

H. Amplifier Protection: Prevents damage from shorted or open output.

2.10 CONE-TYPE LOUDSPEAKERS/SPEAKER MICROPHONES

A. Minimum Axial Sensitivity: 91 dB at one meter, with 1-W input.

B. Frequency Response: Within plus or minus 3 dB from 70 to 15,000 Hz.

C. Minimum Dispersion Angle: 100 degrees.

D. Line Transformer: Maximum insertion loss of 0.5 dB, power rating equal to speaker's, and at least four level taps.

E. Enclosures: Steel housings or back boxes, acoustically dampened, with front face of at least 0.0478-inch (1.2-mm) steel and whole assembly rust proofed and factory primed; complete with mounting assembly and suitable for surface ceiling, flush ceiling, pendant or wall mounting; with relief of back pressure.

F. Baffle: For flush speakers, minimum thickness of 0.032-inch (0.8-mm) aluminum [brushed to a satin sheen and lacquered] [with textured white finish] <Insert finish>.

Retain first paragraph below for areas subject to high impact or abuse.

G. Vandal-Proof, High-Strength Baffle: For [flush] [surface]-mounted speakers, self-aging cast aluminum with tensile strength of 44,000 psi (303 MN/sq. m), 0.025inch (0.65-mm) minimum thickness; countersunk heat-treated alloy mounting screws; and textured white epoxy finish.

H. Size: 8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (140-g) ceramic magnet.

2.11 HORN-TYPE LOUDSPEAKERS/SPEAKER MICROPHONES

A. Speakers shall be all-metal, weatherproof construction; complete with universal mounting brackets.

B. Frequency Response: Within plus or minus 3 dB from 275 to 14,000 Hz.

C. Minimum Power Rating of Driver: 15 W, continuous.

D. Minimum Dispersion Angle: 110 degrees.

E. Line Transformer: Maximum insertion loss of 0.5 dB, power rating equal to speaker's, and at least four level taps.

2.12 CONDUCTORS AND CABLES

Retain this article unless cabling is specified in Section 271500 "Communications Horizontal Cabling."

A. Conductors: Jacketed, twisted pair and twisted multipair, untinned solid copper. Sizes as recommended by system manufacturer, but no smaller than No. 22 AWG.

B. Insulation: Thermoplastic, not less than 1/32 inch (0.8 mm) thick.

C. Shielding: For speaker-microphone leads and elsewhere where recommended by manufacturer; No. 34 AWG, tinned, soft-copper strands formed into a braid or equivalent foil.

1. Minimum Shielding Coverage on Conductors: 60 percent.

D. Plenum Cable: Listed and labeled for plenum installation.

2.13 RACEWAYS

Retain one of first three paragraphs below. Coordinate selection with "Wiring Methods" Article and with Section 260533 "Raceway and Boxes for Electrical Systems." Retain first paragraph to allow Contractor to choose any material specified in Section 260533 "Raceway and Boxes for Electrical Systems."

A. Educational Intercommunication and Program System Raceways and Boxes: Comply with requirements in Section 260533 "Raceway and Boxes for Electrical Systems."

B. Educational Intercommunication and Program System Raceways and Boxes: Same as required for electrical branch circuits specified in Section 260533 "Raceway and Boxes for Electrical Systems."

C. Educational Intercommunication and Program System Raceways and Boxes: [EMT] [ENT] [RNC] [Optical-fiber/communication raceways and fittings] [Metal wireways] [Nonmetal wireways] [Surface metal raceways] [Surface nonmetal raceways].

D. Outlet boxes shall be not less than 2 inches (50 mm) wide, 3 inches (75 mm) high, and 2-1/2 inches (64 mm) deep.

Retain paragraph below to prohibit use of flexible metal conduit.

E. Flexible metal conduit is prohibited.

PART 3 -  EXECUTION

3.1 WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings. Coordinate selection with "Raceways" Article.

A. Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters[, and except in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used]. Conceal raceway and cables except in unfinished spaces.

Retain first subparagraph below if selecting option in paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements for raceways and boxes specified in Section 260533 "Raceway and Boxes for Electrical Systems."

B. Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

C. Wiring within Enclosures: Bundle, lace, and train cables to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

3.2 INSTALLATION OF RACEWAYS

A. Comply with requirements in Section 260533 "Raceway and Boxes for Electrical Systems" for installation of conduits and wireways.

B. Install manufactured conduit sweeps and long-radius elbows whenever possible.

3.3 INSTALLATION OF CABLES

A. Comply with NECA 1.

B. General Requirements:

1. Terminate conductors; no cable shall contain unterminated elements. Make terminations only at outlets and terminals.

2. Splices, Taps, and Terminations: Arrange on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures. Cables may not be spliced.

3. Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

4. Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

5. Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points. Remove and discard cable if damaged during installation and replace it with new cable.

6. Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used.

C. Open-Cable Installation:

1. Install cabling with horizontal and vertical cable guides in telecommunication spaces with terminating hardware and interconnection equipment.

2. Suspend speaker cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceiling by cable supports not more than [60 inches (1524 mm)] <Insert dimension> apart.

3. Cable shall not be run through structural members or be in contact with pipes, ducts, or other potentially damaging items.

D. Separation of Wires: Separate speaker-microphone, line-level, speaker-level, and power wiring runs. Install in separate raceways or, where exposed or in same enclosure, separate conductors at least 12 inches (300 mm) apart for speaker microphones and adjacent parallel power and telephone wiring. Separate other intercommunication equipment conductors as recommended by equipment manufacturer.

3.4 INSTALLATION

A. Match input and output impedances and signal levels at signal interfaces. Provide matching networks where required.

B. Identification of Conductors and Cables: Color-code conductors and apply wire and cable marking tape to designate wires and cables so they identify media in coordination with system wiring diagrams.

C. Weatherproof Equipment: For units that are mounted outdoors, in damp locations, or where exposed to weather, install consistent with requirements of weatherproof rating.

D. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.5 GROUNDING

A. Ground cable shields and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

B. Signal Ground Terminal: Locate at main equipment cabinet. Isolate from power system and equipment grounding.

Retain paragraph below for special applications only.

C. Install grounding electrodes as specified in Section 260526 "Grounding and Bonding for Electrical Systems."

3.6 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Schedule tests with at least seven days' advance notice of test performance.

2. After installing educational intercommunications and program systems and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test: Test originating station-to-station[, all-call, and page] messages at each intercommunication station. Verify proper routing and volume levels and that system is free of noise and distortion. Test each available message path from each station on system.

Retain subparagraph below if paging is specified.

4. Power Output Test: Measure electrical power output of each paging amplifier at normal gain settings of 150, 1000, and 2500 Hz. Maximum variation in power output at these frequencies is plus or minus 3 dB.

C. Inspection: Verify that units and controls are properly labeled and interconnecting wires and terminals are identified. Prepare a list of final tap settings of paging and independent room speaker-line matching transformers.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Educational intercommunications and program systems will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

END OF SECTION 275123.50

	EDUCATIONAL INTERCOMMUNICATIONS AND PROGRAM SYSTEMS
	275123.50 - 1



