Copyright 2010 AIA
MasterSpec Professional
11/10

SECTION 323113 - CHAIN LINK FENCES AND GATES
PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes chain-link fences and swing gates.

1.2 PERFORMANCE REQUIREMENTS

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated

B. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

1.4 INFORMATIONAL SUBMITTALS

A. Product Certificates: For each type of chain-link fence and gate, from manufacturer.

B. Product Test Reports: For framing strength according to ASTM F 1043.

C. Sample of special warranty.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 WARRANTY

A. Special Warranty: Manufacturer's standard form in which Manufacturer agrees to repair or replace components of chain-link fences and gates that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, deterioration of metals, metal finishes, and other materials beyond normal weathering.

2. Warranty Period: One year from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 CHAIN-LINK FENCE FABRIC

A. General: Provide fabric in one-piece heights measured between top and bottom of outer edge of selvage knuckle or twist. Comply with CLFMI Product Manual and with requirements indicated below:

1. Fabric Height: As indicated on Drawings.

2. Steel Wire Fabric: Wire with a diameter of 0.148 inch.

a. Mesh Size: 2 inches.

b. Zinc-Coated Fabric: ASTM A 392, Type II, Class 2, 2.0 oz./sq. ft with zinc coating.

3. Selvage: Knuckled at both selvages.

2.2 FENCE FRAMING

A. Posts and Rails: Comply with ASTM F 1043 for framing, including rails, braces, and line; terminal; and corner posts. Provide members with minimum dimensions and wall thickness according to ASTM F 1043 based on the following:

1. Fence Height: As indicated on Drawings.

2. Horizontal Framework Members: Intermediate, top and bottom rails complying with ASTM F 1043.

3. Brace Rails: Comply with ASTM F 1043.

4. Metallic Coating for Steel Framing:

a. Type A zinc coating.

b. Type B zinc with organic overcoat.

c. External, Type B zinc with organic overcoat and internal, Type D zinc-pigmented coating.

d. Type C, Zn-5-Al-MM alloy coating.

e. Coatings: Any coating above.

2.3 TENSION WIRE

Always retain this article if fence has no top rail. Bottom horizontal members enhance security and should be specified on any fence constructed with slats or screening. Consider specifying top and bottom tension wire or, alternatively, specify top and bottom rails.

Retain one of two paragraphs below for tension wire to match fabric material and, if applicable, coating weight.

A. Metallic-Coated Steel Wire: 0.177-inch- (4.5-mm-) diameter, marcelled tension wire complying with ASTM A 817 and ASTM A 824, with the following metallic coating:

Retain one of three subparagraphs below.

1. Type I, aluminum coated (aluminized).

2. Type II, zinc coated with minimum coating weight matching chain-link fabric coating weight.

3. Type III, Zn-5-Al-MM alloy with minimum coating weight matching chain-link fabric coating weight

B. Polymer-Coated Steel Wire: [0.177-inch- (4.5-mm-)] [0.148-inch- (3.8-mm-)] diameter, tension wire complying with ASTM F 1664, [Class 1] [Class 2a] [Class 2b] over [aluminum] [zinc] [Zn-5-Al-MM-alloy]-coated steel wire.

1. Color: [Match chain-link fabric] [Dark green] [Olive green] [Brown] [Black] [As selected by Architect from manufacturer's full range], complying with ASTM F 934.

2.4 SWING GATES

Industrial swing gate frames and dimensions determine gate-post material, size, and weight according to ASTM F 900 for gates up to 24 feet (7.3 m) wide. If default values do not suit Project, insert sizes and minimum weights of components. Require verification that components not covered by ASTM standards comply with or exceed structural and coating requirements in ASTM F 900.

A. General: Comply with ASTM F 900 for gate posts and [single] [double] swing gate types.

1. Gate Leaf Width: [36 inches (914 mm)] [As indicated] <Insert width>.

Dimensions in options in subparagraph below are values set by ASTM F 900 to determine default sizes and weights of framing members.

2. Gate Fabric Height: [72 inches (1830 mm) or less] [More than 72 inches (1830 mm)] [As indicated] <Insert height>.

B. Pipe and Tubing:

Retain one of first two subparagraphs below, or retain both if frames and posts are of different materials.

1. Zinc-Coated Steel: Comply with ASTM F 1043 and ASTM F 1083; [protective coating and finish to match fence framing] [manufacturer's standard protective coating and finish] <Insert finish>.

2. Aluminum: Comply with ASTM B 429/B 429M; [mill] [manufacturer's standard] <Insert finish> finish.

See ASTM F 900 if size of members is critical and revise both subparagraphs below.

3. Gate Posts: [Round tubular steel] [Rectangular tubular steel] [Round tubular aluminum] [Rectangular tubular aluminum].

4. Gate Frames and Bracing: [Round tubular steel] [Rectangular tubular steel] [Round tubular aluminum] [Rectangular tubular aluminum].

Retain one option in first paragraph below, or retain both for Contractor's option.

C. Frame Corner Construction: [Welded] [or] [assembled with corner fittings].

Retain paragraph below for gates that are manually operated. Revise if specifying automatic gate. ASTM F 2200 and UL 325 do not permit latches with automatic vehicle gates but do permit provisions for padlocking and locking devices.

D. Hardware:

1. Hinges: [180-degree inward] [180-degree outward] [360-degree inward and outward] swing.

2. Latches permitting operation from both sides of gate[ with provision for padlocking accessible from both sides of gate].

3. Padlock and Chain: <Insert requirements for padlocks and chains if not Owner furnished>.

4. Lock: [Manufacturer's standard] <Insert type> internal device[ furnished in lieu of gate latch].

5. Closer: [Manufacturer's standard] <Insert type>.

6. <Insert hardware items and accessories>.

2.5 FITTINGS

A. General: Comply with ASTM F 626.

B. Barbed Wire Arms: [Pressed steel or cast iron] [Aluminum], with clips, slots, or other means for attaching strands of barbed wire[, and means for attaching to posts] [, integral with post cap]; for each post unless otherwise indicated, and as follows:

1. Provide line posts with arms that accommodate top rail or tension wire.

2. Provide corner arms at fence corner posts.

3. Type I, single slanted arm.

Retain last subparagraph above or first subparagraph below for attaching three or fewer barbed wire strands.

4. Type II, single vertical arm.

5. Type III, V-shaped arm.

Retain last subparagraph above for attaching six barbed wire strands or subparagraph below for attaching five. Because V-shaped arms can provide a handhold, they may not be optimal for maximum-security applications where climbing is a threat.

6. Type IV, A-shaped arm.

C. Finish:

1. Metallic Coating for Pressed Steel or Cast Iron: Not less than 1.2 oz. /sq. ft. (366 g /sq. m) zinc.

ASTM F 626 specifies that the polymer coating match the color coating of the fence chain-link fabric.

a. Polymer coating over metallic coating.

2. Aluminum: Mill finish.

2.6 PRIVACY SLATS

Retain one of first three paragraphs below. If more than one material is required, indicate location of each on Drawings. Consider effect of privacy slats specified on wind and snow loads. Coordinate selection of material with direction of slat installation retained in Part 3.

Retain first paragraph below for evergreen-hedge-type lattice screen.

A. Material: PVC, UV-light stabilized, [flame resistant, four ply,] not less than [0.006 inch (0.15 mm)] [0.023 inch (0.58 mm)] thick;[ attached to not less than 0.0475-inch- (1.21-mm-) diameter, twisted galvanized wire; hedge-type lattice;] sized to fit mesh specified for direction indicated.

B. Material: Polyethylene tubular slats, not less than 0.023 inch (0.58 mm) thick, manufactured for chain-link fences from virgin polyethylene containing UV inhibitor, sized to fit mesh specified for direction indicated; with [vandal-resistant fasteners and lock strips] [fins for increased privacy factor].

C. Material: Fiber-glass-reinforced plastic, UV-light stabilized, not less than 0.06 inch (1.5 mm) thick, sized to fit mesh specified for direction indicated[; with vandal-resistant fasteners and lock strips].

Retain paragraph below only if material retained has a color selection option. If more than one color is required, indicate location of each on Drawings.

D. Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] [As indicated on Drawings] <Insert color>.

2.7 BARBED WIRE

If retaining this article, describe components for barbed wire installation, along with barbed wire arms in "Fittings" Article, to suit Project. If more than one arrangement of components is required, indicate location of each on Drawings. Barbed wire descriptions below are examples. Revise to suit product and Project.

A. Steel Barbed Wire: Comply with ASTM A 121, for two-strand barbed wire, 0.099-inch- (2.51-mm-) diameter line wire with 0.080-inch- (2.03-mm-) diameter, four-point round barbs spaced not more than 5 inches (127 mm) o.c.

1. Aluminum Coating: Type A.

2. Zinc Coating: Type Z, Class 3.

Barbs are not polymer coated.

B. Polymer-Coated, Galvanized-Steel Barbed Wire: Comply with ASTM F 1665 two-strand barbed wire, 0.080-inch- (2.03-mm-) diameter line wire with 0.080-inch- (2.03-mm-) diameter, four-point round [aluminum alloy] [galvanized-steel] barbs spaced not more than 5 inches (127 mm) o.c.:

1. Polymer Coating: [Class 1] [Class 2a] [Class 2b] over [aluminum] [zinc] [Zn-5-Al-MM-alloy]-coated steel wire.

a. Color: [Match chain-link fabric] [Dark green] [Olive green] [Brown] [Black] [As selected by Architect from manufacturer's full range], complying with ASTM F 934.

2.8 GROUT AND ANCHORING CEMENT

A. Nonshrink, Nonmetallic Grout: Premixed, factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C 1107. Provide grout, recommended in writing by manufacturer, for exterior applications.

B. Erosion-Resistant Anchoring Cement: Factory-packaged, nonshrink, nonstaining, hydraulic-controlled expansion cement formulation for mixing with potable water at Project site to create pourable anchoring, patching, and grouting compound. Provide formulation that is resistant to erosion from water exposure without needing protection by a sealer or waterproof coating and that is recommended in writing by manufacturer, for exterior applications.

PART 3 -  EXECUTION

3.1 INSTALLATION

Verify that survey in first paragraph below is specified in Section 017300 "Execution" or is otherwise available. Consider using sleeves to leave voids in new concrete substrates.

A. Examine areas and conditions, with Installer present, for compliance with requirements for[ a verified survey of property lines and legal boundaries,] site clearing, earthwork, pavement work, and other conditions affecting performance of the Work.

1. Do not begin installation before final grading is completed unless otherwise permitted by Architect.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

C. Stake locations of fence lines, gates, and terminal posts. Do not exceed intervals of 500 feet (152.5 m) or line of sight between stakes. Indicate locations of utilities, lawn sprinkler system, underground structures, benchmarks, and property monuments.

D. Install chain-link fencing to comply with ASTM F 567 and more stringent requirements indicated.

Retain first two paragraphs below for locations with rock-free, stable soil conditions. Revise if conditions include unstable or rocky soils. See ASTM F 567 default requirements.

E. Post Excavation: Drill or hand-excavate holes for posts to diameters and spacings indicated, in firm, undisturbed soil.

F. Post Setting: Set posts [in concrete] [with mechanical anchors] [by mechanically driving into soil] at indicated spacing into firm, undisturbed soil.

1. Verify that posts are set plumb, aligned, and at correct height and spacing, and hold in position during setting with concrete or mechanical devices.

Retain first subparagraph below for concrete footings.

2. Concrete Fill: Place concrete around posts to dimensions indicated and vibrate or tamp for consolidation. Protect aboveground portion of posts from concrete splatter.

Retain one of first four subparagraphs below to suit Project.

a. Exposed Concrete: Extend 2 inches (50 mm) above grade; shape and smooth to shed water.

b. Concealed Concrete: Top [2 inches (50 mm)] <Insert dimension> below grade [as indicated on Drawings ]to allow covering with surface material.

c. Posts Set into Concrete in Sleeves: Use steel pipe sleeves preset and anchored into concrete for installing posts. After posts have been inserted into sleeves, fill annular space between post and sleeve with [nonshrink, nonmetallic grout] [anchoring cement], mixed and placed to comply with anchoring material manufacturer's written instructions, and finished sloped to drain water away from post.

d. Posts Set into Voids in Concrete: Form or core drill holes not less than 5 inches (125 mm) deep and 3/4 inch (20 mm) larger than OD of post. Clean holes of loose material, insert posts, and fill annular space between post and concrete with [nonshrink, nonmetallic grout] [anchoring cement], mixed and placed to comply with anchoring material manufacturer's written instructions, and finished sloped to drain water away from post.

3. Mechanically Driven Posts: Drive into soil to depth of [30 inches (762 mm)] [36 inches (914 mm)] <Insert dimension>. Protect post top to prevent distortion.

Retain options in first paragraph below to suit Project. Where fencing changes direction by 15 degrees or more, at abrupt changes in grade, and for long stretches of fence in the range of 300 to 500 feet (91.4 to 152.5 m), manufacturers may recommend locating pull posts with braces at both sides.

G. Terminal Posts: Locate terminal end, corner, and gate posts per ASTM F 567 and terminal pull posts at changes in horizontal or vertical alignment of [15 degrees or more] [30 degrees or more] [as indicated on Drawings] <Insert requirement>.

Revise first paragraph below for unusual load conditions. Posts are usually spaced 10 feet (3 m) o.c.

H. Line Posts: Space line posts uniformly at [96 inches (2440 mm)] [10 feet (3 m)] <Insert dimension> o.c.

Retain first paragraph below if applicable.

I. Tension Wire: Install according to ASTM F 567, maintaining plumb position and alignment of fencing. Provide horizontal tension wire at the following locations:

1. Extended along [top] [and] [bottom] of fence fabric.

2. [As indicated] <Insert requirements>.

Fabric in first paragraph below is usually placed outside framework. Retain, revise, or delete dimension to suit Project. 2 inches (50 mm) complies with ASTM F 567 and is usually specified, but tennis courts require 1 inch (25 mm) between finish grade and bottom of selvage.

J. Chain-Link Fabric: Apply fabric to [outside] [inside] of enclosing framework. Leave [1 inch (25.4 mm)] [2 inches (50 mm)] between finish grade or surface and bottom selvage unless otherwise indicated.

Retain first paragraph below if applicable.

K. Privacy Slats: Install slats in direction indicated, securely locked in place.

Retain one of three subparagraphs below for installation direction. Factory-cut slats with vandal-resistant lock strips may be limited to vertical installation. Fiber-glass-reinforced plastic slats may be installed in vertical, horizontal, diagonal, and a combination of directions. PVC and polyethylene tubular slats may be installed in vertical and diagonal directions. PVC hedge-type lattice may be installed vertically. Privacy factors below are examples only.

1. [Vertically] [Horizontally], [for privacy factor of 70 to 75] <Insert privacy factor range>.

2. Diagonally, [for privacy factor of 80 to 85] <Insert privacy factor range>.

3. Direction[ and privacy factor] as indicated.

L. Barbed Wire: Install barbed wire uniformly spaced [, angled toward security side of fence] [as indicated on Drawings]. Pull wire taut, install securely to extension arms, and secure to end post or terminal arms.

M. Install gates according to manufacturer's written instructions, level, plumb, and secure for full opening without interference. Attach fabric as for fencing. Attach hardware using tamper-resistant or concealed means. Install ground-set items in concrete for anchorage. Adjust hardware for smooth operation and lubricate where necessary.

N. Gates: Adjust gates to operate smoothly, easily, and quietly, free of binding, warp, excessive deflection, distortion, nonalignment, misplacement, disruption, or malfunction, throughout entire operational range. Confirm that latches and locks engage accurately and securely without forcing or binding.

END OF SECTION 323113

	CHAIN LINK FENCES AND GATES
	323113 - 1



