Copyright 2004 AIA
MASTERSPEC Full Length
05/04 (R 05/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 03450 - ARCHITECTURAL PRECAST CONCRETE
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Architectural precast concrete cladding[ and load-bearing] units.

2. Insulated, architectural precast concrete units.

3. Brick-faced, architectural precast concrete units.

4. Stone-faced, architectural precast concrete units.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 3 Section "Cast-in-Place Concrete" for installing connection anchors in concrete.

2. Division 3 Section "Glass Fiber Reinforced Concrete."

3. Division 4 Section "Cast Stone" for wet or dry cast stone facings, trim, and accessories.

4. Division 4 Section "Unit Masonry Assemblies" for thin brick setting materials and installation after precast concrete panel production.

5. Division 5 Section "Structural Steel" for furnishing and installing connections attached to structural-steel framing.

6. Division 5 Section "Metal Fabrications" for kickers and other miscellaneous steel shapes.

7. Division 7 Section "Water Repellents" for water-repellent finish treatments.

8. Division 8 Section "Aluminum Windows" for windows set into architectural precast concrete units.

9. Division 9 Section "Ceramic Tile" for ceramic tile setting materials and installation.

1.3 DEFINITION

Retain this Article if a design reference sample has been preapproved by Architect.

A. Design Reference Sample:  Sample of approved architectural precast concrete color, finish and texture, preapproved by Architect.

1.4 PERFORMANCE REQUIREMENTS

A. Structural Performance:  Provide architectural precast concrete units and connections capable of withstanding the following design loads within limits and under conditions indicated:

1. Loads:  As indicated.

Retain subparagraph above if design loads are shown on Drawings or delete subparagraph above and retain first five subparagraphs below if including design loads here; revise requirements to suit Project, and add other performance and design criteria if applicable.

2. Dead Loads:  <Insert applicable dead loads.>

3. Live Loads:  <Insert applicable live loads.>

4. Wind Loads:  <Insert applicable wind loads or wind-load criteria, positive and negative for various parts of building as required by applicable building code or ASCE 7, including basic wind speed, importance factor, exposure category, and pressure coefficient.>

5. Seismic Loads:  <Insert applicable seismic design data including seismic performance category, importance factor, use group, seismic design category, seismic zone, site classification, site coefficient, and drift criteria.>

6. Project Specific Loads:  <Insert applicable loads.>

7. Design framing system and connections to maintain clearances at openings, to allow for fabrication and construction tolerances, to accommodate live-load deflection, shrinkage and creep of primary building structure, and other building movements as follows:

Indicate locations here or on Drawings if different movements are anticipated for different building elements.  If preferred, change deflection limits in subparagraph below to ratios such as L/300 for floors and L/200 for roofs.

a. Upward and downward movement of [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)].

Revise subparagraph below to suit local conditions.  Temperature data are available from National Climatic Data Center, www.ncdc.noaa.gov.

8. Thermal Movements:  Provide for in-plane thermal movements resulting from annual ambient temperature changes of [80 deg F (26 deg C)] [120 deg F (67 deg C)] <Insert temperature range>.

Delete subparagraph below if fire-resistance rating is not required.  Fire ratings depend on occupancy and building construction type, and are generally a building code requirement.

9. Fire-Resistance Rating:  Select material and minimum thicknesses to provide [1] [2] <Insert number>-hour fire rating.

Delete subparagraph below if window washing system is not required.  Indicate design criteria here or on Drawings for window washing system, including material and equipment.

10. Window Washing System:  Design precast units supporting window washing system indicated to resist pull-out and horizontal shear forces transmitted from window washing equipment.

Delete subparagraph below if precast units are not used in parking structures to resist impact load.  Revise loads to suit Project.  Loads are based on PCI recommendations.

11. Vehicular Impact Loads:  Design spandrel beams acting as vehicular barriers for passenger cars to resist a single [6000-lb (26.7-kN)] <Insert load> service load and [10,000-lb (44.5-kN)] <Insert load> ultimate load applied horizontally in any direction to the spandrel beam, with anchorages or attachments capable of transferring this load to the structure.  Design spandrel beams assuming the load to act at a height of 18 inches (460 mm) above the floor or ramp surface on an area not to exceed 1 sq. ft. (0.93 sq. m).

1.5 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. LEED Submittal:

Retain subparagraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  An alternative method of complying with Credit MR 4.1 and MR 4.2 requirements is to retain requirement in Division 1 Section "LEED Requirements" that gives Contractor the option and responsibility for determining how Credit MR 4.1 and MR 4.2 requirements will be met.

1. Product Data for Credit MR 4.1[ and Credit MR 4.2]:  For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content.

a. Include statement indicating costs for each product having recycled content.

C. Design Mixtures:  For each precast concrete mixture.  Include compressive strength and water-absorption tests.

D. Shop Drawings:  Detail fabrication and installation of architectural precast concrete units.  Indicate locations, plans, elevations, dimensions, shapes, and cross sections of each unit.  Indicate joints, reveals, and extent and location of each surface finish.  Indicate details at building corners.

Delete subparagraphs below not applicable to Project.

1. Indicate separate face and backup mixture locations and thicknesses.

2. Indicate welded connections by AWS standard symbols.  Detail loose and cast-in hardware and connections.

3. Indicate locations, tolerances, and details of anchorage devices to be embedded in or attached to structure or other construction.

4. Indicate locations, extent, and treatment of dry joints if two-stage casting is proposed.

5. Include plans and elevations showing unit location and sequence of erection for special conditions.

6. Indicate location of each architectural precast concrete unit by same identification mark placed on panel.

7. Indicate relationship of architectural precast concrete units to adjacent materials.

8. Indicate locations and details of brick units, including corner units and special shapes, and joint treatment.

9. Indicate locations and details of stone facings, anchors, and joint widths.

10. Design Modifications:  If design modifications are proposed to meet performance requirements and field conditions, submit design calculations and Shop Drawings.  Do not adversely affect the appearance, durability, or strength of units when modifying details or materials and maintain the general design concept.

Retain subparagraph below if retaining "Performance Requirements" Article.  Delete or modify if Architect assumes or is required by law to assume design responsibility.

11. Comprehensive engineering analysis [signed and sealed] [certified] by the qualified professional engineer responsible for its preparation.  Show governing panel types, connections, and types of reinforcement, including special reinforcement.  Indicate location, type, magnitude, and direction of loads imposed on the building structural frame from architectural precast concrete.

Retain paragraph and subparagraphs below if finishes, colors, and textures are preselected, specified, or scheduled.  Coordinate with sample panels and range samples in "Quality Assurance" Article.

E. Samples:  For each type of finish indicated on exposed surfaces of architectural precast concrete units, in sets of 3, illustrating full range of finish, color, and texture variations expected; approximately 12 by 12 by 2 inches (300 by 300 by 50 mm).

1. When other faces of precast concrete unit are exposed, include Samples illustrating workmanship, color, and texture of backup concrete as well as facing concrete.

Retain subparagraph below if Samples of thin brick facings are required.

2. Samples for each brick unit required, showing full range of color and texture expected.  Include Sample showing color and texture of joint treatment.

Retain one or both subparagraphs below if joints for thin brick facings are grouted.

a. Grout Samples for Initial Selection:  Color charts consisting of actual sections of grout showing manufacturer's full range of colors.

b. Grout Samples for Verification:  Showing color and texture of joint treatment.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

F. Welding certificates.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

G. Qualification Data:  For [Installer] [fabricator] [testing agency].

H. Material Test Reports:  For aggregates.

I. Material Certificates:  For the following items, signed by manufacturers:

Edit list below to suit Project.

1. Cementitious materials.

2. Reinforcing materials and prestressing tendons.

3. Admixtures.

4. Bearing pads.

5. Structural-steel shapes and hollow structural sections.

6. Brick units and accessories.

7. Stone anchors.

Retain paragraph below if submittal is required.

J. Source quality-control test reports.

Retain paragraph below if Contractor is responsible for field quality-control testing.  Retain option if Contractor is responsible for special inspections.

K. Field quality-control test[ and special inspection] reports.

1.6 QUALITY ASSURANCE

Retain one of first two paragraphs below if qualifying erectors.  Retain first if PCI-certified erector is required.  See PCI's Web site, www.pci.org, for current listing of erectors.

A. Installer Qualifications:  A precast concrete erector qualified and designated by PCI's Certificate of Compliance to erect Category [A (Architectural Systems) for non-load] [S2 (Complex Structural Systems) for load]-bearing members.

Retain first paragraph below if PCI-certified erector is not required or is not available in Project location.  Basis of audit is PCI MNL 127, "PCI Erector's Manual - Standards and Guidelines for the Erection of Precast Concrete Products."

B. Installer Qualifications:  A precast concrete erector who has retained a "PCI-Certified Field Auditor" to conduct a field audit of a project in same category as this Project before erection of precast concrete and who can produce an Erectors' Post-Audit Declaration.

C. Fabricator Qualifications: A firm that assumes responsibility for engineering architectural precast concrete units to comply with performance requirements.  This responsibility includes preparation of Shop Drawings and comprehensive engineering analysis by a qualified professional engineer.

Usually retain subparagraph below.  PCI plant certification was established in 1967 and is a different program than APA's plant certification established in 1993.  Consult APA or PCI for further information.

1. Participates in PCI's plant certification program[ at time of bidding] and is designated a PCI-certified plant for Group A, Category A1 - Architectural Cladding and Load Bearing Units[ or participates in APA's "Plant Certification Program for Production of Architectural Precast Concrete Products" and is designated an APA-certified plant].

Retain first paragraph below if Contractor selects testing agency for testing in addition to that required under PCI's certification program.  Testing agency is normally engaged by Owner.

D. Testing Agency Qualifications:  An independent testing agency[, acceptable to authorities having jurisdiction,] qualified according to ASTM C 1077 and ASTM E 329 for testing indicated.

E. Design Standards:  Comply with ACI 318 (ACI 318M) and design recommendations of PCI MNL 120, "PCI Design Handbook - Precast and Prestressed Concrete," applicable to types of architectural precast concrete units indicated.

F. Quality-Control Standard:  For manufacturing procedures and testing requirements, quality-control recommendations, and dimensional tolerances for types of units required, comply with PCI MNL 117, "Manual for Quality Control for Plants and Production of Architectural Precast Concrete Products."

Delete paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

G. Welding:  Qualify procedures and personnel according to AWS D1.1/D.1.1M, "Structural Welding Code - Steel"; and AWS D1.4, "Structural Welding Code - Reinforcing Steel."

Retain paragraph below if fire-rated units or assemblies are required.  Select either option, or both, if acceptable to authorities having jurisdiction.

H. Calculated Fire-Test-Response Characteristics:  Where indicated, provide architectural precast concrete units whose fire resistance has been calculated according to [ACI 216.1/TMS 0216.1, "Standard Method for Determining Fire Resistance of Concrete and Masonry Construction Assemblies,"] [PCI MNL 124, "Design for Fire Resistance of Precast Prestressed Concrete,"] and is acceptable to authorities having jurisdiction.

PCI recommends review of preproduction sample panels.  Revise number and size of sample panels in paragraph below to suit Project.

I. Sample Panels:  After sample approval and before fabricating architectural precast concrete units, produce a minimum of [2] <Insert number> sample panels approximately [16 sq. ft. (1.5 sq. m)] <Insert size> in area for review by Architect.  Incorporate full-scale details of architectural features, finishes, textures, and transitions in sample panels.

1. Locate panels where indicated or, if not indicated, as directed by Architect.

2. Damage part of an exposed-face surface for each finish, color, and texture, and demonstrate adequacy of repair techniques proposed for repair of surface blemishes.

3. After acceptance of repair technique, maintain one sample panel at manufacturer's plant and one at Project site in an undisturbed condition as a standard for judging the completed Work.

4. Demolish and remove sample panels when directed.

PCI recommends production of finish and texture range samples when color and texture uniformity concerns could be an issue, Architect or precaster has not had previous experience with specified mixture and finish, or a large project has multiple approving authorities.

J. Range Samples:  After sample panel approval and before fabricating architectural precast concrete units, produce a minimum of [3] [5] <Insert number> sets of samples, approximately [16 sq. ft. (1.5 sq. m)] <Insert number> in area, representing anticipated range of each color and texture on Project's units.  Following range sample, maintain one set of samples at Project site and remaining sample sets at manufacturer's plant as color and texture approval reference.

Delete paragraph and subparagraphs below if sample panels and range samples above will suffice and added expense of mockups is not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

K. Mockups:  After sample panel[ and range sample] approval but before production of architectural precast concrete units, construct full-sized mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

Revise or delete three subparagraphs below to suit Project.

1. Build mockup as indicated on Drawings including [aluminum framing, glass, sealants,] <Insert construction> and architectural precast concrete complete with anchors, connections, flashings, and joint fillers.

Retain first subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 1 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

2. Approved mockups may become part of the completed Work if undamaged at time of Substantial Completion.

3. Approval of mockups does not constitute approval of deviations from the Contract Documents unless such deviations are specifically approved by Architect in writing.

If retaining paragraph and subparagraphs below, determine where preconstruction testing will be specified and include requirements in that Section.  Requirements in paragraph below are limited to building a preconstruction testing mockup at a testing agency's facility.

L. Preconstruction Testing Mockup:  Provide a full-size mockup of architectural precast concrete indicated on Drawings for preconstruction testing.  Refer to Division [1] [8] <Insert Division number> Section "<Insert Section title>" for preconstruction testing requirements.

Revise or delete subparagraphs below to suit Project.  Coordinate with other Sections that include construction to be included in a preconstruction testing mockup to clearly indicate extent of work required in this Section.

1. Build preconstruction testing mockup as indicated on Drawings including [aluminum framing, glass, sealants,] <Insert construction> and architectural precast concrete complete with anchors, connections, flashings, and joint fillers.

2. Build preconstruction testing mockup at testing agency facility.

Delete paragraph below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 1.

M. Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 1 Section "Project Management and Coordination."

1.7 DELIVERY, STORAGE, AND HANDLING

A. Deliver architectural precast concrete units in such quantities and at such times to limit unloading units temporarily on the ground.

B. Support units during shipment on nonstaining shock-absorbing material.

C. Store units with adequate dunnage and bracing and protect units to prevent contact with soil, to prevent staining, and to prevent cracking, distortion, warping or other physical damage.

D. Place stored units so identification marks are clearly visible, and units can be inspected.

E. Handle and transport units in a position consistent with their shape and design in order to avoid excessive stresses which would cause cracking or damage.

F. Lift and support units only at designated points shown on Shop Drawings.

1.8 SEQUENCING

A. Furnish loose connection hardware and anchorage items to be embedded in or attached to other construction without delaying the Work.  Provide locations, setting diagrams, templates, instructions, and directions, as required, for installation.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Delete this Article unless naming fabricators.  See PCI's magazine "Ascent" or its Web site, www.pci.org, for current PCI-certified plant listings.

Retain one of two paragraphs and list of fabricators in this Article.  If retaining first paragraph, include procedure for approval of other fabricators in Instructions to Bidders.  See Division 1 Section "Product Requirements."

A. Available Fabricators:  Subject to compliance with requirements, fabricators offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Fabricators:  Subject to compliance with requirements, provide products by one of the following:

1. <Insert, in separate subparagraphs, fabricator's name; product name or designation.>

2.2 MOLD MATERIALS

A. Molds:  Rigid, dimensionally stable, non-absorptive material, warp and buckle free, that will provide continuous and true precast concrete surfaces within fabrication tolerances indicated; nonreactive with concrete and suitable for producing required finishes.

1. Mold-Release Agent:  Commercially produced liquid-release agent that will not bond with, stain or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

Delete paragraph below if not using form liners.  Form liners may be used to achieve a special off-the-form finish or to act as a template for thin or half-brick facings.  Revise to add description of selected form liner if required.

B. Form Liners:  Units of face design, texture, arrangement, and configuration [indicated] [to match those used for precast concrete design reference sample].  Furnish with manufacturer's recommended liquid-release agent that will not bond with, stain, or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

Retain paragraph below if surface retarder is applied to molds to help obtain exposed-aggregate finish.

C. Surface Retarder:  Chemical set retarder, capable of temporarily delaying final hardening of newly placed concrete mixture to depth of reveal specified.

2.3 REINFORCING MATERIALS

Retain first paragraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation.  The Steel Recycling Institute indicates that reinforcing bars are made by the electric arc furnace method, which typically has 57.5 percent postconsumer recycled content and 6.5 percent preconsumer recycled content.

A. Recycled Content of Steel Products:  Provide products with an average recycled content of steel products so postconsumer recycled content plus one-half of preconsumer recycled content is not less than [25] [60] <Insert number> percent.

Select one or more paragraphs in this Article to suit steel reinforcement requirements.  Distinguish locations of each type of reinforcement here or on Drawings.  If retaining Part 1 "Performance Requirements" Article, consider reviewing selections with fabricators.

B. Reinforcing Bars:  ASTM A 615/A 615M, Grade 60 (Grade 420), deformed.

Retain paragraph below for reinforcement that is welded or if added ductility is sought.

C. Low-Alloy-Steel Reinforcing Bars:  ASTM A 706/A 706M, deformed.

Retain galvanized reinforcing bars in paragraph below where corrosive environment or severe exposure conditions justify extra cost.  Presence of chromate film on the surface of galvanized coating is usually visible as light yellow tint on the surface.  ASTM B 201 describes a test method for determining presence of chromate coatings.

D. Galvanized Reinforcing Bars:  [ASTM A 615/A 615M, Grade 60 (Grade 420)] [ASTM A 706/A 706M], deformed bars, ASTM A 767/A 767M, Class II zinc coated, hot-dip galvanized[, and chromate wash treated after fabrication and bending].

Consider using epoxy coating where corrosive environment or severe exposure conditions justify extra cost.  In first paragraph below, retain ASTM A 775/A 775M for a bendable epoxy coating; retain ASTM A 934/A 934M for a nonbendable epoxy coating.

E. Epoxy-Coated Reinforcing Bars:  [ASTM A 615/A 615M, Grade 60 (Grade 420)] [ASTM A 706/A 706M], deformed bars, [ASTM A 775/A 775M] [or] [ASTM A 934/A 934M] epoxy coated.

F. Steel Bar Mats:  ASTM A 184/A 184M, fabricated from [ASTM A 615/A 615M, Grade 60 (Grade 420)] [ASTM A 706/A 706M], deformed bars, assembled with clips.

G. Plain-Steel Welded Wire Reinforcement:  ASTM A 185, fabricated from [as-drawn] [galvanized] steel wire into flat sheets.

H. Deformed-Steel Welded Wire Reinforcement:  ASTM A 497/A 497M, flat sheet.

I. Epoxy-Coated-Steel Wire:  ASTM A 884/A 884M, Class A coated, [plain] [deformed], flat sheet, Type [1 bendable] [2 nonbendable] coating.

J. Supports:  Suspend reinforcement from back of mold or use bolsters, chairs, spacers, and other devices for spacing, supporting, and fastening reinforcing bars and welded wire reinforcement in place according to PCI MNL 117.

2.4 PRESTRESSING TENDONS

Retain this Article if precast concrete units will be prestressed, either pretensioned or post-tensioned.

A. Prestressing Strand:  ASTM A 416/A 416M, Grade 270 (Grade 1860), uncoated, 7-wire, low-relaxation strand.

For aggressive climates, revise subparagraph below by adding an anchorage device encapsulation system consisting of caps and sleeves.

1. Coat unbonded post-tensioning strand with corrosion inhibitor passing ASTM D 1743 and sheath with polypropylene tendon sheathing.  Include anchorage devices and coupler assemblies.

2.5 CONCRETE MATERIALS

Delete materials in this Article that are not required; revise to suit Project.

A. Portland Cement:  ASTM C 150, Type I or Type III, gray, unless otherwise indicated.

Mixing with white cement will improve color uniformity of gray cement.  White cement has greater color consistency than gray cement and should be used for pastel colors.  For darker colors, variations of gray cement have less effect on final color hue.

1. For surfaces exposed to view in finished structure, mix gray with white cement, of same type, brand, and mill source.

B. Supplementary Cementitious Materials:

Select mineral or cementitious admixtures from four subparagraphs below.  Because fly ash, silica fume, and ground slag affect color uniformity, they are not recommended by PCI where appearance is important.

1. Fly Ash:  ASTM C 618, Class C or F, with maximum loss on ignition of 3 percent.

2. Metakaolin Admixture:  ASTM C 618, Class N.

3. Silica Fume Admixture:  ASTM C 1240, with optional chemical and physical requirement.

4. Ground Granulated Blast-Furnace Slag:  ASTM C 989, Grade 100 or 120.

ASTM C 33 limits deleterious substances in coarse aggregate depending on climate severity and in-service location of concrete.  Class 5S is the most restrictive designation for architectural concrete exposed to severe weathering.  PCI MNL 117 also establishes strict limits on deleterious substances for fine and coarse aggregates.

C. Normal-Weight Aggregates:  Except as modified by PCI MNL 117, ASTM C 33, with coarse aggregates complying with Class 5S.  Stockpile fine and coarse aggregates for each type of exposed finish from a single source (pit or quarry) for Project.

Revise two subparagraphs below to add descriptions of selected coarse- and fine-face aggregate colors and sources if required.

1. Face-Mixture-Coarse Aggregates:  Selected, hard, and durable; free of material that reacts with cement or causes staining; to match selected finish sample.

Retain one option from first subparagraph below or insert gradation and maximum aggregate size if known.  Fine and coarse aggregates are not always from same source.

a. Gradation:  [Uniformly graded] [Gap graded] [To match design reference sample].

2. Face-Mixture-Fine Aggregates:  Selected, natural or manufactured sand of same material as coarse aggregate, unless otherwise approved by Architect.

Lightweight aggregates in a face mixture are not recommended in cold or humid climates (if exposed to the weather) unless their performance has been verified by tests or records of previous satisfactory usage in similar environments.  If normal-weight aggregates are used in face mixture, PCI does not recommend lightweight aggregates in backup mixture due to bowing potential.

D. Lightweight Aggregates:  Except as modified by PCI MNL 117, ASTM C 330, with absorption less than 11 percent.

Delete first paragraph below if coloring admixture is not required.  Add color selection if known.

E. Coloring Admixture:  ASTM C 979, synthetic or natural mineral-oxide pigments or colored water-reducing admixtures, temperature stable, and nonfading.

F. Water:  Potable; free from deleterious material that may affect color stability, setting, or strength of concrete and complying with chemical limits of PCI MNL 117.

G. Air-Entraining Admixture:  ASTM C 260, certified by manufacturer to be compatible with other required admixtures.

H. Chemical Admixtures:  Certified by manufacturer to be compatible with other admixtures and to not contain calcium chloride, or more than 0.15 percent chloride ions or other salts by weight of admixture.

Select one or more chemical admixtures from seven subparagraphs below if chemical admixtures are permitted; limit chemical admixture types if required.  Water-reducing admixtures, Types A, D, and E, or a high-range water reducer, Type F, predominate.

1. Water-Reducing Admixtures:  ASTM C 494/C 494M, Type A.

2. Retarding Admixture:  ASTM C 494/C 494M, Type B.

3. Water-Reducing and Retarding Admixture:  ASTM C 494/C 494M, Type D.

4. Water-Reducing and Accelerating Admixture:  ASTM C 494/C 494M, Type E.

5. High-Range, Water-Reducing Admixture:  ASTM C 494/C 494M, Type F.

6. High-Range, Water-Reducing and Retarding Admixture:  ASTM C 494/C 494M, Type G.

7. Plasticizing and Retarding Admixture:  ASTM C 1017/C 1017 M.

2.6 STEEL CONNECTION MATERIALS

Edit this Article to suit Project.  Add other materials as required.

A. Carbon-Steel Shapes and Plates:  ASTM A 36/A 36M.

B. Carbon-Steel-Headed Studs:  ASTM A 108, AISI 1018 through AISI 1020, cold finished, AWS D1.1/D1.1M, Type A or B, with arc shields and with minimum mechanical properties of PCI MNL 117, Table 3.2.3.

C. Carbon-Steel Plate:  ASTM A 283/A 283M.

D. Malleable Iron Castings:  ASTM A 47/A 47M.

E. Carbon-Steel Castings:  ASTM A 27/A 27M, Grade 60-30 (Grade 415-205).

F. High-Strength, Low-Alloy Structural Steel:  ASTM A 572/A 572M.

G. Carbon-Steel Structural Tubing:  ASTM A 500, Grade B.

H. Wrought Carbon-Steel Bars:  ASTM A 675/A 675M, Grade 65 (Grade 450).

I. Deformed-Steel Wire or Bar Anchors:  ASTM A 496 or ASTM A 706/A 706M.

ASTM A 307 defines the term "studs" to include stud stock and threaded rods.

J. Carbon-Steel Bolts and Studs:  ASTM A 307, Grade A (ASTM F 568M, Property Class 4.6); carbon-steel, hex-head bolts and studs; carbon-steel nuts, ASTM A 563 (ASTM A 563M); and flat, unhardened steel washers, ASTM F 844.

High-strength bolts are used for friction-type connections between steel members and are not recommended by PCI between steel and concrete because concrete creep and crushing of concrete during bolt tightening reduce effectiveness.

K. High-Strength Bolts and Nuts:  ASTM A 325 (ASTM A 325M), Type 1, heavy hex steel structural bolts; heavy hex carbon-steel nuts, ASTM A 563 (ASTM A 563M); and hardened carbon-steel washers, ASTM F 436 (ASTM F 436M).

Retain paragraph and subparagraphs below if galvanized finish is required.  Revise locations of galvanized items if required.  Field welding should generally not be permitted on galvanized elements unless galvanizing is removed or acceptable welding procedures are submitted.  Hot-dip galvanized finish provides greater corrosion resistance than electrodeposited zinc coating.  Electrodeposition is usually limited to threaded fasteners.

L. Zinc-Coated Finish:  For exterior steel items[, steel in exterior walls,] and items indicated for galvanizing, apply zinc coating by [hot-dip process according to ASTM A 123/A 123M or ASTM A 153/A 153M] [electrodeposition according to ASTM B 633, SC 3, Types 1 and 2].

1. For steel shapes, plates, and tubing to be galvanized, limit silicon content of steel to less than 0.03 percent or to between 0.15 and 0.25 percent or limit sum of silicon and 2.5 times phosphorous content to 0.09 percent.

2. Galvanizing Repair Paint:  High-zinc-dust-content paint with dry film containing not less than 94 percent zinc dust by weight, and complying with DOD-P-21035A or SSPC-Paint 20.

Retain first paragraph below if paint finish is required.  Revise locations of priming if required.  MPI 79 in first option provides some corrosion protection, while SSPC-Paint 25, without topcoating, provides minimal corrosion protection.

M. Shop-Primed Finish:  Prepare surfaces of nongalvanized steel items, except those surfaces to be embedded in concrete, according to requirements in SSPC-SP 3 and shop-apply [lead- and chromate-free, rust-inhibitive primer, complying with performance requirements in MPI 79] [SSPC-Paint 25] according to SSPC-PA 1.

N. Welding Electrodes:  Comply with AWS standards.

2.7 STAINLESS-STEEL CONNECTION MATERIALS

Delete this Article if not required.  Retain when resistance to staining merits extra cost in parking structures and other high-moisture or corrosive areas.

A. Stainless-Steel Plate:  ASTM A 666, Type 304, of grade suitable for application.

B. Stainless-Steel Bolts and Studs:  ASTM F 593, Alloy 304 or 316, hex-head bolts and studs; stainless-steel nuts; and flat, stainless-steel washers.

1. Lubricate threaded parts of stainless-steel bolts with an antiseize thread lubricant during assembly.

C. Stainless-Steel-Headed Studs:  ASTM A 276, with minimum mechanical properties of PCI MNL 117, Table 3.2.3.

2.8 BEARING PADS

Delete this Article if not applicable.  Choice of bearing pad can usually be left to fabricator; coordinate selection with structural engineer if required.

A. Provide one of the following bearing pads for architectural precast concrete units[ as recommended by precast fabricator for application]:

1. Elastomeric Pads:  AASHTO M 251, plain, vulcanized, 100 percent polychloroprene (neoprene) elastomer, molded to size or cut from a molded sheet, Type A durometer hardness of 50 to 70, ASTM D 2240, minimum tensile strength 2250 psi (15.5 MPa), ASTM D 412.

2. Random-Oriented, Fiber-Reinforced Elastomeric Pads:  Preformed, randomly oriented synthetic fibers set in elastomer.  Type A durometer hardness of 70 to 90, ASTM D 2240; capable of supporting a compressive stress of 3000 psi (20.7 MPa) with no cracking, splitting, or delaminating in the internal portions of pad.  Test one specimen for every 200 pads used in Project.

3. Cotton-Duck-Fabric-Reinforced Elastomeric Pads:  Preformed, horizontally layered cotton-duck fabric bonded to an elastomer; Type A durometer hardness of 80 to 100, ASTM D 2240; complying with AASHTO's "AASHTO Load and Resistance Factor Design (LRFD) Bridge Design Specifications, Division II, Section 18.10.2, or with MIL-C-882E.

4. Frictionless Pads:  Tetrafluoroethylene (Teflon), glass-fiber reinforced, bonded to stainless or mild-steel plate, of type required for in-service stress.

5. High-Density Plastic:  Multimonomer, nonleaching, plastic strip.

2.9 ACCESSORIES

A. Reglets:  Specified in Division 7 Section "Sheet Metal Flashing and Trim."

Select paragraph above or first paragraph below if applicable.  Coordinate reglet material with counterflashing materials and details.

B. Reglets:  [PVC extrusions,] [Stainless steel, Type 302 or 304,] [Copper,] felt or fiber filled, or with face opening of slots covered.

C. Precast Accessories:  Provide clips, hangers, plastic or steel shims, and other accessories required to install architectural precast concrete units.

2.10 GROUT MATERIALS

Add other proprietary grout systems to suit Project.  Show locations of each grout here or on Drawings if retaining more than one type.

A. Sand-Cement Grout:  Portland cement, ASTM C 150, Type I, and clean, natural sand, ASTM C 144 or ASTM C 404.  Mix at ratio of 1 part cement to 2-1/2 parts sand, by volume, with minimum water required for placement and hydration.

Retain first paragraph below if nonshrink grout is required or if cement-grout shrinkage could cause structural deficiency.  For critical installations, require manufacturer to provide field supervision.

B. Nonmetallic, Nonshrink Grout:  Premixed, nonmetallic, noncorrosive, nonstaining grout containing selected silica sands, portland cement, shrinkage-compensating agents, plasticizing and water-reducing agents, complying with ASTM C 1107, Grade A for drypack and Grades B and C for flowable grout and of consistency suitable for application within a 30-minute working time.

C. Epoxy-Resin Grout:  Two-component, mineral-filled epoxy resin; ASTM C 881/C 881M, of type, grade, and class to suit requirements.

2.11 THIN BRICK UNITS AND ACCESSORIES

Retain this Article if specifying thin veneer brick-faced precast concrete panels.  Type TBX brick units feature the tightest dimensional tolerances but may be too dimensionally variable to fit securely within form liner templates.  Select thin brick manufacturer and product and retain paragraph and subparagraphs below or establish an allowance.

A. Thin Brick Units:  ASTM C 216, Type FBX or ASTM C 1088, Grade Exterior, Type TBX, [not less than 1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] thick with a tolerance of plus or minus 1/16 inch (1.6 mm), and as follows:

Retain one of two subparagraphs and list of manufacturers and products below or establish an allowance.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. <Insert, in separate subparagraphs, manufacturer's name; product name or designation.>

Select from first five subparagraphs below for IP face sizes with equivalent metric dimensions or sixth subparagraph for inserting another face size.  Verify availability of sizes.

3. Face Size:  2-1/4 inches (57 mm) high by 8 inches (203 mm) long.

4. Face Size:  2-1/4 inches (57 mm) high by 7-1/2 to 7-5/8 inches (190 to 194 mm) long.

5. Face Size:  2-3/4 to 2-13/16 inches (70 to 71 mm) high by 7-1/2 to 7-5/8 inches (190 to 194 mm) long.

6. Face Size:  3-1/2 to 3-5/8 inches (89 to 92 mm) high by 7-1/2 to 7-5/8 inches (190 to 194 mm) long.

7. Face Size:  3-1/2 to 3-5/8 inches (89 to 92 mm) high by 11-1/2 to 11-5/8 inches (292 to 295 mm) long.

8. Face Size: <Insert dimensions.>

9. [Where indicated to "match existing," ]provide thin brick matching color, texture, and face size of existing adjacent brick work.

a. <Insert information on existing brick if known.>

Select from first four subparagraphs below for products manufactured to metric face sizes; select fifth subparagraph for inserting another face size.  Verify availability of sizes.

10. Face Size:  57 mm high by 190 mm long.

11. Face Size:  70 mm high by 190 mm long.

12. Face Size:  90 mm high by 190 mm long.

13. Face Size:  90 mm high by 290 mm long.

14. Face Size: <Insert dimensions.>

Show details of special conditions and shapes on Drawings if required.

15. Special Shapes:  Include corners, edge corners, and end edge corners.

PCI states that thin brick units with higher rates of absorption than values in first subparagraph below should be wetted before placing concrete to improve bond.  Before retaining below, verify that thin brick selected complies with requirements.

16. Initial Rate of Absorption:  Less than 30 g/30 sq. in. (30 g/194 sq. cm) per minute; ASTM C 67.

17. Efflorescence:  Tested according to ASTM C 67 and rated "not effloresced."

Delete subparagraph below if surface-coated thin brick is not used.

18. Surface Coating:  Thin brick with colors or textures applied as coatings shall withstand 50 cycles of freezing and thawing; ASTM C 67 with no observable difference in applied finish when viewed from 10 feet (3 m).

Edit subparagraph below to suit Project or delete if brick is specified by product name.  Options are examples of descriptive requirements for appearance where a proprietary specification cannot be used.  If approving a color range for brick, view sufficient area of loose bricks or a completed building to make an informed determination.

19. Face Color and Texture:  [Match Architect's samples] [Medium brown, wire cut] [Full-range red, sand molded] [Gray, velour].

Retain subparagraph below, deleting inapplicable descriptions if required.

20. Back Surface Texture:  Scored, combed, wire roughened, ribbed, keybacked, or dovetailed.

Retain first paragraph below if mortar setting brick joints before placing precast concrete mix.

B. Sand-Cement Mortar:  Portland cement, ASTM C 150, Type I, and clean, natural sand, ASTM C 144.  Mix at ratio of 1 part cement to 4 parts sand, by volume, with minimum water required for placement.

Delete paragraph and subparagraphs below if not filling thin brick unit joints with pointing grout after precast concrete panel production.

C. Latex-Portland Cement Pointing Grout:  ANSI A118.6 and as follows:

Select one or both types of grout from first two subparagraphs below.

1. Dry-grout mixture, factory prepared, of portland cement, graded aggregate, and dry, redispersible, ethylene-vinyl-acetate additive for mixing with water; uniformly colored.

2. Commercial portland cement grout, factory prepared, with liquid styrene-butadiene rubber or acrylic-resin latex additive; uniformly colored.

3. Colors:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

2.12 STONE MATERIALS AND ACCESSORIES

Retain this Article if stone facing is required.  Performance criteria, preconstruction material testing, material quality, fabrication, and finish requirements are usually specified in Division 4 Section "Dimension Stone Cladding." Replace paragraph below with stone requirements if preferred.

A. Stone facing for architectural precast concrete is specified in Division 4 Section "Dimension Stone Cladding."

Anchors are generally supplied by stone fabricator or, in some cases, by precaster.  Specify supplier.  Anchors may be toe in, toe out, or dowels.

B. Anchors:  Stainless steel, ASTM A 666, Type 304, of temper and diameter required to support loads without exceeding allowable design stresses.

Grommets will usually be required if filling dowel holes with rigid epoxy.

1. Fit each anchor leg with neoprene grommet collar of width at least twice the diameter and of length at least five times the diameter of anchor.

C. Sealant Filler:  ASTM C 920, low-modulus, multicomponent, nonsag urethane sealant complying with requirements in Division 7 Section "Joint Sealants" and that is nonstaining to stone substrate.

Dowel hole filling is used to prevent water intrusion into stone and future discoloration at anchor locations.  Retain paragraph above for flexible filler or first paragraph and subparagraph below for rigid filler.

D. Epoxy Filler:  ASTM C 881/C 881M, 100 percent solids, sand-filled nonshrinking, nonstaining of type, class, and grade to suit application.

1. Elastomeric Anchor Sleeve:  1/2 inch (13 mm) long, Type A durometer hardness of 60, ASTM D 2240.

E. Bond Breaker:  [Preformed, compressible, resilient, nonstaining, nonwaxing, closed-cell polyethylene foam pad, nonabsorbent to liquid and gas, 1/8 inch (3.2 mm) thick] [Polyethylene sheet, ASTM D 4397, 6 to 10 mils (0.15 to 0.25 mm) thick].

2.13 INSULATED PANEL ACCESSORIES

Retain this Article if insulated, architectural precast concrete panels are required.  Select insulation material from one of three paragraphs below; if using more then one type, identify location of each on Drawings.

A. Molded-Polystyrene Board Insulation:  ASTM C 578, Type [I, 0.90 lb/cu. ft. (15 kg/cu. m)] [VIII, 1.15 lb/cu. ft. (18 kg/cu. m)] [II, 1.35 lb/cu. ft. (22 kg/cu. m)]; [square] [ship-lap] edges; with R-value of <Insert value> and thickness of <Insert dimension>.

B. Extruded-Polystyrene Board Insulation:  ASTM C 578, Type [IV, 1.60 lb/cu. ft. (26 kg/cu. m)] [X, 1.30 lb/cu. ft. (21 kg/cu. m)] [VI, 1.80 lb/cu. ft. (29 kg/cu. m)]; [square] [ship-lap] edges; with R-value of <Insert value> and thickness of <Insert dimension>.

C. Polyisocyanurate Board Insulation:  ASTM C 591, Type [I, 1.8 lb/cu. ft. (29 kg/cu. m)] [IV, 2 lb/cu. ft. (32 kg/cu. m)] [II, 2.5 lb/cu. ft. (40 kg/cu. m)] unfaced, with R-value of <Insert value> and thickness of <Insert dimension>.

Select wythe connectors from paragraph below.

D. Wythe Connectors:  [Glass-fiber and vinyl-ester polymer connectors] [Polypropylene pin connectors] [Stainless-steel pin connectors] [Bent galvanized reinforcing bars or galvanized welded wire trusses] [Cylindrical metal sleeve anchors] manufactured to connect wythes of precast concrete panels.

2.14 CONCRETE MIXTURES

A. Prepare design mixtures for each type of precast concrete required.

Revise subparagraph below if fly ash, silica fume, or metakaolin and silica fume are permitted.  Revise percentages to suit Project.

1. Limit use of fly ash and silica fume to 20 percent of portland cement by weight; limit metakaolin and silica fume to 10 percent of portland cement by weight.

B. Design mixtures may be prepared by a qualified independent testing agency or by qualified precast plant personnel at architectural precast concrete fabricator's option.

C. Limit water-soluble chloride ions to maximum percentage by weight of cement permitted by ACI 318 (ACI 318M) or PCI MNL 117 when tested according to ASTM C 1218/C 1218M.

Architectural precast concrete units may be manufactured with a separate architectural face mixture and a structural backup mixture.  Face and backup mixtures should have similar shrinkage and expansion coefficients.  Similar water-cementitious materials ratios and cement-aggregate ratios are recommended by PCI to limit bowing or warping.  Retain first option in paragraph below if lightweight backup concrete mix is required; second option if normal-weight face and backup mixtures are required; third option if full-depth, normal-weight mixture is required; or fourth option if choice of normal-weight face and backup mixtures or full-depth mixtures is fabricator's option.

D. Normal-Weight Concrete Mixtures:  Proportion [face mixtures] [face and backup mixtures] [full-depth mixture] [face and backup mixtures or full-depth mixtures, at fabricator's option] by either laboratory trial batch or field test data methods according to ACI 211.1, with materials to be used on Project, to provide normal-weight concrete with the following properties:

Retain subparagraph below or revise to suit Project.  Higher-strength mixtures may be available; verify availability with fabricators.

1. Compressive Strength (28 Days):  5000 psi (34.5 MPa) minimum.

Water-cementitious materials ratio of 0.40 to 0.45 is usual for architectural precast concrete.  Lower ratios may be possible with use of high-range water reducers.  Revise ratio in subparagraph below to suit Project.

2. Maximum Water-Cementitious Materials Ratio:  0.45.

Water absorption indicates susceptibility to weather staining.  PCI states that limits in paragraph below are suitable for average exposures.  Different parts of a single panel cannot be produced with different absorptions.  Verify that fabricators can produce units with lower water absorption because special consolidation techniques to increase concrete density are required.

E. Water Absorption:  6 percent by weight or 14 percent by volume, tested according to PCI MNL 117.

Lightweight backup mixtures must be compatible with normal-weight face mixtures to minimize bowing or warping.  Retain paragraph below if required or as an option if satisfactory durability and in-service performance are verified by fabricator.  Coordinate with selection of normal-weight face mixture option above.

F. Lightweight Concrete Backup Mixtures:  Proportion mixtures by either laboratory trial batch or field test data methods according to ACI 211.2, with materials to be used on Project, to provide lightweight concrete with the following properties:

Retain subparagraph below or revise to suit Project.  Higher-strength mixtures may be available; verify availability with fabricators.

1. Compressive Strength (28 Days):  5000 psi (34.5 MPa).

Increase or decrease unit weight in subparagraph below to suit Project.  Coordinate with lightweight-aggregate supplier and architectural precast concrete fabricator.  Lightweight concretes with lightweight and normal-weight aggregate in mixture will usually be heavier than unit weight below.

2. Unit Weight:  Calculated equilibrium unit weight of 115 lb/cu. ft. (1842 kg/cu. m), plus or minus 3 lb/cu. ft. (48 kg/cu. m), according to ASTM C 567.

G. Add air-entraining admixture at manufacturer's prescribed rate to result in concrete at point of placement having an air content complying with PCI MNL 117.

H. When included in design mixtures, add other admixtures to concrete mixtures according to manufacturer's written instructions.

2.15 MOLD FABRICATION

A. Molds:  Accurately construct molds, mortar tight, of sufficient strength to withstand pressures due to concrete-placement operations and temperature changes and for prestressing and detensioning operations.  Coat contact surfaces of molds with release agent before reinforcement is placed.  Avoid contamination of reinforcement and prestressing tendons by release agent.

Delete form liners in subparagraph below unless needed to produce exposed surface finish.

1. Place form liners accurately to provide finished surface texture indicated.  Provide solid backing and supports to maintain stability of liners during concrete placement.  Coat form liner with form-release agent.

B. Maintain molds to provide completed architectural precast concrete units of shapes, lines, and dimensions indicated, within fabrication tolerances specified.

1. Form joints are not permitted on faces exposed to view in the finished work.

Select one option from subparagraph below; show details on Drawings or revise description to add dimensions.  Sharp edges or corners of precast concrete units are vulnerable to chipping.

2. Edge and Corner Treatment:  Uniformly [chamfered] [radiused].

2.16 THIN BRICK FACINGS

Retain this Article if using thin or half-brick facings on architectural precast concrete units.

A. Place form liner templates accurately to provide grid for thin brick facings.  Provide solid backing and supports to maintain stability of liners while placing thin bricks and during concrete placement.

B. Securely place thin brick units face down into form liner pockets and place concrete backing mixture.

Delete first two paragraphs and associated subparagraph below if bonding back of thin brick directly to concrete instead of using mortar.

C. Completely fill joint cavities between thin brick units with sand-cement mortar, and place precast concrete backing mixture while sand-cement mortar is still fluid enough to ensure bond.

Retain first paragraph and subparagraph below if grouting is required.  Delete if joints will remain fully recessed as cast.

D. Mix and install grout according to ANSI A108.10.  Completely fill joint cavities between thin brick units with grout, and compress into place without spreading grout onto faces of thin brick units.  Remove excess grout immediately to prevent staining of brick.

Select joint profile from options in subparagraph below or revise to suit Project.  Joints are placed in order of decreasing weathertightness according to BIA Technical Note 21C.

1. Tool joints to a [slightly concave] [grapevine] [V-]shape when pointing grout is thumbprint hard.

E. Clean faces and joints of brick facing.

2.17 STONE FACINGS

Retain this Article if stone facing is required.

A. Accurately position stone facings to comply with requirements and in locations indicated on Shop Drawings.  Install anchors, supports, and other attachments indicated or necessary to secure stone in place.  Keep concrete reinforcement a minimum of 3/4 inch (19 mm) from the back surface of stone.  Use continuous spacers to obtain uniform joints of widths indicated and with edges and faces aligned according to established relationships and indicated tolerances.

Retain subparagraph below and revise anchor spacing if required as a result of preconstruction testing of stone anchors for shear and tension specified in Division 4 Section "Dimension Stone Cladding."

1. Stone to Precast Anchorages:  Provide anchors in numbers, types and locations required to satisfy specified performance criteria, but not less than 2 anchors per stone unit of less than 2 sq. ft. (0.19 sq. m) in area and 4 anchors per unit of less than 12 sq. ft. (1.1 sq. m) in area; for units larger than 12 sq. ft. (1.1 sq. m) in area, provide anchors spaced not more than 24 inches (600 mm) o.c. horizontally and vertically.  Locate anchors a minimum of 6 inches (150 mm) from stone edge.

Retain one of two options in paragraph below if sealing dowel holes.  Use sealant if flexible filler is required; use epoxy if rigid filler is required.

B. Fill anchor holes with [sealant filler and install anchors] [epoxy filler and install anchors with elastomeric anchor sleeve at back surface of stone].

Retain one of two subparagraphs below.  PCI recommends no bonding between stone facing and precast concrete to minimize bowing, cracking, and staining of stone.

1. Install polyethylene sheet to prevent bond between back of stone facing and concrete substrate and to ensure no passage of precast matrix to stone surface.

2. Install 1/8-inch (3-mm) polyethylene-foam bond breaker to prevent bond between back of stone facing and concrete substrate and to ensure no passage of precast matrix to stone surface.  Maintain minimum projection requirements of stone anchors into concrete substrate.

2.18 FABRICATION

A. Cast-in Anchors, Inserts, Plates, Angles, and Other Anchorage Hardware:  Fabricate anchorage hardware with sufficient anchorage and embedment to comply with design requirements.  Accurately position for attachment of loose hardware, and secure in place during precasting operations.  Locate anchorage hardware where it does not affect position of main reinforcement or concrete placement.

1. Weld-headed studs and deformed bar anchors used for anchorage according to AWS D1.1/D1.1M and AWS C5.4, "Recommended Practices for Stud Welding."

Coordinate first paragraph below with Division 5 Section "Metal Fabrications" for furnishing and installing loose hardware items.

B. Furnish loose hardware items including steel plates, clip angles, seat angles, anchors, dowels, cramps, hangers, and other hardware shapes for securing architectural precast concrete units to supporting and adjacent construction.

C. Cast-in reglets, slots, holes, and other accessories in architectural precast concrete units as indicated on the Contract Drawings.

Delete first paragraph below if not applicable.

D. Cast-in openings larger than 10 inches (250 mm) in any dimension.  Do not drill or cut openings or prestressing strand without Architect's approval.

E. Reinforcement:  Comply with recommendations in PCI MNL 117 for fabricating, placing, and supporting reinforcement.

1. Clean reinforcement of loose rust and mill scale, earth, and other materials that reduce or destroy the bond with concrete.  When damage to epoxy-coated reinforcing exceeds limits specified in ASTM A 775/A 775M, repair with patching material compatible with coating material and epoxy coat bar ends after cutting.

2. Accurately position, support, and secure reinforcement against displacement during concrete-placement and consolidation operations.  Completely conceal support devices to prevent exposure on finished surfaces.

3. Place reinforcement to maintain at least 3/4-inch (19-mm) minimum coverage.  Arrange, space, and securely tie bars and bar supports to hold reinforcement in position while placing concrete.  Direct wire tie ends away from finished, exposed concrete surfaces.

4. Place reinforcing steel and prestressing strand to maintain at least 3/4-inch (19-mm) minimum concrete cover.  Increase cover requirements for reinforcing steel to 1-1/2 inches (38 mm) when units are exposed to corrosive environment or severe exposure conditions.  Arrange, space, and securely tie bars and bar supports to hold reinforcement in position while placing concrete.  Direct wire tie ends away from finished, exposed concrete surfaces.

5. Install welded wire fabric in lengths as long as practicable.  Lap adjoining pieces at least one full mesh spacing and wire tie laps, where required by design.  Offset laps of adjoining widths to prevent continuous laps in either direction.

F. Reinforce architectural precast concrete units to resist handling, transportation, and erection stresses.

Delete first paragraph and subparagraphs below if no precast, prestressed architectural concrete units are required.  Option to prestress may be left to fabricator if objective is to aid handling and to control cracking of units during installation.

G. Prestress tendons for architectural precast concrete units by either pretensioning or post-tensioning methods.  Comply with PCI MNL 117.

Revise release or post-tensioning strength in first subparagraph below to an actual compressive strength if required.  PCI permits a release strength as low as 2500 psi (17.2 MPa) for normal-weight concrete and 3000 psi (20.7 MPa) for lightweight concrete.

1. Delay detensioning or post-tensioning of precast, prestressed architectural concrete units until concrete has reached its indicated minimum design release compressive strength as established by test cylinders cured under same conditions as concrete.

2. Detension pretensioned tendons either by gradually releasing tensioning jacks or by heat- cutting tendons, using a sequence and pattern to prevent shock or unbalanced loading.

3. If concrete has been heat cured, detension while concrete is still warm and moist to avoid dimensional changes that may cause cracking or undesirable stresses.

4. Protect strand ends and anchorages with bituminous, zinc-rich, or epoxy paint to avoid corrosion and possible rust spots.

H. Comply with requirements in PCI MNL 117 and requirements in this Section for measuring, mixing, transporting, and placing concrete.  After concrete batching, no additional water may be added.

Retain first paragraph below if a separate face mixture is required or is Contractor's option.

I. Place face mixture to a minimum thickness after consolidation of the greater of 1 inch (25 mm) or 1.5 times the maximum aggregate size, but not less than the minimum reinforcing cover specified.

J. Place concrete in a continuous operation to prevent seams or planes of weakness from forming in precast concrete units.

1. Place backup concrete mixture to ensure bond with face-mixture concrete.

K. Thoroughly consolidate placed concrete by internal and external vibration without dislocating or damaging reinforcement and built-in items, and minimize pour lines, honeycombing, or entrapped air on surfaces.  Use equipment and procedures complying with PCI MNL 117.

1. Place self-consolidating concrete without vibration according to PCI TR-6, "Interim Guidelines for the Use of Self-Consolidating Concrete in Precast/Prestressed Concrete Institute Member Plants."

L. Comply with PCI MNL 117 for hot- and cold-weather concrete placement.

M. Identify pickup points of architectural precast concrete units and orientation in structure with permanent markings, complying with markings indicated on Shop Drawings.  Imprint or permanently mark casting date on each architectural precast concrete unit on a surface that will not show in finished structure.

N. Cure concrete, according to requirements in PCI MNL 117, by moisture retention without heat or by accelerated heat curing using low-pressure live steam or radiant heat and moisture.  Cure units until compressive strength is high enough to ensure that stripping does not have an effect on performance or appearance of final product.

O. Discard and replace architectural precast concrete units that do not comply with requirements, including structural, manufacturing tolerance, and appearance, unless repairs meet requirements in PCI MNL 117 and Architect's approval.

2.19 INSULATED PANEL CASTING

Delete this Article if integrally insulated panels are not required.

A. Cast and screed supported wythe over mold.

B. Place insulation boards abutting edges and ends of adjacent boards.  Insert wythe connectors through insulation, and consolidate concrete around connectors according to connector manufacturer's written instructions.

C. Cast and screed top wythe to meet required finish.

2.20 FABRICATION TOLERANCES

A. Fabricate architectural precast concrete units straight and true to size and shape with exposed edges and corners precise and true so each finished panel complies with PCI MNL 117 product tolerances as well as position tolerances for cast-in items.

Select paragraph above or first paragraph and subparagraphs below.  PCI MNL 117 product tolerances, referenced above and listed below, are standardized throughout the industry.

B. Fabricate architectural precast concrete units straight and true to size and shape with exposed edges and corners precise and true so each finished panel complies with the following product tolerances:

1. Overall Height and Width of Units, Measured at the Face Exposed to View:  As follows:

a. 10 feet (3 m) or under, plus or minus 1/8 inch (3 mm).

b. 10 to 20 feet (3 to 6 m), plus 1/8 inch (3 mm), minus 3/16 inch (5 mm).

c. 20 to 40 feet (6 to 12 m), plus or minus 1/4 inch (6 mm).

d. Each additional 10 feet (3 m), plus or minus 1/16 inch (1.5 mm).

2. Overall Height and Width of Units, Measured at the Face Not Exposed to View:  As follows:

a. 10 feet (3 m) or under, plus or minus 1/4 inch (6 mm).

b. 10 to 20 feet (3 to 6 m), plus 1/4 inch (6 mm), minus 3/8 inch (10 mm).

c. 20 to 40 feet (6 to 12 m), plus or minus 3/8 inch (10 mm).

d. Each additional 10 feet (3 m), plus or minus 1/8 inch (3 mm).

3. Total Thickness or Flange Thickness:  Plus 1/4 inch (6 mm), minus 1/8 inch (3 mm).

4. Rib Thickness:  Plus or minus 1/8 inch (3 mm).

5. Rib to Edge of Flange:  Plus or minus 1/8 inch (3 mm).

6. Distance between Ribs:  Plus or minus 1/8 inch (3 mm).

7. Variation from Square or Designated Skew (Difference in Length of the Two Diagonal Measurements):  Plus or minus 1/8 inch per 72 inches (3 mm per 1830 mm) or 1/2 inch (13 mm) total, whichever is greater.

8. Length and Width of Block-outs and Openings within One Unit:  Plus or minus 1/4 inch (6 mm).

9. Location and Dimension of Block-outs Hidden from View and Used for HVAC and Utility Penetrations:  Plus or minus 3/4 inch (19 mm).

10. Dimensions of Haunches:  Plus or minus 1/4 inch (6 mm).

11. Haunch Bearing Surface Deviation from Specified Plane:  Plus or minus 1/8 inch (3 mm).

12. Difference in Relative Position of Adjacent Haunch Bearing Surfaces from Specified Relative Position:  Plus or minus 1/4 inch (6 mm).

13. Bowing:  Plus or minus L/360, maximum 1 inch (25 mm).

14. Local Smoothness:  1/4 inch per 10 feet (6 mm per 3 m).

15. Warping:  1/16 inch per 12 inches (1.5 mm per 300 mm) of distance from nearest adjacent corner.

16. Tipping and Flushness of Plates:  Plus or minus 1/4 inch (6 mm).

17. Dimensions of Architectural Features and Rustications:  Plus or minus 1/8 inch (3 mm).

C. Position Tolerances:  For cast-in items measured from datum line location, as indicated on Shop Drawings.

1. Weld Plates:  Plus or minus 1 inch (25 mm).

2. Inserts:  Plus or minus 1/2 inch (13 mm).

3. Handling Devices:  Plus or minus 3 inches (75 mm).

4. Reinforcing Steel and Welded Wire Fabric:  Plus or minus 1/4 inch (6 mm) where position has structural implications or affects concrete cover; otherwise, plus or minus 1/2 inch (13 mm).

5. Reinforcing Steel Extending out of Member:  Plus or minus 1/2 inch (13 mm) of plan dimensions.

6. Tendons:  Plus or minus 1/4 inch (6 mm), vertical; plus or minus 1 inch (25 mm), horizontal.

7. Location of Rustication Joints:  Plus or minus 1/8 inch (3 mm).

8. Location of Opening within Panel:  Plus or minus 1/4 inch (6 mm).

9. Location of Flashing Reglets:  Plus or minus 1/4 inch (6 mm).

10. Location of Flashing Reglets at Edge of Panel:  Plus or minus 1/8 inch (3 mm).

11. Reglets for Glazing Gaskets:  Plus or minus 1/8 inch (3 mm).

12. Electrical Outlets, Hose Bibs:  Plus or minus 1/2 inch (13 mm).

13. Location of Bearing Surface from End of Member:  Plus or minus 1/4 inch (6 mm).

14. Allowable Rotation of Plate, Channel Inserts, and Electrical Boxes:  2-degree rotation or 1/4 inch (6 mm) maximum over the full dimension of unit.

15. Position of Sleeve:  Plus or minus 1/2 inch (13 mm).

16. Location of Window Washer Track or Buttons:  Plus or minus 1/8 inch (3 mm).

Delete paragraph and subparagraphs below if brick-faced architectural units are not used.

D. Brick-Faced Architectural Precast Concrete Units:  Restrict the following misalignments to 2 percent of number of bricks in a unit.

1. Alignment of Mortar Joints:

a. Jog in Alignment:  1/8 inch (3 mm).

b. Alignment with Panel Centerline:  Plus or minus 1/8 inch (3 mm).

2. Variation in Width of Exposed Mortar Joints:  Plus or minus 1/8 inch (3 mm).

3. Tipping of Individual Bricks from the Panel Plane of Exposed Brick Surface:  Plus 1/16 inch (1.5 mm); minus 1/4 inch (6 mm) less than or equal to depth of form liner joint.

4. Exposed Brick Surface Parallel to Primary Control Surface of Panel:  Plus 1/4 inch (6 mm); minus 1/8 inch (3 mm).

5. Individual Brick Step in Face from Panel Plane of Exposed Brick Surface:  Plus 1/16 inch (1.5 mm); minus 1/4 inch (6 mm) less than or equal to depth of form liner joint.

Delete paragraph and subparagraphs below if stone veneer-faced architectural precast units are not used.

E. Stone Veneer-Faced Architectural Precast Concrete Units:

Tolerances in three subparagraphs below are generally appropriate for smooth-finished stone.  Retain, delete, or revise to suit Project.

1. Variation in Cross-Sectional Dimensions:  For thickness of walls from dimensions indicated:  Plus or minus 1/4 inch (6 mm).

2. Variation in Joint Width:  1/8 inch in 36 inches (3 mm in 900 mm) or a quarter of nominal joint width, whichever is less.

Revise or delete subparagraph below for natural-cleft, thermal, and similar finishes.

3. Variation in Plane between Adjacent Stone Units (Lipping):  1/16 inch (1.5 mm) difference between planes of adjacent units.

2.21 FINISHES

A. Panel faces shall be free of joint marks, grain, and other obvious defects.  Corners, including false joints shall be uniform, straight, and sharp.  Finish exposed-face surfaces of architectural precast concrete units to match approved [design reference sample] [sample panels] [mockups] and as follows:

This Article presumes Architect has preapproved one or more design reference samples.  Include complete description of design reference sample here.  If preapproving fabricators, coordinate with "Manufacturers" Article.  Revise if multiple samples are approved.

1. Design Reference Sample:  <Insert description and identify fabricator and code number of sample.>

Delete subparagraph below if not required.  If retaining, revise and add reference number; PCI publishes numbered, color photographs of 428 precast concrete finishes; see PCI's Web site, www.pci.org.  Add reference number combinations if more than one finish is required.

2. PCI's "Architectural Precast Concrete - Color and Texture Selection Guide," of plate numbers indicated.

Select type of finish from subparagraphs below if needed.  If more than one finish is required, add locations to finish descriptions or indicate on Drawings.  Add more-detailed descriptions of finishes outlined below if greater definition, such as light, medium, or deep, is required,.  See PCI MNL 117 for more information on finishes.  An as-cast finish generally results in a mottled surface or non-uniform finish.

3. As-Cast Surface Finish:  Provide surfaces free of pockets, sand streaks, and honeycombs.

4. Textured-Surface Finish:  Impart by form liners or inserts to provide surfaces free of pockets, streaks, and honeycombs, with uniform color and texture.

5. Bushhammer Finish:  Use power or hand tools to remove matrix and fracture coarse aggregates.

6. Exposed-Aggregate Finish:  Use chemical retarding agents applied to concrete forms and washing and brushing procedures to expose aggregate and surrounding matrix surfaces after form removal.

7. Abrasive-Blast Finish:  Use abrasive grit, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces.

8. Acid-Etched Finish:  Use acid and hot-water solution, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces.  Protect hardware, connections, and insulation from acid attach.

9. Honed Finish:  Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

10. Polished Finish:  Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

11. Sand-Embedment Finish:  Use selected stones placed in a sand bed in bottom of mold, with sand removed after curing.

B. Finish exposed [top] [bottom] [and back] surfaces of architectural precast concrete units to match face-surface finish.

Retain paragraph above or below if applicable.  Revise below to float finish or light-broom finish if smooth, steel-trowel finish is unnecessary.

C. Finish exposed [top] [bottom] [and back] surfaces of architectural precast concrete units by smooth, steel-trowel finish.

Revise finish in paragraph below to light-broom, stippled, or as-cast finish if float finish is unnecessary, or upgrade to smooth, steel-trowel finish.

D. Finish unexposed surfaces of architectural precast concrete units by float finish.

2.22 SOURCE QUALITY CONTROL

Retain paragraph below if establishing a minimum standard of plant testing and inspecting.  PCI MNL 117 mandates source testing requirements and a plant "Quality Systems Manual."  PCI certification also ensures periodic auditing of plants for compliance with requirements in PCI MNL 117.

A. Quality-Control Testing:  Test and inspect precast concrete according to PCI MNL 117 requirements.  If using self-consolidating concrete, also test and inspect according to PCI TR-6, "Interim Guidelines for the Use of Self-Consolidating Concrete in Precast/Prestressed Concrete Institute Member Plants."

Delete first paragraph and subparagraph below if not required.  PCI certification may be acceptable to authorities having jurisdiction without further monitoring of plant quality-control and testing program by Owner.

B. Owner will employ an independent testing agency to evaluate architectural precast concrete fabricator's quality-control and testing methods.

1. Allow Owner's testing agency access to material storage areas, concrete production equipment, concrete placement, and curing facilities.  Cooperate with Owner's testing agency and provide samples of materials and concrete mixtures as may be requested for additional testing and evaluation.

C. Strength of precast concrete units will be considered deficient if units fail to comply with ACI 318 (ACI 318M) requirements for concrete strength.

Review testing and acceptance criteria with structural engineer.  In first paragraph and subparagraphs below, add criteria for load tests if required.

D. Testing:  If there is evidence that strength of precast concrete units may be deficient or may not comply with ACI 318 (ACI 318M) requirements, precaster will employ an independent testing agency to obtain, prepare, and test cores drilled from hardened concrete to determine compressive strength according to ASTM C 42/C 42M.

1. A minimum of three representative cores will be taken from units of suspect strength, from locations directed by Architect.

2. Cores will be tested in an air-dry condition.

PCI's recommendations in first subparagraph below are more stringent than ACI's.

3. Strength of concrete for each series of 3 cores will be considered satisfactory if average compressive strength is equal to at least 85 percent of 28-day design compressive strength and no single core is less than 75 percent of 28-day design compressive strength.

4. Test results will be made in writing on same day that tests are performed, with copies to Architect, Contractor, and precast concrete fabricator.  Test reports will include the following:

a. Project identification name and number.

b. Date when tests were performed.

c. Name of precast concrete fabricator.

d. Name of concrete testing agency.

e. Identification letter, name, and type of precast concrete unit(s) represented by core tests; design compressive strength; type of break; compressive strength at breaks, corrected for length-diameter ratio; and direction of applied load to core in relation to horizontal plane of concrete as placed.

E. Patching:  If core test results are satisfactory and precast concrete units comply with requirements, clean and dampen core holes and solidly fill with precast concrete mixture that has no coarse aggregate, and finish to match adjacent precast concrete surfaces.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine supporting structural frame or foundation and conditions for compliance with requirements for installation tolerances, true and level bearing surfaces, and other conditions affecting performance.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

C. Do not install precast concrete units until supporting cast-in-place building structural framing has attained minimum allowable design compressive strength or supporting steel or other structure is complete.

3.2 INSTALLATION

A. Install clips, hangers, bearing pads, and other accessories required for connecting architectural precast concrete units to supporting members and backup materials.

B. Erect architectural precast concrete level, plumb, and square within specified allowable tolerances.  Provide temporary supports and bracing as required to maintain position, stability, and alignment as units are being permanently connected.

1. Install temporary steel or plastic spacing shims or bearing pads as precast concrete units are being erected.  Tack weld steel shims to each other to prevent shims from separating.

2. Maintain horizontal and vertical joint alignment and uniform joint width as erection progresses.

3. Remove projecting lifting devices and grout fill voids within recessed lifting devices flush with surface of adjacent precast surfaces when recess is exposed.

4. Unless otherwise indicated, maintain uniform joint widths of 3/4 inch (19 mm).

C. Connect architectural precast concrete units in position by bolting, welding, grouting, or as otherwise indicated on Shop Drawings.  Remove temporary shims, wedges, and spacers as soon as practical after connecting and grouting are completed.

1. Do not permit connections to disrupt continuity of roof flashing.

D. Welding:  Comply with applicable AWS D1.1/D1.1M and AWS D1.4 for welding, welding electrodes, appearance, quality of welds, and methods used in correcting welding work.

1. Protect architectural precast concrete units and bearing pads from damage by field welding or cutting operations, and provide noncombustible shields as required.

2. Welds not specified shall be continuous fillet welds, using no less than the minimum fillet as specified by AWS.

3. Clean weld-affected metal surfaces with chipping hammer followed by brushing, and apply a minimum 4.0-mil- (0.1-mm-) thick coat of galvanized repair paint to galvanized surfaces according to ASTM A 780.

Retain last subparagraph above or first subparagraph below.

4. Clean weld-affected metal surfaces with chipping hammer followed by brushing, and reprime damaged painted surfaces.

5. Remove, reweld, or repair incomplete and defective welds.

E. At bolted connections, use lock washers, tack welding, or other approved means to prevent loosening of nuts after final adjustment.

1. Where slotted connections are used, verify bolt position and tightness.  For sliding connections, properly secure bolt but allow bolt to move within connection slot.  For friction connections, apply specified bolt torque and check 25 percent of bolts at random by calibrated torque wrench.

In paragraph below, revise locations and extent of grouting if required.

F. Grouting Connections:  Grout connections where required or indicated.  Retain grout in place until hard enough to support itself.  Pack spaces with stiff grout material, tamping until voids are completely filled.  Place grout to finish smooth, level, and plumb with adjacent concrete surfaces.  Keep grouted joints damp for not less than 24 hours after initial set.  Promptly remove grout material from exposed surfaces before it affects finishes or hardens.

3.3 ERECTION TOLERANCES

A. Erect architectural precast concrete units level, plumb, square, true, and in alignment without exceeding the noncumulative erection tolerances of PCI MNL 117, Appendix I.

Select paragraph above or paragraph and subparagraphs below.  Usually retain above unless tolerances for Project deviate from PCI recommendations.  PCI MNL 117 erection tolerances are referenced above and listed below.

B. Erect architectural precast concrete units level, plumb, square, and true, without exceeding the following noncumulative erection tolerances:

1. Plan Location from Building Grid Datum:  Plus or minus 1/2 inch (13 mm).

2. Plan Location from Centerline of Steel:  Plus or minus 1/2 inch (13 mm).

3. Top Elevation from Nominal Top Elevation:  As follows:

a. Exposed Individual Panel:  Plus or minus 1/4 inch (6 mm).

b. Non-Exposed Individual Panel:  Plus or minus 1/2 inch (13 mm).

c. Exposed Panel Relative to Adjacent Panel:  1/4 inch (6 mm).

d. Non-Exposed Panel Relative to Adjacent Panel:  1/2 inch (13 mm).

4. Support Elevation from Nominal Support Elevation:  As follows:

a. Maximum Low:  1/2 inch (13 mm).

b. Maximum High:  1/4 inch (6 mm).

5. Maximum Plumb Variation over the Lesser of Height of Structure or 100 Feet (30 m):  1 inch (25 mm).

6. Plumb in Any 10 Feet (3 m) of Element Height:  1/4 inch (6 mm).

7. Maximum Jog in Alignment of Matching Edges:  1/4 inch (6 mm).

8. Joint Width (Governs over Joint Taper):  Plus or minus 1/4 inch (6 mm).

9. Maximum Joint Taper:  3/8 inch (10 mm).

10. Joint Taper in 10 Feet (3 m):  1/4 inch (6 mm).

11. Maximum Jog in Alignment of Matching Faces:  1/4 inch (6 mm).

12. Differential Bowing or Camber, as Erected, between Adjacent Members of Same Design:  1/4 inch (6 mm).

13. Opening Height between Spandrels:  Plus or minus 1/4 inch (6 mm).

3.4 FIELD QUALITY CONTROL

Retain first option in paragraph below if Owner engages a special inspector.  If authorities having jurisdiction permit Contractor to engage a special inspector, retain second option and retain option for submitting special inspection reports in Part 1 "Submittals" Article.

A. Special Inspections:  [Owner will engage] [Engage] a qualified special inspector to perform the following special inspections and prepare reports:

1. Erection of precast concrete members.

2. <Insert special inspections.>

Retain first paragraph below, with or without paragraph above, to identify who shall perform tests and inspections.  If retaining second option, retain requirement for field quality-control test reports in Part 1 "Submittals" Article.

B. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections and prepare test reports.

C. Field welds will be subject to visual inspections and nondestructive testing according to ASTM E 165 or ASTM E 709.  High-strength bolted connections will be subject to inspections.

D. Testing agency will report test results promptly and in writing to Contractor and Architect.

E. Repair or remove and replace work where tests and inspections indicate that it does not comply with specified requirements.

F. Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

3.5 REPAIRS

Blemishes occurring after delivery are normally repaired before final joint sealing and cleaning as weather permits.

A. Repair architectural precast concrete units if permitted by Architect.  The Architect reserves the right to reject repaired units that do not comply with requirements.

Precast concrete manufacturer should develop appropriate repair mixtures and techniques during production sample approval process.

B. Mix patching materials and repair units so cured patches blend with color, texture, and uniformity of adjacent exposed surfaces and show no apparent line of demarcation between original and repaired work, when viewed in typical daylight illumination from a distance of 20 feet (6 m).

C. Prepare and repair damaged galvanized coatings with galvanizing repair paint according to ASTM A 780.

Retain paragraph above if using galvanized anchors, connections, and other items; retain first paragraph below if items are prime painted.

D. Wire brush, clean, and paint damaged prime-painted components with same type of shop primer.

E. Remove and replace damaged architectural precast concrete units when repairs do not comply with requirements.

3.6 CLEANING

A. Clean surfaces of precast concrete units exposed to view.

B. Clean mortar, plaster, fireproofing, weld slag, and other deleterious material from concrete surfaces and adjacent materials immediately.

C. Clean exposed surfaces of precast concrete units after erection and completion of joint treatment to remove weld marks, other markings, dirt, and stains.

1. Perform cleaning procedures, if necessary, according to precast concrete fabricator's recommendations.  Clean soiled precast concrete surfaces with detergent and water, using stiff fiber brushes and sponges, and rinse with clean water.  Protect other work from staining or damage due to cleaning operations.

2. Do not use cleaning materials or processes that could change the appearance of exposed concrete finishes or damage adjacent materials.

END OF SECTION 03450END OF SECTION 03450

ARCHITECTURAL PRECAST CONCRETE
03450 - 1

