Copyright 2005 AIA
MASTERSPEC
05/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 08460 - AUTOMATIC ENTRANCE DOORS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. [Exterior] [Interior] [Exterior and interior], sliding, power-operated automatic entrances.

2. [Exterior] [Interior] [Exterior and interior], swinging, power-operated automatic entrances.

3. [Exterior] [Interior] [Exterior and interior], folding, power-operated automatic entrances.

4. [Exterior] [Interior] [Exterior and interior], power-assist automatic entrances.

5. [Exterior] [Interior] [Exterior and interior], low-energy automatic entrances.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]" for [installing recessed metal frames for control mats in concrete] [and] [forming recesses in concrete for recessed thresholds].

2. Division 8 Sections for doors and entrances controlled by automatic door operators furnished separately in Division 8 Section "Automatic Door Operators."

3. Division 8 Section "ICU/CCU Entrance Doors" for swinging-sliding and swinging-telescoping, manual ICU/CCU entrance door assemblies.

4. Division 8 Section "Revolving Entrance Doors."

5. Division 8 Section "Automatic Door Operators" for automatic door operators furnished separately from doors and frames.

6. Division 16 Sections for electrical connections including conduit and wiring for automatic entrance operators[ and access-control devices].

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. AAADM:  American Association of Automatic Door Manufacturers.

B. Activation Device:  Device that, when actuated, sends an electrical signal to the door operator to open the door.

C. IBC:  International Building Code.

D. Safety Device:  Device that, to avoid injury, prevents a door from opening or closing.

Retain first option in paragraph below for sliding, swinging, or folding power-operated doors; retain second option for power-assist and low-energy doors.

E. For automatic door terminology, refer to [BHMA A156.10] [and] [BHMA A156.19] for definitions of terms.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design automatic entrances, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

B. Structural Performance:  Automatic entrances shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated according to [SEI/ASCE 7] <Insert requirement>.

Consult a structural engineer experienced in engineering building entrances of type indicated to quantify design loads applicable to Project.  Verify compliance with codes.  See the Evaluations.

Retain subparagraphs below if design loads and load combinations are not indicated on Drawings.

1. Seismic Loads:  <Insert loads>.

2. Wind Loads:  <Insert loads>.

In windborne-debris regions of hurricane-prone areas, authorities having jurisdiction may require debris-impact and cyclic-pressure testing for glazed assemblies.  Retain first option in first paragraph below for entrances within 30 feet (9.1 m) of grade; retain second option for entrances more than 30 feet (9.1 m) above grade according to the IBC.  See "Wind Loads" Article in the Evaluations, and verify requirements of authorities having jurisdiction before retaining below.

C. Windborne-Debris-Impact-Resistance-Test Performance:  Provide automatic entrances that pass [large missile-impact] [small missile-impact] and cyclic-pressure tests of [ASTM E 1996 according to the IBC] <Insert testing and code requirements>.

D. Thermal Movements:  Allow for thermal movements from ambient and surface temperature changes.  Base calculations on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values in subparagraph below (for aluminum in particular) are suitable for most of the U.S.

1. Temperature Change (Range):  [120 deg F (67 deg C), ambient; 180 deg F (100 deg C)] <Insert temperature range>, material surfaces.

E. Operating Temperature Range:  Provide automatic entrances that operate within [minus 20 to plus 122 deg F (minus 29 to plus 50 deg C)] <Insert temperature range>.

First option in first paragraph below at a static-air-pressure difference of 1.57 lbf/sq. ft. (75 Pa) complies with ASHRAE/IESNA 90.1.  ASTM E 283 requires using a static-air-pressure difference of 1.57 lbf/sq. ft. (75 Pa) unless otherwise indicated, which is equivalent to a 25-mph (40-km/h) wind.  Static-air-pressure difference of 6.24 lbf/sq. ft. (300 Pa) is equivalent to a 50-mph (80-km/h) wind.

F. Air Infiltration:  Maximum air leakage through fixed glazing and framing areas of [1.25 cfm/sq. ft. (6.4 L/s x sq. m)] <Insert rate> of fixed entrance system area when tested according to ASTM E 283 at a minimum static-air-pressure difference of [1.57 lbf/sq. ft. (75 Pa)] [6.24 lbf/sq. ft. (300 Pa)] <Insert pressure>.

G. Opening-Force Requirements:

Retain applicable subparagraphs below.  First subparagraph is from the IBC and NFPA 101 for means-of-egress doors.  The IBC also requires compliance with BHMA A156.10 and BHMA A156.19.  Verify requirements of authorities having jurisdiction.

1. Power-Operated Doors:  Not more than 50 lbf (222 N) required to manually set door in motion if power fails, and not more than 15 lbf (67 N) required to open door to minimum required width.

First two subparagraphs below are from BHMA A156.10; third subparagraph is from BHMA A156.19.

2. Power-Operated Swinging Doors:  Not more than 30 lbf (133 N) required to manually open door if power fails.

3. Breakaway Device for Power-Operated Doors:  Not more than 50 lbf (222 N) required for a breakaway door or panel to open.

4. Power-Assist and Low-Energy Doors:  Not more than 15 lbf (67 N) required to release a latch if provided, not more than 30 lbf (133 N) required to manually set door in motion, and not more than 15 lbf (67 N) required to fully open door if power fails.

Subparagraph below is based on U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA) and Architectural Barriers Act (ABA) Accessibility Guidelines for Buildings and Facilities."

5. Accessible Interior Doors:  Not more than 5 lbf (22 N) to fully open door.

H. Entrapment Force Requirements:

Retain applicable subparagraphs below.  First three subparagraphs are from BHMA A156.10; fourth subparagraph is from BHMA A156.19.  Verify requirements of authorities having jurisdiction.

1. Power-Operated Sliding Doors:  Not more than 30 lbf (133 N) required to prevent stopped door from closing.

2. Power-Operated Swinging Doors:  Not more than 40 lbf (178 N) required to prevent stopped door from closing or completely opening.

3. Power-Operated Folding Doors:  Not more than 30 lbf (133 N) required to prevent stopped door from closing and not more than 40 lbf (178 N) required to prevent stopped door from completely opening.

4. Low-Energy Doors:  Not more than 15 lbf (67 N) required to prevent stopped door from closing or opening.

1.5 SUBMITTALS

First four paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for automatic entrances.  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

B. Shop Drawings:  For automatic entrances.  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work.

Retain first subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

1. For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

2. Wiring Diagrams:  For power, signal, and control wiring.

3. Activation and safety devices.

4. Include hardware schedule and indicate hardware types, functions, quantities, and locations.

C. Samples for Initial Selection:  For units with factory-applied [color] [and] [metal-cladding] finishes.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above.  Insert requirements for hardware samples if necessary.

D. Samples for Verification:  For each type of exposed finish required, in manufacturer's standard sizes.

If custom components are needed, add requirement for fabrication sample that indicates details of assembly or provision that an isometric drawing in Shop Drawings is acceptable.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

E. Delegated-Design Submittal:  For automatic entrances indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations:  Calculate requirements for seismic restraints.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For [Installer] [manufacturer] [certified inspector].

Retain first paragraph below for material or product certificates from manufacturers.  Retain option if retaining "Emergency-Exit Door Requirements" Paragraph in "Quality Assurance" Article.

G. Product Certificates:  For each type of[ emergency-exit] automatic entrance, from manufacturer.

H. Product Test Reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency, for automatic entrances.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

I. Field quality-control reports.

J. Maintenance Data:  For automatic entrances, safety devices, and control systems to include in maintenance manuals.

K. Warranties:  Sample of special warranties.

1.6 QUALITY ASSURANCE

A. Manufacturer Qualifications:  A manufacturer with company certificate issued by AAADM.

B. Installer Qualifications:  Manufacturer's authorized representative who is trained and approved for installation and maintenance of units required for this Project[ and who employs a certified inspector].

Retain subparagraph below if retaining "Maintenance Service" Article.

1. Maintenance Proximity:  Not more than [two] <Insert number> hours' normal travel time from Installer's place of business to Project site.

Retain first paragraph below if retaining option in "Installer Qualifications" Paragraph or if retaining "Maintenance Service" Article.

C. Certified Inspector Qualifications:  Certified by AAADM.

D. Source Limitations for Automatic Entrances:  Obtain automatic entrances from single source from single manufacturer.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

See the Evaluations for discussion of standards in first two paragraphs below.

F. Power-Operated Door Standard:  BHMA A156.10.

G. Power-Assist and Low-Energy Door Standard:  BHMA A156.19.

Retain first paragraph below only if automatic doors are a required means of egress.

H. Emergency-Exit Door Requirements:  Comply with requirements of authorities having jurisdiction for automatic entrances serving as a required means of egress.

Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

I. Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

Retain subparagraph below if additional requirements are necessary; include information about conference.

1. Review methods and procedures related to automatic entrances including, but not limited to, the following:

a. Structural load limitations.

b. Construction schedule.  Verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

c. Coordination with electrical, glazing, and other trades.

Coordinate subparagraph below with "Field Quality Control" Article.

d. Required testing, inspecting, and certifying procedures.

If needed, insert agenda items not listed in Division 1 Section "Project Management and Coordination."

1.7 PROJECT CONDITIONS

A. Field Measurements:  Verify actual dimensions of openings to receive automatic entrances by field measurements before fabrication.

1.8 COORDINATION

Retain applicable paragraphs in this article.

A. Coordinate sizes and locations of recesses in concrete floors for [recessed sliding tracks] [and] [recessed control mats] that control automatic entrances.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Templates:  Obtain templates for doors, frames, and other work specified to be factory prepared for installing automatic entrances, and distribute to parties involved.  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing automatic entrances to comply with indicated requirements.

C. Coordinate hardware with doors, frames, and related work to ensure proper size, thickness, hand, function, and finish.  Coordinate hardware for automatic entrances with hardware required for rest of Project.

D. Electrical System Roughing-in:  Coordinate layout and installation of automatic entrances with connections to power supplies[ and access-control system].

1.9 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of automatic entrances that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures including, but not limited to, excessive deflection.

b. Faulty operation of operators, controls, and hardware.

c. Deterioration of metals, metal finishes, and other materials beyond normal weathering and use.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

2. Warranty Period:  [Two] <Insert number> years from date of Substantial Completion.

Verify available special finish warranties.  Extended 20-year finish warranties are sometimes available for 70-percent fluoropolymer coatings.

B. Special Finish Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components that show evidence of deterioration of factory-applied finishes within specified warranty period.

1. Deterioration includes, but is not limited to, the following:

a. Color fading more than 5 Hunter units when tested according to ASTM D 2244.

b. Chalking in excess of a No. 8 rating when tested according to ASTM D 4214.

c. Cracking, checking, peeling, or failure of paint to adhere to bare metal.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

2. Warranty Period:  [20] <Insert number> years from date of Substantial Completion.

1.10 MAINTENANCE SERVICE

Consider deleting this article for light or residential use; usually retain for critical units.

A. Initial Maintenance Service:  Beginning at Substantial Completion, provide [three] [six] [nine] [12] months' full maintenance by skilled employees of automatic entrance Installer.  Include [monthly] [quarterly] preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper automatic entrance operation at rated speed and capacity.  Provide parts and supplies the same as those used in the manufacture and installation of original equipment.

1. Engage a certified inspector to perform safety inspection after each adjustment or repair and at end of maintenance period.  Furnish completed inspection reports to Owner.

2. Perform maintenance, including emergency callback service, during normal working hours.

Usually retain subparagraph above and delete subparagraph below except for critical locations.  Below adds appreciable cost.

3. Include 24-hour-per-day, 7-day-per-week, emergency callback service.

PART 2 -  PRODUCTS

2.1 MATERIALS

A. Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

1. Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221 (ASTM B 221M).

2. Sheet and Plate:  ASTM B 209 (ASTM B 209M).

B. Steel Reinforcement:  With manufacturer's standard corrosion-resistant primer complying with SSPC-PS Guide No. 12.00 applied immediately after surface preparation and pretreatment.  Select surface preparation methods according to recommendations in SSPC-SP COM and prepare surfaces according to applicable SSPC standard.

1. Structural Shapes, Plates, and Bars:  ASTM A 36/A 36M.

2. Cold-Rolled Sheet and Strip:  ASTM A 1008/A 1008M.

3. Hot-Rolled Sheet and Strip:  ASTM A 1011/A 1011M.

C. Stainless-Steel Bars:  ASTM A 276 or ASTM A 666, Type 304.

D. Stainless-Steel Tubing:  ASTM A 554, Grade MT 304.

Retain one or more of first three paragraphs below for metal cladding.

E. Stainless-Steel Sheet:  ASTM A 240/A 240M or ASTM A 666, [Type 304] <Insert alloy type>, stretcher-leveled standard of flatness, in entrance manufacturer's standard thickness.

Retain first paragraph below for brassy yellow color.

F. Brass Sheet:  ASTM B 36/B 36M, Alloy UNS No. C26000 (cartridge brass, 70 percent copper), in entrance manufacturer's standard thickness.

Retain first paragraph below for bronze look.  Neither alloy is a true tin bronze, but both closely match color of extruded architectural bronze (also not a true tin bronze).  Revise if only one of these two alloys is acceptable, or to specify another alloy.

G. Bronze Sheet:  ASTM B 36/B 36M, Alloy UNS No. C28000 (muntz metal, 60 percent copper) or Alloy UNS No. C23000 (red brass, 85 percent copper), in entrance manufacturer's standard thickness.

H. Glazing:  As specified in Division 8 Section "[Glazing] [Security Glazing]."

I. Sealants and Joint Fillers:  As specified in Division 7 Section "Joint Sealants."

Retain first paragraph below for leveling floor tracks of sliding doors.

J. Nonmetallic, Shrinkage-Resistant Grout:  Premixed, nonmetallic, noncorrosive, nonstaining grout; complying with ASTM C 1107; of consistency suitable for application.

K. Bituminous Paint:  Cold-applied, asphalt-mastic paint complying with SSPC-Paint 12 requirements, except containing no asbestos; formulated for 30-mil (0.76-mm) thickness per coat.

L. Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, nonstaining, nonbleeding fasteners and accessories compatible with adjacent materials.

2.2 SLIDING AUTOMATIC ENTRANCES

A. General:  Provide manufacturer's standard automatic entrances including doors[, sidelites], framing, headers, carrier assemblies, roller tracks, door operators, activation and safety devices, and accessories required for a complete installation.

Refer to the tables at the end of the Evaluations for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Copy paragraph below and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

B. [All-Glass] [Sliding] [Telescoping] Automatic Entrance <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. [Single-] [and] [Biparting-]Sliding Units:

1) Besam Automated Entrance Systems, Inc.; an ASSA ABLOY Group company.

2) DORMA Automatics; Div. of DORMA Group North America.

3) Gildor, Inc.

4) Horton Automatics; Div. of Overhead Door Corporation.

5) KM Systems, Inc.

6) Nabco Entrances Inc.

7) Sierra Automatic Doors, Inc.

8) Stanley Access Technologies; Div. of The Stanley Works.

9) Tormax Technologies, Inc.

10) <Insert manufacturer's name>.

b. [Single-] [and] [Biparting-]Telescoping Sliding Units:

1) Besam Automated Entrance Systems, Inc.; an ASSA ABLOY Group company.

2) Gildor, Inc.

3) Horton Automatics; Div. of Overhead Door Corporation.

4) KM Systems, Inc.

5) Nabco Entrances Inc.

6) Sierra Automatic Doors, Inc.

7) Stanley Access Technologies; Div. of The Stanley Works.

8) Tormax Technologies, Inc.

9) <Insert manufacturer's name>.

Retain one of three "Configuration" Subparagraphs below.  Indicate arrangement and location of doors, sidelites, and transoms on Drawings.  Pocketed sidelites in first two subparagraphs are discussed in "Safety Considerations" Article in the Evaluations.

3. Configuration:  Single-sliding door, with one sliding leaf[, transom,] and[ pocketed] sidelite.

a. Traffic Pattern:  [One] [Two] way.

b. Emergency Breakaway Capability:  [Sliding leaf only] [Sliding leaf and sidelite] [As indicated on Drawings].

c. Mounting:  [Between jambs] [Surface].

4. Configuration:  Biparting-sliding doors, with two sliding leaves[, transom,] and[ pocketed] sidelites on each side.

a. Traffic Pattern:  [One] [Two] way.

b. Emergency Breakaway Capability:  [Sliding leaves only] [Sliding leaves and sidelites] [As indicated on Drawings].

c. Mounting:  [Between jambs] [Surface].

5. Configuration:  [Single-telescoping-sliding door, with three] [Biparting-telescoping-sliding doors, with six] sliding leaves[, transom,] and sidelight(s).

a. Traffic Pattern:  [One] [Two] way.

b. Emergency Breakaway Capability:  [Center leaves only] [All leaves] [As indicated on Drawings].

c. Mounting:  Between jambs.

6. Operator Features:

Adjust list below to suit Project.  Consult manufacturers for availability and necessity of adjustability for specific applications.

a. Power opening and closing.

b. Drive System:  [Chain] [or] [belt].

c. Adjustable opening and closing speeds.

d. Adjustable hold-open time between 0 and 30 seconds.

e. Obstruction recycle.

f. On-off/hold-open switch to control electric power to operator[, key operated].

g. Energy-conservation switch that reduces door-opening width.

h. <Insert features required>.

7. Sliding Door Carrier Assemblies and Overhead Roller Tracks:  Manufacturer's standard carrier assembly that allows vertical adjustment; consisting of nylon- or delrin-covered, ball-bearing-center steel wheels operating on a continuous roller track, or ball-bearing-center steel wheels operating on a nylon- or delrin-covered, continuous roller track.  Support doors from carrier assembly by cantilever and pivot assembly.

a. Rollers:  Minimum of two ball-bearing roller wheels and two antirise rollers for each active leaf.

8. Sliding Door Threshold:  Manufacturer's standard threshold members and bottom-guide track system, with stainless-steel, ball-bearing-center roller wheels.

Retain one of two "Configuration" Subparagraphs below, or delete both subparagraphs and indicate sill configuration on Drawings.  First subparagraph may be used with or without surface or recessed control mats.  Coordinate with control system used.

a. Configuration:  Saddle-type threshold across door opening and [surface-mounted] [recessed] guide track system at sidelites.

b. Configuration:  No threshold across door opening and [surface-mounted] [recessed] guide track system at sidelites.

9. Combination Activation and Safety Device:  Combination motion/presence sensor.

Retain subparagraph above or select one activation device and one safety device from first seven subparagraphs below.  Above is most common.

Retain one of first three subparagraphs below.  Motion sensor is the most common activation device, and wall push-plate switch is often used for clean rooms.  Key switch is usually a supplementary activation device.

10. Activation Device:  Motion sensor mounted on each side of door header to detect pedestrians in activating zone and to open door.

11. Activation Device:  Control mat installed on ingress side of door to detect pedestrians in activating zone and to open door.

12. Activation Device:  [Push-plate switch] [Push-button switch] [Key switch] [on each side of door] to activate door operator.

Retain one of first four subparagraphs below with any activation device above.  Safety control mats are typically used only with activation control mats.

13. Safety Devices:  Two photoelectric beams mounted in sidelite jambs to detect pedestrians in presence zone and to prevent door from closing.

14. Safety Devices:  Presence sensor mounted to underside of door header[ and one photoelectric beam mounted in sidelite jambs] to detect pedestrians in presence zone and to prevent door from closing.

15. Safety Devices:  Presence sensor mounted on each side of door header[ and one photoelectric beam mounted in sidelite jambs] to detect pedestrians in presence zone and to prevent door from closing.

16. Safety Devices:  Control mat installed on egress side of door to detect pedestrians in presence and safety zones and to prevent door from closing.

Presence sensor in first subparagraph below is safety device offered by only a few manufacturers; it is optional feature and in addition to other safety devices.  Retain if required.

17. Sidelite Safety Device:  Presence sensor, mounted above each sidelite on side of door opening through which doors travel, to detect obstructions and to prevent door from opening.

Revise subparagraph below if different finish is required for components of automatic entrances.  If more than one finish is required, indicate location of each on Drawings, in schedules, or by inserts.

18. Finish:  Finish framing, door(s)[, sidelite(s),] and header with [Class I, clear anodic finish] [Class II, clear anodic finish] [Class I, color anodic finish] [Class II, color anodic finish] [baked-enamel finish] [high-performance organic finish (two-coat fluoropolymer)] [high-performance organic finish (three-coat fluoropolymer)] [metal cladding] [finish matching adjacent curtain wall] [finish matching adjacent storefront].

Retain one of two subparagraphs below.  First four options in first subparagraph are for color anodic finish and may vary in color range and availability among manufacturers.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

Retain subparagraph below only for metal-clad finish.  Verify availability of metal-clad finishes with manufacturers before specifying.

b. Metal Cladding:  [No. 4 directional-satin-finish stainless steel] [No. 8 mirrorlike reflective, nondirectional-polish-finish stainless steel] [Satin brass] [Polished brass] [Satin bronze] [Polished bronze] <Insert finish>.

2.3 SWINGING AUTOMATIC ENTRANCES

A. General:  Provide manufacturer's standard automatic entrances including doors, framing, headers, door operators, activation and safety devices, and accessories required for a complete installation.

Refer to the tables at the end of the Evaluations for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Copy first paragraph below and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

B. Swinging, Power-Operated Automatic Entrance <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Besam Automated Entrance Systems, Inc.; an ASSA ABLOY Group company.

b. DORMA Automatics; Div. of DORMA Group North America.

c. Horton Automatics; Div. of Overhead Door Corporation.

d. Stanley Access Technologies; Div. of The Stanley Works.

e. Tormax Technologies, Inc.

f. <Insert manufacturer's name>.

Retain one of two "Configuration" subparagraphs below.  Indicate arrangement and location of doors on Drawings.

3. Configuration:  Single-swinging door[ with transom].

a. Traffic Pattern:  [One] [Two] way.

b. Mounting:  [Between jambs] [Surface].

4. Configuration:  Pair of swinging doors[ with transom].

BHMA standard requires third option in first subparagraph below to have door leaves separated by vertical frame and guide rails.

a. Traffic Pattern:  [One way] [Two way] [Double egress].

b. Mounting:  [Between jambs] [Surface].

5. Operator Features:

Adjust list below to suit Project.  Consult manufacturers for availability and necessity of adjustability for specific applications.

a. Power opening and [spring] [power] closing.

b. Adjustable opening and closing speeds.

c. Adjustable hold-open time between 0 and 30 seconds.

d. Adjustable backcheck and latching.

e. Obstruction recycle.

f. Automatic door re-open if stopped while closing.

g. On-off/hold-open switch to control electric power to operator[, key operated].

h. <Insert features required>.

6. Combination Activation and Safety Device:  Combination motion/presence sensor.

Retain subparagraph above or select one activation device and one safety device from first six subparagraphs below.  Above is most common.

Retain one of first three subparagraphs below.  Motion sensor is the most common activation device, and wall push-plate switch is often used for clean rooms.  Key switch is usually a supplementary activation device.

7. Activation Device:  Motion sensor mounted on each side of door header to detect pedestrians in activating zone and to open door.

8. Activation Device:  Control mat installed on ingress side of door to detect pedestrians in activating zone and to open door.

9. Activation Device:  [Push-plate switch] [Push-button switch] [Key switch] [on each side of door] to activate door operator.

Retain one of first three subparagraphs below with any activation device above.  Safety control mats are typically used only with activation control mats.

10. Safety Devices:  Presence sensor mounted on [door header] [horizontal door muntin] [guide rail] to detect pedestrians in presence zone and to prevent door from closing.

11. Safety Devices:  Two photoelectric beams mounted in guide rails to detect pedestrians in presence zone and to prevent door from closing.

12. Safety Devices:  Control mat installed on egress side of door to detect pedestrians in presence and safety zones and to prevent door from closing.

Insert list of hardware here if Project has special hardware requirements.  See the Evaluations for discussion of hardware.

Revise subparagraph below if different finish is required for components of automatic entrances.  If more than one finish is required, indicate location of each on Drawings, in schedules, or by inserts.

13. Finish:  Finish framing, door(s), and header with [Class I, clear anodic finish] [Class II, clear anodic finish] [Class I, color anodic finish] [Class II, color anodic finish] [baked-enamel finish] [high-performance organic finish (two-coat fluoropolymer)] [high-performance organic finish (three-coat fluoropolymer)] [metal cladding] [finish matching adjacent curtain wall] [finish matching adjacent storefront].

Retain one of two subparagraphs below.  First four options in first subparagraph are for color anodic finish and may vary in color range and availability among manufacturers.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

Retain subparagraph below only for metal-clad finish.  Verify availability of metal-clad finishes with manufacturers before specifying.

b. Metal Cladding:  [No. 4 directional-satin-finish stainless steel] [No. 8 mirrorlike reflective, nondirectional-polish-finish stainless steel] [Satin brass] [Polished brass] [Satin bronze] [Polished bronze] <Insert finish>.

Copy paragraph below and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

C. Swinging, [Power-Assist] [Low-Energy, Power-Operated] [Low-Energy, Power-Open] Automatic Entrance <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. DORMA Automatics; Div. of DORMA Group North America.

b. Horton Automatics; Div. of Overhead Door Corporation.

c. Stanley Access Technologies; Div. of The Stanley Works.

d. Tormax Technologies, Inc.

e. <Insert manufacturer's name>.

Retain one of two "Configuration" subparagraphs below.  Indicate arrangement and location of doors on Drawings.

3. Configuration:  Single-swinging door[ with transom].

a. Traffic Pattern:  [One] [Two] way.

b. Mounting:  [Between jambs] [Surface].

4. Configuration:  Pair of swinging doors[ with transom].

BHMA standard requires third option in first subparagraph below to have door leaves separated by vertical frame and guide rails.

a. Traffic Pattern:  [One way] [Two way] [Double egress].

b. Mounting:  [Between jambs] [Surface].

5. Operator Features:

Adjust list below to suit Project.  Consult manufacturers for availability and necessity of adjustability for specific applications.

a. Power opening and [spring] [power] closing.

b. Adjustable opening and closing speeds.

c. Adjustable hold-open time between 0 and 30 seconds.

d. Adjustable backcheck and latching.

e. Obstruction recycle.

f. Automatic door re-open if stopped while closing.

g. On-off/hold-open switch to control electric power to operator[, key operated].

h. <Insert features required>.

Select activation device from options in first subparagraph below.  Power-assist and low-energy doors are seldom used with other activation devices, although it is not disallowed by BHMA A156.19.  If another activation device is desired, insert requirements.

6. Activation Device:  [Push-plate switch] [Push-button switch] [Key switch] [on each side of door] to activate door operator.

Power-assist and low-energy doors are not required by BHMA A156.19 to have auxiliary safety devices.  If auxiliary safety devices are desired, insert requirements here.

Insert list of hardware here if Project has special hardware requirements.  See the Evaluations for discussion of hardware.

Revise subparagraph below if different finish is required for components of automatic entrances.  If more than one finish is required, indicate location of each on Drawings, in schedules, or by inserts.

7. Finish:  Finish framing, door(s), and header with [Class I, clear anodic finish] [Class II, clear anodic finish] [Class I, color anodic finish] [Class II, color anodic finish] [baked-enamel finish] [high-performance organic finish (two-coat fluoropolymer)] [high-performance organic finish (three-coat fluoropolymer)] [metal cladding] [finish matching adjacent curtain wall] [finish matching adjacent storefront].

Retain one of two subparagraphs below.  First four options in first subparagraph are for color anodic finish and may vary in color range and availability among manufacturers.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

Retain subparagraph below only for metal-clad finish.  Verify availability of metal-clad finishes with manufacturers before specifying.

b. Metal Cladding:  [No. 4 directional-satin-finish stainless steel] [No. 8 mirrorlike reflective, nondirectional-polish-finish stainless steel] [Satin brass] [Polished brass] [Satin bronze] [Polished bronze] <Insert finish>.

2.4 FOLDING AUTOMATIC ENTRANCES

A. General:  Provide manufacturer's standard automatic entrances including doors, framing, headers, overhead tracks, door operators, activation and safety devices, and accessories required for a complete installation.

Refer to the tables at the end of the Evaluations for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Copy first paragraph below and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

B. Folding, Power-Operated Automatic Entrance <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Besam Automated Entrance Systems, Inc.; an ASSA ABLOY Group company.

b. Gildor, Inc.

c. Horton Automatics; Div. of Overhead Door Corporation.

d. KM Systems, Inc.

e. Nabco Entrances Inc.

f. Sierra Automatic Doors, Inc.

g. Stanley Access Technologies; Div. of The Stanley Works.

h. <Insert manufacturer's name>.
3. Configuration:  [One pair of folding doors that fold to one side] [Two pairs of folding doors (biparting) that fold to each side] of door opening[ with transom].

a. Traffic Pattern:  [One] [Two] way.

b. Mounting:  [Between jambs] [Surface].

4. Operator Features:

Adjust list below to suit Project.  Consult manufacturers for availability and necessity of adjustability for specific applications.

a. Power opening and [spring] [power] closing.

b. Adjustable opening and closing speeds.

c. Adjustable hold-open time between 0 and 30 seconds.

d. Obstruction recycle.

e. Automatic door re-open if stopped while closing.

f. On-off/hold-open switch to control electric power to operator[, key operated].

g. <Insert features required>.

5. Folding Door Overhead Tracks:  Manufacturer's standard assembly, secured to header; consisting of guide track and breakaway system.  Connect one folding leaf at the top to door operator, and set on a floor-mounted bottom pivot; no bottom track is permitted.

6. Combination Activation and Safety Device:  Combination motion/presence sensor.

Retain subparagraph above or select one activation device and one safety device from first six subparagraphs below.  Above is most common.

Retain one of first three subparagraphs below.  Motion sensor is the most common activation device; key switch is usually a supplementary activation device.

7. Activation Device:  Motion sensor mounted on each side of door header to detect pedestrians in activating zone and to open door.

8. Activation Device:  Control mat installed on ingress side of door to detect pedestrians in activating zone and to open door.

9. Activation Device:  [Push-plate switch] [Push-button switch] [Key switch] [on each side of door] to activate door operator.

Retain one of first three subparagraphs below with any activation device above.  Safety control mats are typically used only with activation control mats.

10. Safety Devices:  Presence sensor mounted on [door header] [horizontal door muntin] [guide rail] to detect pedestrians in presence zone and to prevent door from closing.

11. Safety Devices:  Two photoelectric beams mounted in guide rails to detect pedestrians in presence zone and to prevent door from closing.

12. Safety Devices:  Control mat installed on egress side of door to detect pedestrians in presence and safety zones and to prevent door from closing.

Revise subparagraph below if different finish is required for components of automatic entrances.  If more than one finish is required, indicate location of each on Drawings, in schedules, or by inserts.

13. Finish:  Finish framing, door(s), and header with [Class I, clear anodic finish] [Class II, clear anodic finish] [Class I, color anodic finish] [Class II, color anodic finish] [baked-enamel finish] [high-performance organic finish (two-coat fluoropolymer)] [high-performance organic finish (three-coat fluoropolymer)] [metal cladding] [finish matching adjacent curtain wall] [finish matching adjacent storefront].

Retain one of two subparagraphs below.  First four options in first subparagraph are for color anodic finish and may vary in color range and availability among manufacturers.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

Retain subparagraph below only for metal-clad finish.  Verify availability of metal-clad finishes with manufacturers before specifying.

b. Metal Cladding:  [No. 4 directional-satin-finish stainless steel] [No. 8 mirrorlike reflective, nondirectional-polish-finish stainless steel] [Satin brass] [Polished brass] [Satin bronze] [Polished bronze] <Insert finish>.

Copy paragraph below and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

C. Folding, [Low-Energy, Power-Operated] [Low-Energy, Power-Open] Automatic Entrance <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Besam Automated Entrance Systems, Inc.; an ASSA ABLOY Group company.

b. Horton Automatics; Div. of Overhead Door Corporation.

c. <Insert manufacturer's name>.

3. Configuration:  [One pair of folding doors that fold to one side] [Two pairs of folding doors (biparting) that fold to each side] of door opening[ with transom].

a. Traffic Pattern:  [One] [Two] way.

b. Mounting:  [Between jambs] [Surface].

4. Operator Features:

Adjust list below to suit Project.  Consult manufacturers for availability and necessity of adjustability for specific applications.

a. Power opening and [spring] [power] closing.

b. Adjustable opening and closing speeds.

c. Adjustable hold-open time between 0 and 30 seconds.

d. Obstruction recycle.

e. Automatic door re-open if stopped while closing.

f. On-off/hold-open switch to control electric power to operator[, key operated].

g. <Insert features required>.

5. Folding Door Overhead Tracks:  Manufacturer's standard assembly, secured to header; consisting of guide track and breakaway system.  Connect one folding leaf at the top to door operator, and set on a floor-mounted bottom pivot; no bottom track is permitted.

Select activation device from options in first subparagraph below.  Low-energy doors are seldom used with other activation devices, although it is not disallowed by BHMA A156.19.  If another activation device is desired, insert requirements.

6. Activation Device:  [Push-plate switch] [Push-button switch] [Key switch] [on each side of door] to activate door operator.

Power-assist and low-energy doors are not required by BHMA A156.19 to have auxiliary safety devices.  If auxiliary safety devices are desired, insert requirements here.

Revise subparagraph below if different finish is required for components of automatic entrances.  If more than one finish is required, indicate location of each on Drawings, in schedules, or by inserts.

7. Finish:  Finish framing, door(s), and header with [Class I, clear anodic finish] [Class II, clear anodic finish] [Class I, color anodic finish] [Class II, color anodic finish] [baked-enamel finish] [high-performance organic finish (two-coat fluoropolymer)] [high-performance organic finish (three-coat fluoropolymer)] [metal cladding] [finish matching adjacent curtain wall] [finish matching adjacent storefront].

Retain one of two subparagraphs below.  First four options in first subparagraph are for color anodic finish and may vary in color range and availability among manufacturers.

a. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

Retain subparagraph below only for metal-clad finish.  Verify availability of metal-clad finishes with manufacturers before specifying.

b. Metal Cladding:  [No. 4 directional-satin-finish stainless steel] [No. 8 mirrorlike reflective, nondirectional-polish-finish stainless steel] [Satin brass] [Polished brass] [Satin bronze] [Polished bronze] <Insert finish>.

2.5 ENTRANCE COMPONENTS

A. Framing[ and Transom] Members:  Manufacturer's standard extruded aluminum, minimum 0.125 inch (3.2 mm) thick and reinforced as required to support imposed loads.

1. Nominal Size:  [1-3/4 by 4-1/2 inches (45 by 115 mm)] [1-3/4 by 6 inches (45 by 150 mm)] [As indicated on Drawings] <Insert nominal size>.

Retain subparagraph below for separately framed sidelites or transoms.

2. Extruded Glazing Stops and Applied Trim:  Minimum 0.062-inch (1.6-mm) wall thickness.

Retain first paragraph below for stile and rail doors.  Retain appropriate option if doors are metal clad.

B. Stile and Rail Doors:  Manufacturer's standard 1-3/4-inch- (45-mm-) thick, glazed doors with minimum 0.125-inch- (3.2-mm-) thick, extruded-aluminum tubular stile and rail members[ and clad in stainless-steel sheet] [ and clad in brass sheet] [ and clad in bronze sheet].  Mechanically fasten corners with reinforcing brackets that are welded, or incorporate concealed tie-rods that span full length of top and bottom rails.

1. Glazing Stops and Gaskets:  [Beveled] [Square], snap-on, extruded-aluminum stops and manufacturer's standard preformed gaskets.

Verify availability of stile and rail dimensions in first two subparagraphs below with manufacturers.

2. Stile Design:  [Thin stile, less than 1-3/4-inch (45-mm) nominal width] [Narrow stile, 2-1/8-inch (55-mm) nominal width] [Medium stile, 3-1/2-inch (90-mm) nominal width] [Wide stile, more than 4-inch (100-mm) nominal width] [As indicated on Drawings].

3. Rail Design:  [5-inch (125-mm) nominal height] [6-1/2-inch (165-mm) nominal height] [10-inch (254-mm) nominal height] [As indicated on Drawings].

Retain subparagraph below if required.  Many manufacturers include muntins as standard.

4. Muntin Bars:  Horizontal tubular rail member for each door; match stile design and finish.

Retain first paragraph below only for all-glass sliding doors.  Retain appropriate option if rails are metal clad.

C. All-Glass Sliding Doors:  Fabricated from 13-mm-thick tempered glass, with polished vertical edges and minimum 0.125-inch- (3.2-mm-) thick, extruded-aluminum top and bottom rails[ and clad in stainless-steel sheet] [ and clad in brass sheet] [ and clad in bronze sheet].

1. Rail Design:  [3-1/2-inch (90-mm)] [5-inch (125-mm)] nominal height.

D. [Sidelite(s)] [and] [Transom]:  Manufacturer's standard 1-3/4-inch- (45-mm-) deep [sidelite(s)] [and] [transom] with minimum 0.125-inch- (3.2-mm-) thick, extruded-aluminum tubular stile and rail members[ and clad in stainless-steel sheet,] [ and clad in brass sheet,] [ and clad in bronze sheet,] matching door design and finish.

1. Glazing Stops and Gaskets:  Same materials and design as for stile and rail door.

Retain subparagraph above or first subparagraph below; below is for all-glass sliding doors.

2. Glazing Stops and Gaskets:  [Beveled] [Square], snap-on, extruded-aluminum stops and manufacturer's standard preformed gaskets.

Retain subparagraph below if required for sidelites.

3. Muntin Bars:  Horizontal tubular rail members for each sidelite; match stile design.

E. Headers:  Fabricated from minimum 0.125-inch- (3.2-mm-) thick, extruded aluminum and extending full width of automatic entrance units to conceal door operators and controls.  Provide hinged or removable access panels for service and adjustment of door operators and controls.  Secure panels to prevent unauthorized access.

1. Mounting:  [Surface mounted] [Concealed, with one side of header flush with framing].

Retain subparagraph below only for sliding doors.

2. Capacity:  Capable of supporting doors up to [175 lb (79 kg) per leaf over spans up to 14 feet (4.3 m)] <Insert load and span required> without intermediate supports.

a. Provide sag rods for spans exceeding 14 feet (4.3 m).

F. Brackets and Reinforcements:  Manufacturer's standard high-strength aluminum with nonstaining, nonferrous shims for aligning system components.

G. Signage:  Affixed to both sides of each door as required by [BHMA A156.10] [and] [BHMA A156.19] for type of door and its operation.

Decals in first subparagraph below are the most typical applications.

1. Application Process:  [Decals] [Silk-screened] [Door manufacturer's standard process] <Insert requirement>.

Retain subparagraph below for signs on field-installed glass surfaces.

2. Provide sign materials with instructions for field application after glazing is installed.

2.6 DOOR OPERATORS AND ACTIVATION AND SAFETY DEVICES

See the Evaluations for discussion of door operators.

A. Door Operators:  Provide door operators of size recommended by manufacturer for door size, weight, and movement; for condition of exposure; and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.

1. Door Operator Performance:  Provide door operators that will open and close doors and maintain them in fully closed position when subjected to Project's design wind loads.

2. Electromechanical Operators:  Concealed, self-contained, overhead unit powered by fractional-horsepower, permanent-magnet dc motor; with closing speed controlled mechanically by gear train and dynamically by braking action of electric motor; with solid-state microprocessor controller; UL 325; and with manual operation with power off.

Retain applicable operator controls in remaining paragraphs.  Coordinate with devices retained in "Sliding Automatic Entrances," "Swinging Automatic Entrances," and "Folding Automatic Entrances" articles.

B. Motion Sensors:  Self-contained, K-band-frequency, microwave-scanner units with metal or plastic housing; adjustable to provide detection field sizes and functions required by BHMA A156.10; with relay hold time of not less than 2 to 10 seconds.

1. Provide capability for switching between bidirectional and unidirectional detection.

2. For one-way-traffic entrances, sensor on egress side shall not be active when doors are fully closed.

C. Presence Sensors:  Self-contained, infrared-scanner units with metal or plastic housing; adjustable to provide detection field sizes and functions required by BHMA A156.10; with relay hold time of [not less than 2 to 10 seconds] [1.5 seconds fixed].  Sensors shall remain active at all times.

D. Combination Motion/Presence Sensors:  Self-contained units; consisting of both motion and presence sensors in a single metal or plastic housing; adjustable to provide detection field sizes and functions required by BHMA A156.10.

1. Motion Sensor:  K-band-frequency, microwave-scanner units; with relay hold time of not less than 2 to 10 seconds.

a. Provide capability for switching between bidirectional and unidirectional detection.

b. For one-way-traffic entrances, sensor on egress side shall not be active when doors are fully closed.

2. Presence Sensor:  Infrared-scanner units; with relay hold time of [not less than 2 to 10 seconds] [1.5 seconds fixed].  Sensors shall remain active at all times.

E. Photoelectric Beams:  Pulsed infrared, sender-receiver assembly for recessed mounting.  Beams shall not be active when doors are fully closed.

Mats and activation switches in first five paragraphs below vary among manufacturers; each manufacturer offers a variety.  Consult manufacturers and revise retained paragraphs as needed.

F. Control Mats:  1/2-inch- (13-mm-) thick, synthetic-rubber or flexible-plastic mat in safety-ribbed surface pattern, with extruded-aluminum frame; with pressure switches for low-voltage control wiring; and complying with performance requirements in BHMA A156.10.

1. Color:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities].

If needed, add requirements for monograms and directional arrows.

2. Frame:  [Recessed to fit flush with floor, with concealed anchors] [Surface mounted, with tapered safety edge].

3. Size:  As indicated, but no smaller than required by BHMA A156.10 including Appendix A.

G. Push-Plate Switch:  Momentary-contact door control switch with flat push-plate actuator[ with contrasting-colored, engraved message].

Retain one of two "Configuration" subparagraphs below.

1. Configuration:  [Round] [Square] push plate with 4-by-4-inch (100-by-100-mm) junction box.

a. Mounting:  [Recess mounted, semiflush in wall] [Surface mounted on wall] [As indicated on Drawings].

2. Configuration:  Rectangular push plate with 2-by-4-inch (50-by-100-mm) junction box.

a. Mounting:  [Recess mounted, semiflush in wall] [Recess mounted in door jamb] [Surface mounted on wall] [Surface mounted on post] [Surface mounted on guide rail] [As indicated on Drawings].

3. Push-Plate Material:  [Stainless steel] [Plastic] as selected by Architect from manufacturer's full range.

4. Message:  [Plain face with no message.] ["Push to Open."] [International symbol of accessibility.] [International symbol of accessibility and "Push to Open."]

Retain first paragraph below for push-button switch or delete and insert other requirements.

H. Push-Button Switch:  Momentary-contact door control switch with 1 red-button actuator; enclosed in nominal [2-by-4-inch (50-by-100-mm)] [4-by-4-inch (100-by-100-mm)] junction box.

1. Provide faceplate engraved with "Press to Open" letters[ and international symbol of accessibility] in contrasting color.

2. Provide blue plastic cover engraved with "Press Button to Open" in white letters and international symbol of accessibility.

3. Mounting:  [Surface mounted on wall] [Surface mounted on post] [Surface mounted on guide rail] [Recess mounted in wall] [As indicated on Drawings].

4. Face-Plate Material:  [Stainless steel] [Painted metal] as selected by Architect from manufacturer's full range.

I. Key Switch:  Recess-mounted, door control switch with key-controlled actuator; enclosed in 2-by-4-inch (50-by-100-mm) junction box.  Provide faceplate engraved with letters indicating switch functions.

1. Face-Plate Material:  [Stainless steel] [Painted metal] as selected by Architect from manufacturer's full range.

2. Functions:  [On-off, momentary contact] [On-off, maintained contact] [Two-way automatic, hold open, one-way exit, and off] [Two-way automatic, hold open, one-way exit, off, full open, and partial open].

3. Mounting:  [Recess mounted, semiflush in wall] [Recess mounted in door jamb] [Surface mounted on wall] [Surface mounted on post] [As indicated on Drawings].

J. Wireless or Remote Radio Control Switch:  Manufacturer's standard radio control system consisting of header-mounted receiver and [wall-mounted] [hand-held, battery-operated] transmitter switch.

1. Wall-Mounted Transmitter Switch:  One red-button, momentary-contact actuator enclosed in 4-by-4-inch (100-by-100-mm) junction box.  Provide blue plastic cover engraved with "Press Button to Open" in white letters and international symbol of accessibility.

K. Electrical Interlocks:  Unless units are equipped with self-protecting devices or circuits, provide electrical interlocks to prevent activation of operator when door is locked, latched, or bolted.

Retain paragraph below only for sliding doors at exterior locations or where reduced opening-width control is required to conserve energy and reduce amount of air exchange.

L. Opening-Width Control:  Two-position switch that in the normal position allows sliding doors to travel to full opening width and in the alternate position reduces opening to a selected partial opening width.

If needed, insert requirements for access-control system.  Verify availability with manufacturers and coordinate with Division 16 access-control requirements if any.

2.7 HARDWARE

Before editing this article, verify requirements for accessible entrances, emergency-exit doors, and other requirements of authorities having jurisdiction.

If various door and hardware combinations are needed, insert requirements in "Sliding Automatic Entrances," "Swinging Automatic Entrances," and "Folding Automatic Entrances" articles.

A. General:  Provide units in sizes and types recommended by automatic entrance and hardware manufacturers for entrances and uses indicated.  Finish exposed parts to match door finish[ unless otherwise indicated].

B. Manual Opening for Power-Operated Swinging Doors:  Provide hardware that in a power failure allows door to open with a manual force not to exceed 30 lbf (133 N) according to BHMA A156.10.

C. Breakaway Device for Power-Operated Doors:  Provide breakaway device that allows door to swing out in direction of egress to full 90 degrees from any operating position.  Maximum force to open door shall be 50 lbf (222 N) according to BHMA A156.10.  Interrupt powered operation of door operator while in breakaway mode.

D. Manual Opening for Power-Assist and Low-Energy Doors:  Provide hardware that in a power failure allows door to open with a manual force not to exceed 15 lbf (67 N) to release a latch, if equipped with a latch; 30 lbf (133 N) to set the door in motion; and 15 lbf (67 N) to fully open the door, according to BHMA A156.19.

If required, retain first paragraph below for swinging and folding automatic entrances.  Center pivots are typically provided by manufacturers at hinge stile and can be used for single- or double-acting doors.  Offset hinges are used between panels of folding doors.  Other types of hinges for automatic entrances are uncommon or nonexistent.  Verify with manufacturers the availability of offset pivots or butt hinges before specifying them for swinging automatic entrances.  Consider using automatic door operators provided separately from entrance doors and frames if other than center pivots are required for swinging and folding doors.

E. Hinges:

1. Center-Pivot Sets:  BHMA A156.4, Grade 1, with exposed parts of cast-aluminum alloy.

2. Offset Pivots:  BHMA A156.4, Grade 1, with exposed parts of cast-aluminum alloy.

Butt hinges in subparagraph below are used only for single-acting doors.  Revise hinge size for doors more than 36 inches (914 mm) wide.

3. Butt Hinges:  BHMA A156.1, Grade 1, 5-knuckle, 4-1/2-by-4-inch (114-by-102-mm) ball-bearing butts.

a. Provide nonremovable pins at hinges exposed on outside of door.

b. Provide nonferrous hinges for doors exposed to weather.

c. Provide 3 hinges at each leaf for doors up to 36 inches (914 mm) wide and 80 inches (2032 mm) tall; provide 4 hinges at each leaf for taller doors.

F. Deadlocks:  Manufacturer's standard deadbolt operated by exterior cylinder and interior thumb turn, with minimum 1-inch- (25-mm-) long throw bolt; BHMA A156.5, Grade 1.

1. Cylinders:  [BHMA A156.5, Grade 1, six-pin mortise type.] [As specified in Division 8 Section "Door Hardware."]

a. Keying:  [No master] [Integrate into building master] key system.

Retain first option in first subparagraph below for stile and rail doors; retain second option for all-glass sliding doors.

2. Deadbolts:  [Laminated-steel hook] [Steel], mortise type, BHMA A156.5, Grade 1.

Retain one or more of four subparagraphs below for stile and rail doors.  Delete if flush bolts are prohibited or if exit devices are required.  Verify requirements of authorities having jurisdiction.

3. Two-Point Locking for Sliding Doors:  Mechanism in stile of active door leaf that automatically extends second lockbolt into [overhead carrier assembly] [threshold].

4. Two-Point Locking for Swinging Doors:  Mechanism in stile of active door leaf that automatically extends second lockbolt into [header] [threshold].

5. Two-Point Locking for Single-Folding Doors:  BHMA A156.5, Grade 1, mortise-type, laminated-steel hookbolt mounted in stile of active door leaf that engages strike jamb when operated by cylinder; and with concealed, vertical flush bolt mounted in hinge stile that engages header when operated by cylinder.

6. Two-Point Locking for Biparting-Folding Doors:  BHMA A156.5, Grade 1, mortise-type, laminated-steel hookbolt mounted in stile of active door leaf that engages active leaf of opposite door when operated by cylinder; and with concealed, vertical flush bolts mounted in each hinge stile that engage header when operated by cylinders.

Retain first paragraph below only for sliding doors.  If retaining, delete "Deadlocks" Paragraph above.  Retain below only where essential for security purposes.  Verify requirements with authorities having jurisdiction.  "Fail secure" means that when power is off, door is locked.  "Fail safe" means that when power is off, door is unlocked.  Fail secure is typical for automatic entrances.

G. Automatic Locking for Sliding Door:  Electrically controlled device mounted in header that automatically locks door against sliding when in closed position.  Provide fail [secure] [safe] operation if power fails.

Retain first subparagraph below only for emergency breakaway doors.

1. Include concealed, vertical-rod exit devices, UL 305, with latching into threshold and overhead carrier assembly and released by [full-width panic bar] [push paddle]; and that prevent emergency breakaway doors from swinging and that permit emergency egress.

Retain subparagraph below only if sidelites with emergency breakaway capability are required.

2. Include locking devices for sidelites, to prevent manual break out.

H. Dustproof Strikes for All-Glass Sliding Doors:  [Recessed, floor-type, BHMA A156.16, Grade 1, to receive deadbolt.] [As specified in Division 8 Section "Door Hardware."]

Retain first two paragraphs below only for swinging doors.

I. Push Bars:  [As selected by Architect from manufacturer's full range of full-door-width, single] [Manufacturer's standard surface-mounted, aluminum] push bars.

J. Pull Handles:  [As selected by Architect from manufacturer's full range of pull handles and plates] [Manufacturer's standard aluminum pull handles].

Retain first paragraph below only for swinging or folding automatic entrances if required.

K. Thresholds:  BHMA A156.21, extruded-aluminum raised thresholds; with beveled edges with a slope of not more than 1:2 and a maximum height of 1/2 inch (13 mm).  Provide cutouts as required for door operating hardware.

L. Weather Stripping:  Manufacturer's standard replaceable components.

1. Sliding Type:  AAMA 701, made of wool, polypropylene, or nylon woven pile with nylon-fabric or aluminum-strip backing.

Retain both subparagraphs below only for swinging or folding doors.

2. Compression Type:  Made of ASTM D 2000, molded neoprene, or ASTM D 2287, molded PVC.

3. Weather Sweeps:  Manufacturer's standard nylon brush sweep mounted to underside of door bottom.

Retain paragraph below only for swinging or folding doors.

M. Finger Guards:  Manufacturer's standard collapsible neoprene or PVC gasket.

2.8 ACCESSORIES

Retain one of two paragraphs in this article if guide rails are required.  Guide rails are not required for power-assist or low-energy doors, for sliding doors, or if wall or other separator complies with BHMA A156.10 requirements.  However, they might still be useful in some door layout conditions and where mats are used.  See the Evaluations.

A. Guide Rails:  Fabricated from [anodized-aluminum] [stainless-steel] [bars] [tubing] [bars or tubing], minimum 30 inches (762 mm) high; positioned and projecting from face of door jamb for distance as indicated, but not less than that required by BHMA A156.10 for type of door and direction of travel; with filler panel.

1. Filler Panel:  [Expanded aluminum mesh] [Clear polycarbonate plastic] [Colored polycarbonate plastic].

a. Color:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

Retain first subparagraph below if required.

2. Provide intermediate guide rail suitable for supporting photoelectric beams.

3. Mounting:  [Jamb and floor] [Floor, freestanding].

If retaining paragraph below, verify that guide rail design and layout complies with BHMA A156.10.

B. Guide Rails:  See Division 5 Section "[Pipe and Tube Railings] [Ornamental Railings]."

2.9 FABRICATION

A. General:  Factory fabricate automatic entrance components to designs, sizes, and thicknesses indicated and to comply with indicated standards.

1. Form aluminum shapes before finishing.

2. Weld in concealed locations to greatest extent possible to minimize distortion or discoloration of finish.  Remove weld spatter and welding oxides from exposed surfaces by descaling or grinding.

3. Use concealed fasteners to greatest extent possible.  Where exposed fasteners are required, use countersunk Phillips flat-head machine screws[, finished to match framing] [, fabricated from stainless steel].

a. Where fasteners are subject to loosening or turning out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

b. Reinforce members as required to receive fastener threads.

4. Where aluminum will contact dissimilar metals, protect against galvanic action by painting contact surfaces with primer or by applying sealant or tape recommended by manufacturer for this purpose.

B. Framing:  Provide automatic entrances as prefabricated assemblies.  Complete fabrication, assembly, finishing, hardware application, and other work before shipment to Project site.

1. Fabricate tubular and channel frame assemblies with manufacturer's standard welded or mechanical joints.  Provide subframes and reinforcement as required for a complete system to support required loads.

2. Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

3. Form profiles that are sharp, straight, and free of defects or deformations.

4. Provide components with concealed fasteners and anchor and connection devices.

5. Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

6. Fabricate exterior components to drain water passing joints and condensation and moisture occurring or migrating within system to the exterior.

7. Provide anchorage and alignment brackets for concealed support of assembly from building structure.

8. Allow for thermal expansion of exterior units.

C. Doors:  Factory fabricated and assembled in profiles indicated.  Reinforce as required to support imposed loads and for installing hardware.

Retain first paragraph below only for metal-clad finishes.

D. Metal Cladding:  Provide metal cladding, completely cladding all visible surfaces as part of prefabricated entrance assemblies before shipment to Project site.

1. Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

2. Form profiles that are sharp, straight, and free of defects or deformations.

3. Provide components with concealed fasteners and anchor and connection devices.

4. Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

5. Fabricate exterior components to drain water passing joints and condensation and moisture occurring or migrating within system to the exterior.

6. Allow for thermal expansion at exterior entrances.

E. Door Operators:  Factory fabricated and installed in headers, including adjusting and testing.

F. Glazing:  Fabricate framing with minimum glazing edge clearances for thickness and type of glazing indicated, according to GANA's "Glazing Manual."

Insert requirements for factory glazing if available from manufacturers.  Automatic entrances are generally field glazed.

G. Hardware:  Factory install hardware to greatest extent possible; remove only as required for final finishing operation and for delivery to and installation at Project site.  Cut, drill, and tap for factory-installed hardware before applying finishes.

1. Provide sliding-type weather stripping, mortised into door, at perimeter of doors[ and breakaway sidelites].

Retain remaining subparagraphs only for swinging and folding doors.

2. Provide compression-type weather stripping at fixed stops of exterior doors.  At locations without fixed stops, provide sliding-type weather stripping retained in adjustable strip mortised into door edge.

3. Provide weather sweeps mounted to underside of door bottoms of exterior doors.

Retain subparagraph below if pivoted doors are included.

4. Provide finger guards at each pivoted entrance door that has clearance at hinge side greater than 1/4 inch (6 mm) and less than 3/4 inch (19 mm) with door in any position.  Anchor guards to hinge-jamb frame.

H. Activation and Safety Devices:

1. General:  Factory install devices in doors and headers as required by BHMA A156.10 for type of door and direction of travel.

Retain one of two subparagraphs below if photoelectric beams are required.

2. Install photoelectric beams in vertical jambs of sidelites, with dimension above finished floor as follows:

a. Top Beam:  48 inches (1219 mm).

b. Bottom Beam:  24 inches (610 mm).

3. Install photoelectric beams in sides of guide rails, with dimension above finished floor not less than 24 inches (610 mm).

2.10 GENERAL FINISH REQUIREMENTS

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

B. Protect mechanical finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

Retain first paragraph below for coatings and anodic finishes.

C. Apply organic and anodic finishes to formed metal after fabrication unless otherwise indicated.

D. Appearance of Finished Work:  Noticeable variations in same piece are not acceptable.  Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

2.11 ALUMINUM FINISHES

Retain finishes in this article to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.  Revise mechanical finish if custom anodized finish is required and availability is verified.  If needed and available from manufacturers selected, insert requirements for stainless-steel and copper-alloy finishes.

Retain one of two options in first paragraph below.  Class II finish is standard with many manufacturers; Class I finish is heavy anodized.  Verify availability with manufacturers selected.

A. Clear Anodic Finish:  AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in first paragraph below.  Verify availability with manufacturers selected.

B. Color Anodic Finish:  AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

First paragraph below references AAMA standard for pigmented organic coating on extrusions and panels.

C. Baked-Enamel or Powder-Coat Finish:  AAMA 2603 except with a minimum dry film thickness of 1.5 mils (0.04 mm).  Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

Retain one of two paragraphs below; if both are required, indicate location of each system on Drawings, in schedules, or by inserts.  Retain AAMA 2604 or AAMA 2605 for high- or superior-performance organic coatings, respectively, on extrusions and panels.  These coatings are typically used only for exterior entrances.  If specific products are required, name coating manufacturers and products.

D. High-Performance Organic Finish:  2-coat fluoropolymer finish complying with [AAMA 2604] [AAMA 2605] and containing not less than [50] [70] percent PVDF resin by weight in color coat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

E. High-Performance Organic Finish:  3-coat fluoropolymer finish complying with AAMA 2605 and containing not less than [50] [70] percent PVDF resin by weight in both color coat and clear topcoat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine conditions, with Installer present, for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of automatic entrances.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. General:  Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion.  Rigidly secure nonmovement joints.  Seal joints watertight.

1. Where aluminum will contact dissimilar metals, protect against galvanic action by painting contact surfaces with primer or by applying sealant or tape recommended by manufacturer for this purpose.

2. Where aluminum will contact concrete or masonry, protect against corrosion by painting contact surfaces with bituminous paint.

B. Entrances:  Install automatic entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

Retain first subparagraph below for field-installed hardware items.  Retain option in second subparagraph only for sliding or folding doors.

1. Install surface-mounted hardware using concealed fasteners to greatest extent possible.

2. Set headers,[ carrier assemblies, tracks,] operating brackets, and guides level and true to location with anchorage for permanent support.

3. Install components to drain water passing joints, condensation occurring within framing members, and moisture migrating within system to exterior.

Retain first subparagraph below only for sliding doors if required.  Retain second subparagraph only for swinging and folding doors if required.

4. Level recesses for recessed thresholds using nonshrink grout.

5. Provide thresholds [at exterior doors] [and] [where indicated].

C. Door Operators:  Connect door operators to electrical power distribution system as specified in Division 16 Sections.

Retain first paragraph below only if access-control devices are inserted in Part 2.

D. Access-Control Devices:  Connect access-control devices to access-control system as specified in Division 16 Sections.

E. Activation and Safety Devices:  Install and adjust devices to provide detection field and functions indicated.

Retain first paragraph below if guide rails are specified in Part 2.  Delete if guide rails are specified in another Section.

F. Guide Rails:  Install rails according to BHMA A156.10 including Appendix A and manufacturer's written instructions unless otherwise indicated.

Retain first paragraph below only if factory glazing is not required in Part 2.

G. Glazing:  Install glazing as specified in Division 8 Section "[Glazing] [Security Glazing]."

H. Sealants:  Comply with requirements specified in Division 7 Section "Joint Sealants" to provide weathertight installation.

1. Set [thresholds, ] [bottom-guide track system, ]framing members and flashings in full sealant bed.

2. Seal perimeter of framing members with sealant.

I. Signage:  Apply signage on both sides of each door[ and breakaway sidelight] as required by referenced door standards.

J. Wiring within Automatic Entrance Enclosures:  Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's written limitations on bending radii.  Provide and use lacing bars and distribution spools.

3.3 FIELD QUALITY CONTROL

Retain first option in first paragraph below if Owner engages inspector.  If retaining second option, retain "Field quality-control reports" Paragraph in "Submittals" Article.  Delete this article if not required or if not available from manufacturers selected.

A. Inspection:  [Owner will engage a] [Engage Installer's] certified inspector to test and inspect automatic entrances and prepare test and inspection reports.

1. Certified inspector shall test and inspect each automatic entrance to determine compliance of installed systems with applicable BHMA standards.

2. Inspection Report:  Certified inspector shall submit report in writing to Architect and Contractor within 24 hours after inspection.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

B. Work will be considered defective if it does not pass tests and inspections.

3.4 ADJUSTING

Retain first option in first paragraph below for power-operated doors; retain second option for power-assist and low-energy doors.

A. Adjust door operators, controls, and hardware for smooth and safe operation and for weathertight closure; comply with requirements in [BHMA A156.10] [and] [BHMA A156.19].

B. Lubricate operating hardware and other moving parts as recommended by manufacturer.

C. Readjust door operators and controls after repeated operation of completed installation equivalent to 3 days' use by normal traffic (100 to 300 cycles).  Lubricate hardware, operating equipment, and other moving parts.

D. Occupancy Adjustments:  When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.5 CLEANING AND PROTECTION

A. Clean glass and metal surfaces promptly after installation.  Remove excess glazing and sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish.

1. Comply with requirements in Division 8 Section "[Glazing] [Security Glazing]" for cleaning and maintaining glass.

3.6 DEMONSTRATION

A. Engage a certified inspector to train Owner's maintenance personnel to adjust, operate, and maintain automatic entrances.

END OF SECTION 08460

AUTOMATIC ENTRANCE DOORS
08460 - 1

