Copyright 2005 AIA
MASTERSPEC Full Length
03/05 (R 06/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15082 - PLUMBING INSULATION
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Insulation Materials:

a. Calcium silicate.

b. Cellular glass.

c. Flexible elastomeric.

d. Mineral fiber.

e. Phenolic.

f. Polyisocyanurate.

g. Polyolefin.

h. Polystyrene.

2. Insulating cements.

3. Adhesives.

4. Mastics.

5. Lagging adhesives.

6. Sealants.

7. Factory-applied jackets.

8. Field-applied fabric-reinforcing mesh.

9. Field-applied cloths.

10. Field-applied jackets.

11. Tapes.

12. Securements.

13. Corner angles.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section " Fire-Suppression Systems Insulation."

2. Division 15 Section "HVAC Insulation."

1.3 SUBMITTALS

First four paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include thermal conductivity, thickness, and jackets (both factory and field applied, if any).

B. LEED Submittal:

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesives and sealants.

1. Product Data for Credit EQ 4.1:  For adhesives and sealants, including printed statement of VOC content.

C. Shop Drawings:

1. Detail application of protective shields, saddles, and inserts at hangers for each type of insulation and hanger.

2. Detail attachment and covering of heat tracing inside insulation.

3. Detail insulation application at pipe expansion joints for each type of insulation.

4. Detail insulation application at elbows, fittings, flanges, valves, and specialties for each type of insulation.

5. Detail removable insulation at piping specialties, equipment connections, and access panels.

6. Detail application of field-applied jackets.

7. Detail application at linkages of control devices.

8. Detail field application for each equipment type.

Retain first paragraph below to verify products with Samples.

D. Samples:  For each type of insulation and jacket indicated.  Identify each Sample, describing product and intended use.  Sample sizes are as follows:

1. Sample Sizes:

a. Preformed Pipe Insulation Materials:  12 inches (300 mm) long by NPS 2 (DN 50).

b. Sheet Form Insulation Materials:  12 inches (300 mm) square.

c. Jacket Materials for Pipe:  12 inches (300 mm) long by NPS 2 (DN 50).

d. Sheet Jacket Materials:  12 inches (300 mm) square.

e. Manufacturer's Color Charts:  For products where color is specified, show the full range of colors available for each type of finish material.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For qualified Installer.

Retain first paragraph below if surface-burning characteristics specified in "Quality Assurance" Article are specified to be verified by an independent testing agency.

F. Material Test Reports:  From a qualified testing agency acceptable to authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealers, attachments, cements, and jackets, with requirements indicated.  Include dates of tests and test methods employed.

Retain paragraph below if Contractor is responsible for field quality-control testing and inspecting.

G. Field quality-control reports.

1.4 QUALITY ASSURANCE

Retain first paragraph below if available at Project location.  Apprenticeship programs are usually associated with union shops.  Other craft training programs are available.

A. Installer Qualifications:  Skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the Department of Labor, Bureau of Apprenticeship and Training.

When fire-performance characteristics are important requirements, verify surface-burning characteristics of insulation materials by an independent testing agency and require test report submittals.

B. Fire-Test-Response Characteristics:  Insulation and related materials shall have fire-test-response characteristics indicated, as determined by testing identical products per ASTM E 84, by a testing and inspecting agency acceptable to authorities having jurisdiction.  Factory label insulation and jacket materials and adhesive, mastic, tapes, and cement material containers, with appropriate markings of applicable testing and inspecting agency.

1. Insulation Installed Indoors:  Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

2. Insulation Installed Outdoors:  Flame-spread index of 75 or less, and smoke-developed index of 150 or less.

If retaining "Mockups" Paragraph below, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

C. Mockups:  Before installing insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes.  Build mockups in the location indicated or, if not indicated, as directed by Architect.  Use materials indicated for the completed Work.

1. Piping Mockups:

a. One 10-foot (3-m) section of NPS 2 (DN 50) straight pipe.

b. One each of a 90-degree threaded, welded, and flanged elbow.

c. One each of a threaded, welded, and flanged tee fitting.

d. One NPS 2 (DN 50) or smaller valve, and one NPS 2-1/2 (DN 65) or larger valve.

e. Four support hangers including hanger shield and insert.

f. One threaded strainer and one flanged strainer with removable portion of insulation.

g. One threaded reducer and one welded reducer.

h. One pressure temperature tap.

i. One mechanical coupling.

2. Equipment Mockups:  One tank or vessel.

3. For each mockup, fabricate cutaway sections to allow observation of application details for insulation materials, adhesives, mastics, attachments, and jackets.

4. Notify Architect seven days in advance of dates and times when mockups will be constructed.

5. Obtain Architect's approval of mockups before starting insulation application.

Retain first subparagraph below if mockups are not only for establishing appearance factors.

6. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

7. Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

8. Demolish and remove mockups when directed.

1.5 DELIVERY, STORAGE, AND HANDLING

Retain this article to require shipping container markings.  Container marking is an option in ASTM standards; default condition does not include the marking in this article unless specified in the Contract.

A. Packaging:  Insulation material containers shall be marked by manufacturer with appropriate ASTM standard designation, type and grade, and maximum use temperature.

1.6 COORDINATION

A. Coordinate size and location of supports, hangers, and insulation shields specified in Division 15 Section "Hangers and Supports."

B. Coordinate clearance requirements with piping Installer for piping insulation application and equipment Installer for equipment insulation application.  Before preparing piping Shop Drawings, establish and maintain clearance requirements for installation of insulation and field-applied jackets and finishes and for space required for maintenance.

C. Coordinate installation and testing of heat tracing.

1.7 SCHEDULING

A. Schedule insulation application after pressure testing systems and, where required, after installing and testing heat tracing.  Insulation application may begin on segments that have satisfactory test results.

B. Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

PART 2 -  PRODUCTS

2.1 INSULATION MATERIALS

If retaining more than one type of insulation in this article, indicate where each type applies in insulation system schedules.

A. Comply with requirements in Part 3 schedule articles for where insulating materials shall be applied.

See "Product Characteristics" Article in Evaluations for comparisons and temperature ranges for insulation material properties.

B. Products shall not contain asbestos, lead, mercury, or mercury compounds.

C. Products that come in contact with stainless steel shall have a leachable chloride content of less than 50 ppm when tested according to ASTM C 871.

D. Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

E. Foam insulation materials shall not use CFC or HCFC blowing agents in the manufacturing process.

F. Calcium Silicate:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Industrial Insulation Group (The); Thermo-12 Gold.

b. <Insert manufacturer's name; product name or designation.>

2. Preformed Pipe Sections:  Flat-, curved-, and grooved-block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement.  Comply with ASTM C 533, Type I.

3. Flat-, curved-, and grooved-block sections of noncombustible, inorganic, hydrous calcium silicate with a non-asbestos fibrous reinforcement.  Comply with ASTM C 533, Type I.

4. Prefabricated Fitting Covers:  Comply with ASTM C 450 and ASTM C 585 for dimensions used in preforming insulation to cover valves, elbows, tees, and flanges.

G. Cellular Glass:  Inorganic, incombustible, foamed or cellulated glass with annealed, rigid, hermetically sealed cells.  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cell-U-Foam Corporation; Ultra-CUF.

b. Pittsburgh Corning Corporation; Foamglas Super K.

c. <Insert manufacturer's name; product name or designation.>

2. Block Insulation:  ASTM C 552, Type I.

3. Special-Shaped Insulation:  ASTM C 552, Type III.

4. Board Insulation:  ASTM C 552, Type IV.

If retaining both types of insulation in first two subparagraphs below, indicate where each type applies in insulation system schedules.

5. Preformed Pipe Insulation without Jacket:  Comply with ASTM C 552, Type II, Class 1.

6. Preformed Pipe Insulation with Factory-Applied [ASJ] [ASJ-SSL]:  Comply with ASTM C 552, Type II, Class 2.

7. Factory fabricate shapes according to ASTM C 450 and ASTM C 585.

Flexible elastomeric thermal insulation is not suitable for temperatures lower than minus 70 deg F (minus 57 deg C) and higher than 220 deg F (104 deg C).

H. Flexible Elastomeric:  Closed-cell, sponge- or expanded-rubber materials.  Comply with ASTM C 534, Type I for tubular materials and Type II for sheet materials.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Aeroflex USA Inc.; Aerocel.

b. Armacell LLC; AP Armaflex.

c. RBX Corporation; Insul-Sheet 1800 and Insul-Tube 180.

d. <Insert manufacturer's name; product name or designation.>

I. Mineral-Fiber Blanket Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 553, Type II and ASTM C 1290, Type I.  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. CertainTeed Corp.; Duct Wrap.

b. Johns Manville; Microlite.

c. Knauf Insulation; Duct Wrap.

d. Manson Insulation Inc.; Alley Wrap.

e. Owens Corning; All-Service Duct Wrap.

f. <Insert manufacturer's name; product name or designation.>

J. High-Temperature, Mineral-Fiber Blanket Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 553, Type V, without factory-applied jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Johns Manville; HTB 23 Spin-Glas.

b. Owens Corning; High Temperature Flexible Batt Insulations.

c. <Insert manufacturer's name; product name or designation.>

For operating temperatures higher than 250 deg F (121 deg C), use board insulation in first paragraph below.  The most common jacket for equipment applications is ASJ.

K. Mineral-Fiber Board Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 612, Type IA or Type IB.  For equipment applications, provide insulation [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied FSK jacket].  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. CertainTeed Corp.; Commercial Board.

b. Fibrex Insulations Inc.; FBX.

c. Johns Manville; 800 Series Spin-Glas.

d. Knauf Insulation; Insulation Board.

e. Manson Insulation Inc.; AK Board.

f. Owens Corning; Fiberglas 700 Series.

g. <Insert manufacturer's name; product name or designation.>

For operating temperatures higher than 250 deg F (121 deg C), use high-temperature board insulation in first paragraph below.

L. High-Temperature, Mineral-Fiber Board Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 612, Type III, without factory-applied jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fibrex Insulations Inc.; FBX.

b. Johns Manville; 1000 Series Spin-Glas.

c. Owens Corning; High Temperature Industrial Board Insulations.

d. Rock Wool Manufacturing Company; Delta Board.

e. Roxul Inc.; Roxul RW.

f. Thermafiber; Thermafiber Industrial Felt.

g. <Insert manufacturer's name; product name or designation.>

M. Mineral-Fiber, Preformed Pipe Insulation:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fibrex Insulations Inc.; Coreplus 1200.

b. Johns Manville; Micro-Lok.

c. Knauf Insulation; 1000(Pipe Insulation.

d. Manson Insulation Inc.; Alley-K.

e. Owens Corning; Fiberglas Pipe Insulation.

f. <Insert manufacturer's name; product name or designation.>

ASJ requires field-applied adhesive and staples.  ASJ with SSL does not require field-applied adhesive and staples, resulting in reduced installation labor.

2. Type I, 850 deg F (454 deg C) Materials:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 547, Type I, Grade A, [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied ASJ-SSL].  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Pipe and tank insulation is used for large-diameter piping and vessels.  ASJ is commonly used.

N. Mineral-Fiber, Pipe and Tank Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Semirigid board material with factory-applied [ASJ] [FSK jacket] complying with ASTM C 1393, Type II or Type IIIA Category 2, or with properties similar to ASTM C 612, Type IB.  Nominal density is 2.5 lb/cu. ft. (40 kg/cu. m) or more.  Thermal conductivity (k-value) at 100 deg F (55 deg C) is 0.29 Btu x in./h x sq. ft. x deg F (0.042 W/m x K) or less.  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. CertainTeed Corp.; CrimpWrap.

b. Johns Manville; MicroFlex.

c. Knauf Insulation; Pipe and Tank Insulation.

d. Manson Insulation Inc.; AK Flex.

e. Owens Corning; Fiberglas Pipe and Tank Insulation.

f. <Insert manufacturer's name; product name or designation.>

Phenolic insulation is available in Grades 1 and 2.  Grade 1 has a lower thermal conductivity than Grade 2.  Grade 2 is not commercially available.  Grade 1 is available from only one manufacturer.

O. Phenolic:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kingspan Corp.; Koolphen K.

b. <Insert manufacturer's name; product name or designation.>

2. Preformed pipe insulation of rigid, expanded, closed-cell structure.  Comply with ASTM C 1126, Type III, Grade 1.

3. Block insulation of rigid, expanded, closed-cell structure.  Comply with ASTM C 1126, Type II, Grade 1.

4. Factory fabricate shapes according to ASTM C 450 and ASTM C 585.

5. Factory-Applied Jacket:  Requirements are specified in "Factory-Applied Jackets" Article.

a. Preformed Pipe Insulation:  [None] [ASJ].

b. Board for Equipment Applications:  [None] [ASJ].

P. Polyisocyanurate:  Unfaced, preformed, rigid cellular polyisocyanurate material intended for use as thermal insulation.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Apache Products Company; ISO-25.

b. Dow Chemical Company (The); Trymer.

c. Duna USA Inc.; Corafoam.

d. Elliott Company; Elfoam.

e. <Insert manufacturer's name; product name or designation.>

2. Comply with ASTM C 591, Type I or Type IV, except thermal conductivity (k-value) shall not exceed 0.19 Btu x in./h x sq. ft. x deg F (0.027 W/m x K) at 75 deg F (24 deg C) after 180 days of aging.

3. Flame-spread index shall be 25 or less and smoke-developed index shall be 50 or less for thickness up to 1-1/2 inches (38 mm) as tested by ASTM E 84.

4. Fabricate shapes according to ASTM C 450 and ASTM C 585.

5. Factory-Applied Jacket:  Requirements are specified in "Factory-Applied Jackets" Article.

a. Pipe Applications:  [None] [ASJ] [ASJ-SSL] [PVDC] [PVDC-SSL].

b. Equipment Applications:  [None] [ASJ] [ASJ-SSL] [PVDC] [PVDC-SSL].

Q. Polyolefin:  Unicellular, polyethylene thermal plastic insulation.  Comply with ASTM C 534 or ASTM C 1427, Type I, Grade 1 for tubular materials and Type II, Grade 1 for sheet materials.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Armacell LLC; Tubolit.

b. Nomaco Inc.; IMCOLOCK, IMCOSHEET, NOMALOCK, and NOMAPLY.

c. RBX Corporation; Therma-cell.

d. <Insert manufacturer's name; product name or designation.>

Polystyrene is for outdoor use only; its flame-spread/smoke-developed indexes are not suitable for most indoor applications.

R. Polystyrene:  Rigid, extruded cellular polystyrene intended for use as thermal insulation.  Comply with ASTM C 578, Type IV or Type XIII, except thermal conductivity (k-value) shall not exceed 0.26 Btu x in./h x sq. ft. x deg F (0.038 W/m x K) after 180 days of aging.  Fabricate shapes according to ASTM C 450 and ASTM C 585.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Dow Chemical Company (The); Styrofoam.

b. Knauf Insulation; Knauf Polystyrene.

c. <Insert manufacturer's name; product name or designation.>

2.2 INSULATING CEMENTS

Mineral-fiber insulating cement is suitable for temperatures from 100 to 1600 deg F (38 to 871 deg C).  Vermiculite insulating cement is suitable for temperatures from 100 to 1800 deg F (38 to 982 deg C).

A. Mineral-Fiber Insulating Cement:  Comply with ASTM C 195.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Insulco, Division of MFS, Inc.; Triple I.

b. P. K. Insulation Mfg. Co., Inc.; Super-Stik.

c. <Insert manufacturer's name; product name or designation.>

B. Expanded or Exfoliated Vermiculite Insulating Cement:  Comply with ASTM C 196.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. P. K. Insulation Mfg. Co., Inc.; Thermal-V-Kote.

b. <Insert manufacturer's name; product name or designation.>

Mineral-fiber, hydraulic-setting cement is suitable for temperatures from 100 to 1200 deg F (38 to 649 deg C) and for a smooth surface.

C. Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement:  Comply with ASTM C 449/C 449M.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Insulco, Division of MFS, Inc.; SmoothKote.

b. P. K. Insulation Mfg. Co., Inc.; PK No. 127, and Quik-Cote.

c. Rock Wool Manufacturing Company; Delta One Shot.

d. <Insert manufacturer's name; product name or designation.>

2.3 ADHESIVES

Military Specification referenced in this article is the only standard available when this Section was updated.  MIL-A-3316C was last updated in October 1987.

A. Materials shall be compatible with insulation materials, jackets, and substrates and for bonding insulation to itself and to surfaces to be insulated, unless otherwise indicated.

Product attributes in first paragraph below are based on Foster Products; there are variations among manufacturers listed.

B. Calcium Silicate Adhesive:  Fibrous, sodium-silicate-based adhesive with a service temperature range of 50 to 800 deg F (10 to 427 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-97.

b. Foster Products Corporation, H. B. Fuller Company; 81-27/81-93.

c. Marathon Industries, Inc.; 290.

d. Mon-Eco Industries, Inc.; 22-30.

e. Vimasco Corporation; 760.

f. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

C. Cellular-Glass, Phenolic, Polyisocyanurate, and Polystyrene Adhesive:  Solvent-based resin adhesive, with a service temperature range of minus 75 to plus 300 deg F (minus 59 to plus 149 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-96.

b. Foster Products Corporation, H. B. Fuller Company; 81-33.

c. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Flexible Elastomeric and Polyolefin Adhesive:  Comply with MIL-A-24179A, Type II, Class I.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Aeroflex USA Inc.; Aeroseal.

b. Armacell LCC; 520 Adhesive.

c. Foster Products Corporation, H. B. Fuller Company; 85-75.

d. RBX Corporation; Rubatex Contact Adhesive.

e. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

E. Mineral-Fiber Adhesive:  Comply with MIL-A-3316C, Class 2, Grade A.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-82.

b. Foster Products Corporation, H. B. Fuller Company; 85-20.

c. ITW TACC, Division of Illinois Tool Works; S-90/80.

d. Marathon Industries, Inc.; 225.

e. Mon-Eco Industries, Inc.; 22-25.

f. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

F. Polystyrene Adhesive:  Solvent- or water-based, synthetic resin adhesive with a service temperature range of minus 20 to plus 140 deg F (29 to plus 60 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-96.

b. Foster Products Corporation, H. B. Fuller Company; 97-13.

c. <Insert manufacturer's name; product name or designation.>

G. ASJ Adhesive, and FSK and PVDC Jacket Adhesive:  Comply with MIL-A-3316C, Class 2, Grade A for bonding insulation jacket lap seams and joints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-82.

b. Foster Products Corporation, H. B. Fuller Company; 85-20.

c. ITW TACC, Division of Illinois Tool Works; S-90/80.

d. Marathon Industries, Inc.; 225.

e. Mon-Eco Industries, Inc.; 22-25.

f. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

H. PVC Jacket Adhesive:  Compatible with PVC jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Dow Chemical Company (The); 739, Dow Silicone.

b. Johns-Manville; Zeston Perma-Weld, CEEL-TITE Solvent Welding Adhesive.

c. P.I.C. Plastics, Inc.; Welding Adhesive.

d. Speedline Corporation; Speedline Vinyl Adhesive.

e. <Insert manufacturer's name; product name or designation.>

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2.4 MASTICS

The industry does not have a clear definition that categorizes mastics into vapor barriers, vapor retarders, and breather mastics.  Specification follows the nomenclature used by Foster.  Products with a perm rating of 0.1 and lower are considered vapor barriers.  Products with a perm rating greater than 0.1 and less than 1.0 are considered vapor retarders.  Products with a perm rating greater than 1.0 are called "breathable."  Ambient conditions and operating temperatures must be considered when selecting a mastic.  Consider using water-based mastics for environmental reasons.

LEED-NC Credit EQ 4.1 does not address requirements for mastics.

A. Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-C-19565C, Type II.

Retain subparagraph below if low-emitting materials are required.  Consult mastics manufacturers to determine VOC limits.

1. For indoor applications, use mastics that have a VOC content of <Insert value> g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain one of four mastic paragraphs below.  Product attributes in first paragraph are based on Foster; there are variations among manufacturers listed.

B. Vapor-Barrier Mastic:  Water based; suitable for indoor and outdoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-35.

b. Foster Products Corporation, H. B. Fuller Company; 30-90.

c. ITW TACC, Division of Illinois Tool Works; CB-50.

d. Marathon Industries, Inc.; 590.

e. Mon-Eco Industries, Inc.; 55-40.

f. Vimasco Corporation; 749.

g. <Insert manufacturer's name; product name or designation.>

2. Water-Vapor Permeance:  ASTM E 96, Procedure B, 0.013 perm (0.009 metric perm) at 43-mil (1.09-mm) dry film thickness.

3. Service Temperature Range:  Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

4. Solids Content:  ASTM D 1644, 59 percent by volume and 71 percent by weight.

5. Color:  White.

C. Vapor-Barrier Mastic:  Solvent based; suitable for indoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-30.

b. Foster Products Corporation, H. B. Fuller Company; 30-35.

c. ITW TACC, Division of Illinois Tool Works; CB-25.

d. Marathon Industries, Inc.; 501.

e. Mon-Eco Industries, Inc.; 55-10.

f. <Insert manufacturer's name; product name or designation.>

2. Water-Vapor Permeance:  ASTM F 1249, 0.05 perm (0.03 metric perm) at 35-mil (0.9-mm) dry film thickness.

3. Service Temperature Range:  0 to 180 deg F (Minus 18 to plus 82 deg C).

4. Solids Content:  ASTM D 1644, 44 percent by volume and 62 percent by weight.

5. Color:  White.

D. Vapor-Barrier Mastic:  Solvent based; suitable for outdoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; Encacel.

b. Foster Products Corporation, H. B. Fuller Company; 60-95/60-96.

c. Marathon Industries, Inc.; 570.

d. Mon-Eco Industries, Inc.; 55-70.

e. <Insert manufacturer's name; product name or designation.>

2. Water-Vapor Permeance:  ASTM F 1249, 0.05 perm (0.033 metric perm) at 30-mil (0.8-mm) dry film thickness.

3. Service Temperature Range:  Minus 50 to plus 220 deg F (Minus 46 to plus 104 deg C).

4. Solids Content:  ASTM D 1644, 33 percent by volume and 46 percent by weight.

5. Color:  White.

E. Breather Mastic:  Water based; suitable for indoor and outdoor use on above ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-10.

b. Foster Products Corporation, H. B. Fuller Company; 35-00.

c. ITW TACC, Division of Illinois Tool Works; CB-05/15.

d. Marathon Industries, Inc.; 550.

e. Mon-Eco Industries, Inc.; 55-50.

f. Vimasco Corporation; WC-1/WC-5.

g. <Insert manufacturer's name; product name or designation.>

2. Water-Vapor Permeance:  ASTM F 1249, 3 perms (2 metric perms) at 0.0625-inch (1.6-mm) dry film thickness.

3. Service Temperature Range:  Minus 20 to plus 200 deg F (Minus 29 to plus 93 deg C).

4. Solids Content:  63 percent by volume and 73 percent by weight.

5. Color:  White.

2.5 LAGGING ADHESIVES

LEED-NC Credit EQ 4.1 does not address requirements for lagging adhesives.

A. Description:  Comply with MIL-A-3316C, Class I, Grade A, and shall be compatible with insulation materials, jackets, and substrates.

Retain first subparagraph below if low-emitting materials are required.  Consult lagging adhesive manufacturers to determine VOC limits.

1. For indoor applications, use lagging adhesives that have a VOC content of <Insert value> g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

2. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-52.

b. Foster Products Corporation, H. B. Fuller Company; 81-42.

c. Marathon Industries, Inc.; 130.

d. Mon-Eco Industries, Inc.; 11-30.

e. Vimasco Corporation; 136.

f. <Insert manufacturer's name; product name or designation.>

3. Fire-resistant, water-based lagging adhesive and coating for use indoors to adhere fire-resistant lagging cloths over equipment and pipe insulation.

4. Service Temperature Range:  Minus 50 to plus 180 deg F (Minus 46 to plus 82 deg C).

5. Color:  White.

2.6 SEALANTS

Sealants are categorized into "joint sealants" and "flashing sealants."  Joint sealants are primarily used for vapor sealing longitudinal seams and butt joints of insulation materials.  Flashing sealants are primarily used for sealing jacket and mastic materials.

A. Joint Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Joint Sealants for Cellular-Glass, Phenolic, and Polyisocyanurate Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-76.

b. Foster Products Corporation, H. B. Fuller Company; 30-45.

c. Marathon Industries, Inc.; 405.

d. Mon-Eco Industries, Inc.; 44-05.

e. Pittsburgh Corning Corporation; Pittseal 444.

f. Vimasco Corporation; 750.

g. <Insert manufacturer's name; product name or designation.>

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

2. Joint Sealants for Polystyrene Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-70.

b. Foster Products Corporation, H. B. Fuller Company; 30-45/30-46.

c. Marathon Industries, Inc.; 405.

d. Mon-Eco Industries, Inc.; 44-05.

e. Vimasco Corporation; 750.

f. <Insert manufacturer's name; product name or designation.>

3. Materials shall be compatible with insulation materials, jackets, and substrates.

4. Permanently flexible, elastomeric sealant.

5. Service Temperature Range:  Minus 100 to plus 300 deg F (Minus 73 to plus 149 deg C).

6. Color:  White or gray.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

7. For indoor applications, use sealants that have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Materials in first paragraph below are for sealing metal jacket seams and joints.

B. FSK and Metal Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-76-8.

b. Foster Products Corporation, H. B. Fuller Company; 95-44.

c. Marathon Industries, Inc.; 405.

d. Mon-Eco Industries, Inc.; 44-05.

e. Vimasco Corporation; 750.

f. <Insert manufacturer's name; product name or designation.>

2. Materials shall be compatible with insulation materials, jackets, and substrates.

3. Fire- and water-resistant, flexible, elastomeric sealant.

4. Service Temperature Range:  Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

5. Color:  Aluminum.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

6. For indoor applications, use sealants that have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

C. ASJ Flashing Sealants, and Vinyl, PVDC, and PVC Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; CP-76.

b. <Insert manufacturer's name; product name or designation.>

2. Materials shall be compatible with insulation materials, jackets, and substrates.

3. Fire- and water-resistant, flexible, elastomeric sealant.

4. Service Temperature Range:  Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

5. Color:  White.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

6. For indoor applications, use sealants that have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2.7 FACTORY-APPLIED JACKETS

Coordinate types of factory-applied jacket insulation materials selected and types of factory-applied jackets indicated in insulation system schedules.

For insulation materials with factory-applied jackets for use on applications above 140 deg F (60 deg C), specify sufficient insulation thickness to maintain outer surface temperature of insulation below 140 deg F (60 deg C).  140 deg F (60 deg C) surface temperature is set by OSHA for personnel protection.

A. Insulation system schedules indicate factory-applied jackets on various applications.  When factory-applied jackets are indicated, comply with the following:

1. ASJ:  White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C 1136, Type I.

2. ASJ-SSL:  ASJ with self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip; complying with ASTM C 1136, Type I.

3. FSK Jacket:  Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C 1136, Type II.

PVDC and PVDC-SSL jackets in subparagraphs below are proprietary products offered by Dow under the product name "Saran 540 Vapor Retarder Film" and "Saran 560 Vapor Retarder Film."

4. PVDC Jacket for Indoor Applications:  4-mil- (0.10-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.02 perms (0.013 metric perms) when tested according to ASTM E 96 and with a flame-spread index of 5 and a smoke-developed index of 20 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) Dow Chemical Company (The); Saran 540 Vapor Retarder Film and Saran 560 Vapor Retarder Film.

2) <Insert manufacturer's name; product name or designation.>

5. PVDC Jacket for Outdoor Applications:  6-mil- (0.15-mm-) thick, white PVDC biaxially oriented barrier film with a permeance at 0.01 perms (0.007 metric perms) when tested according to ASTM E 96 and with a flame-spread index of 5 and a smoke-developed index of 25 when tested according to ASTM E 84.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) Dow Chemical Company (The); Saran 540 Vapor Retarder Film and Saran 560 Vapor Retarder Film.

2) <Insert manufacturer's name; product name or designation.>

6. PVDC-SSL Jacket:  PVDC jacket with a self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) Dow Chemical Company (The); Saran 540 Vapor Retarder Film and Saran 560 Vapor Retarder Film.

2) <Insert manufacturer's name; product name or designation.>

2.8 FIELD-APPLIED FABRIC-REINFORCING MESH

Both glass-fiber- and polyester-fabric-reinforcing meshes are acceptable.

Retain three paragraphs below to give Contractor option to use either glass-fiber or polyester fabric.

A. Woven Glass-Fiber Fabric for Pipe Insulation:  Approximately 2 oz./sq. yd. (68 g/sq. m) with a thread count of 10 strands by 10 strands/sq. inch (4 strands by 4 strands/sq. mm) for covering pipe and pipe fittings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Vimasco Corporation; Elastafab 894.

b. <Insert manufacturer's name; product name or designation.>

B. Woven Glass-Fiber Fabric for Equipment Insulation:  Approximately 6 oz./sq. yd. (203 g/sq. m) with a thread count of 5 strands by 5 strands/sq. inch (2 strands by 2 strands/sq. mm) for covering equipment.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; Chil-Glas No. 5.

b. <Insert manufacturer's name; product name or designation.>

C. Woven Polyester Fabric:  Approximately 1 oz./sq. yd. (34 g/sq. m) with a thread count of 10 strands by 10 strands/sq. inch (4 strands by 4 strands/sq. mm), in a Leno weave, for equipment and pipe.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Foster Products Corporation, H. B. Fuller Company; Mast-A-Fab.

b. Vimasco Corporation; Elastafab 894.

c. <Insert manufacturer's name; product name or designation.>

2.9 FIELD-APPLIED CLOTHS

A. Woven Glass-Fiber Fabric:  Comply with MIL-C-20079H, Type I, plain weave, and presized a minimum of 8 oz./sq. yd. (271 g/sq. m).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Alpha Associates, Inc.; Alpha-Maritex 84215 and 84217/9485RW, Luben 59.

b. <Insert manufacturer's name; product name or designation.>

2.10 FIELD-APPLIED JACKETS

Insulation jackets in this article are for field application.  ASTM C 921, Type I, is for use over insulation on equipment and pipes operating at below ambient temperatures at least part of the time or where a vapor barrier is required.  ASTM C 921, Type II, is for use over insulation on pipes operating above ambient temperatures or where a vapor retarder is not required.

A. Field-applied jackets shall comply with ASTM C 921, Type I, unless otherwise indicated.

Although other thicknesses for PVC jackets are available, a flame-spread index of 25 and a smoke-developed index of 50 apply only to thicknesses of 30 mils (0.8 mm) and less.

B. PVC Jacket:  High-impact-resistant, UV-resistant PVC complying with ASTM D 1784, Class 16354-C; thickness as scheduled; roll stock ready for shop or field cutting and forming.  Thickness is indicated in field-applied jacket schedules.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Johns Manville; Zeston.

b. P.I.C. Plastics, Inc.; FG Series.

c. Proto PVC Corporation; LoSmoke.

d. Speedline Corporation; SmokeSafe.

e. <Insert manufacturer's name; product name or designation.>

2. Adhesive:  As recommended by jacket material manufacturer.

PVC jackets are available in several colors.  Colored jackets may be used to replace field painting.  UV rays fade colors in exterior applications.  Some colors (black, gray, and white) do not fade as quickly as other colors (red, orange, and green).  Colored jackets have different emissivity and are not recommended for outdoor use.

3. Color:  [White] [Color-code jackets based on system.  Color as selected by Architect].

4. Factory-fabricated fitting covers to match jacket if available; otherwise, field fabricate.

a. Shapes:  45- and 90-degree, short- and long-radius elbows, tees, valves, flanges, unions, reducers, end caps, soil-pipe hubs, traps, mechanical joints, and P-trap and supply covers for lavatories.

5. Factory-fabricated tank heads and tank side panels.

C. Metal Jacket:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products, Division of ITW; Metal Jacketing Systems.

b. PABCO Metals Corporation; Surefit.

c. RPR Products, Inc.; Insul-Mate.

d. <Insert manufacturer's name; product name or designation.>

2. Aluminum Jacket:  Comply with ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105 or 5005, Temper H-14.

a. [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

b. Finish and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and Polysurlyn barrier offers the best protection.  For most indoor applications, 1-mil (0.025-mm) barrier is adequate.  For outdoor applications, select either 3-mil (0.075-mm) or Polysurlyn barrier.

c. Moisture Barrier for Indoor Applications:  [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick Polysurlyn].

d. Moisture Barrier for Outdoor Applications:  [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick Polysurlyn].

e. Factory-Fabricated Fitting Covers:

1) Same material, finish, and thickness as jacket.

2) Preformed 2-piece or gore, 45- and 90-degree, short- and long-radius elbows.

3) Tee covers.

4) Flange and union covers.

5) End caps.

6) Beveled collars.

7) Valve covers.

8) Field fabricate fitting covers only if factory-fabricated fitting covers are not available.

3. Stainless-Steel Jacket:  ASTM A 167 or ASTM A 240/A 240M.

a. [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

b. Material, finish, and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and Polysurlyn barrier offers the best protection.  For most indoor applications, 1-mil (0.025-mm) barrier is adequate.

c. Moisture Barrier for Indoor Applications:  [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick Polysurlyn].

d. Moisture Barrier for Outdoor Applications:  [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick Polysurlyn].

e. Factory-Fabricated Fitting Covers:

1) Same material, finish, and thickness as jacket.

2) Preformed 2-piece or gore, 45- and 90-degree, short- and long-radius elbows.

3) Tee covers.

4) Flange and union covers.

5) End caps.

6) Beveled collars.

7) Valve covers.

8) Field fabricate fitting covers only if factory-fabricated fitting covers are not available.

D. Underground Direct-Buried Jacket:  125-mil- (3.2-mm-) thick vapor barrier and waterproofing membrane consisting of a rubberized bituminous resin reinforced with a woven-glass fiber or polyester scrim and laminated aluminum foil.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Pittsburgh Corning Corporation; Pittwrap.

b. Polyguard; Insulrap No Torch 125.

c. <Insert manufacturer's name; product name or designation.>

2.11 TAPES

Product performance is based on products manufactured by Venture Tape; there are slight variations among manufacturers listed.

A. ASJ Tape:  White vapor-retarder tape matching factory-applied jacket with acrylic adhesive, complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Avery Dennison Corporation, Specialty Tapes Division; Fasson 0835.

b. Compac Corp.; 104 and 105.

c. Ideal Tape Co., Inc., an American Biltrite Company; 428 AWF ASJ.

d. Venture Tape; 1540 CW Plus, 1542 CW Plus, and 1542 CW Plus/SQ.

e. <Insert manufacturer's name; product name or designation.>

2. Width:  3 inches (75 mm).

3. Thickness:  11.5 mils (0.29 mm).

4. Adhesion:  90 ounces force/inch (1.0 N/mm) in width.

5. Elongation:  2 percent.

6. Tensile Strength:  40 lbf/inch (7.2 N/mm) in width.

7. ASJ Tape Disks and Squares:  Precut disks or squares of ASJ tape.

B. FSK Tape:  Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Avery Dennison Corporation, Specialty Tapes Division; Fasson 0827.

b. Compac Corp.; 110 and 111.

c. Ideal Tape Co., Inc., an American Biltrite Company; 491 AWF FSK.

d. Venture Tape; 1525 CW, 1528 CW, and 1528 CW/SQ.

e. <Insert manufacturer's name; product name or designation.>

2. Width:  3 inches (75 mm).

3. Thickness:  6.5 mils (0.16 mm).

4. Adhesion:  90 ounces force/inch (1.0 N/mm) in width.

5. Elongation:  2 percent.

6. Tensile Strength:  40 lbf/inch (7.2 N/mm) in width.

7. FSK Tape Disks and Squares:  Precut disks or squares of FSK tape.

C. PVC Tape:  White vapor-retarder tape matching field-applied PVC jacket with acrylic adhesive.  Suitable for indoor and outdoor applications.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Avery Dennison Corporation, Specialty Tapes Division; Fasson 0555.

b. Compac Corp.; 130.

c. Ideal Tape Co., Inc., an American Biltrite Company; 370 White PVC tape.

d. Venture Tape; 1506 CW NS.

e. <Insert manufacturer's name; product name or designation.>

2. Width:  2 inches (50 mm).

3. Thickness:  6 mils (0.15 mm).

4. Adhesion:  64 ounces force/inch (0.7 N/mm) in width.

5. Elongation:  500 percent.

6. Tensile Strength:  18 lbf/inch (3.3 N/mm) in width.

D. Aluminum-Foil Tape:  Vapor-retarder tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Avery Dennison Corporation, Specialty Tapes Division; Fasson 0800.

b. Compac Corp.; 120.

c. Ideal Tape Co., Inc., an American Biltrite Company; 488 AWF.

d. Venture Tape; 3520 CW.

e. <Insert manufacturer's name; product name or designation.>

2. Width:  2 inches (50 mm).

3. Thickness:  3.7 mils (0.093 mm).

4. Adhesion:  100 ounces force/inch (1.1 N/mm) in width.

5. Elongation:  5 percent.

6. Tensile Strength:  34 lbf/inch (6.2 N/mm) in width.

PVDC tape is a proprietary product offered by Dow under the product names "Saran 540 Vapor Retarder Tape" and "Saran 560 Vapor Retarder Tape."

E. PVDC Tape:  White vapor-retarder PVDC tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Dow Chemical Company (The); Saran 540 Vapor Retarder Tape.

b. <Insert manufacturer's name; product name or designation.>

2. Width:  3 inches (75 mm).

3. Film Thickness:  [4 mils (0.10 mm)] [6 mils (0.15 mm)].

4. Adhesive Thickness:  1.5 mils (0.04 mm).

5. Elongation at Break:  145 percent.

6. Tensile Strength:  55 lbf/inch (10.1 N/mm) in width.

2.12 SECUREMENTS

A. Bands:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Childers Products; Bands.

b. PABCO Metals Corporation; Bands.

c. RPR Products, Inc.; Bands.

d. <Insert manufacturer's name; product name or designation.>

Wing seals are primarily used for fastening bands together.  Closed seals are occasionally used for large, 84-inch- (2130-mm-) diameter applications and where used with springs.  Wing seals are reusable; closed seals are not.

2. Stainless Steel:  ASTM A 167 or ASTM A 240/A 240M, Type [304] [316] [304 or Type 316]; 0.015 inch (0.38 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [closed seal] [wing or closed seal].

3. Aluminum:  ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14, 0.020 inch (0.51 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [closed seal] [wing or closed seal].

Springs are used for large, 84-inch- (2130-mm-) diameter applications and on applications with rapid changes in expansion and contraction.

4. Springs:  Twin spring set constructed of stainless steel with ends flat and slotted to accept metal bands.  Spring size determined by manufacturer for application.

B. Insulation Pins and Hangers:

1. Capacitor-Discharge-Weld Pins:  Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) AGM Industries, Inc.; CWP-1.

2) GEMCO; CD.

3) Midwest Fasteners, Inc.; CD.

4) Nelson Stud Welding; TPA, TPC, and TPS.

5) <Insert manufacturer's name; product name or designation.>

2. Cupped-Head, Capacitor-Discharge-Weld Pins:  Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) AGM Industries, Inc.; CWP-1.

2) GEMCO; Cupped Head Weld Pin.

3) Midwest Fasteners, Inc.; Cupped Head.

4) Nelson Stud Welding; CHP.

5) <Insert manufacturer's name; product name or designation.>

3. Metal, Adhesively Attached, Perforated-Base Insulation Hangers:  Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place.  Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) AGM Industries, Inc.; Tactoo Insul-Hangers, Series T.

2) GEMCO; Perforated Base.

3) Midwest Fasteners, Inc.; Spindle.

4) <Insert manufacturer's name; product name or designation.>

b. Baseplate:  Perforated, galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

c. Spindle:  [Copper- or zinc-coated, low carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

d. Adhesive:  Recommended by hanger manufacturer.  Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

4. Nonmetal, Adhesively Attached, Perforated-Base Insulation Hangers:  Baseplate fastened to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place.  Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) GEMCO; Nylon Hangers.

2) Midwest Fasteners, Inc.; Nylon Insulation Hangers.

3) <Insert manufacturer's name; product name or designation.>

b. Baseplate:  Perforated, nylon sheet, 0.030 inch (0.76 mm) thick by 1-1/2 inches (38 mm) in diameter.

c. Spindle:  Nylon, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated, up to 2-1/2 inches (63 mm).

d. Adhesive:  Recommended by hanger manufacturer.  Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

5. Self-Sticking-Base Insulation Hangers:  Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place.  Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) AGM Industries, Inc.; Tactoo Insul-Hangers, Series TSA.

2) GEMCO; Press and Peel.

3) Midwest Fasteners, Inc.; Self Stick.

4) <Insert manufacturer's name; product name or designation.>

b. Baseplate:  Galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

c. Spindle:  [Copper- or zinc-coated, low carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

d. Adhesive-backed base with a peel-off protective cover.

6. Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm-) thick, [galvanized-steel] [aluminum] [stainless-steel] sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) AGM Industries, Inc.; RC-150.

2) GEMCO; R-150.

3) Midwest Fasteners, Inc.; WA-150.

4) Nelson Stud Welding; Speed Clips.

5) <Insert manufacturer's name; product name or designation.>

b. Protect ends with capped self-locking washers incorporating a spring steel insert to ensure permanent retention of cap in exposed locations.

7. Nonmetal Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm-) thick nylon sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

a. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1) GEMCO.

2) Midwest Fasteners, Inc.

3) <Insert manufacturer's name.>

C. Staples:  Outward-clinching insulation staples, nominal 3/4-inch- (19-mm-) wide, stainless steel or Monel.

In paragraph below, stainless steel is the most common wire used and is best suited for all applications.

D. Wire:  [0.080-inch (2.0-mm) nickel-copper alloy] [0.062-inch (1.6-mm) soft-annealed, stainless steel] [0.062-inch (1.6-mm) soft-annealed, galvanized steel].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. C & F Wire.

b. Childers Products.

c. PABCO Metals Corporation.

d. RPR Products, Inc.

e. <Insert manufacturer's name.>

2.13 CORNER ANGLES

A. PVC Corner Angles:  30 mils (0.8 mm) thick, minimum 1 by 1 inch (25 by 25 mm), PVC according to ASTM D 1784, Class 16354-C.  White or color-coded to match adjacent surface.

B. Aluminum Corner Angles:  0.040 inch (1.0 mm) thick, minimum 1 by 1 inch (25 by 25 mm), aluminum according to ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105 or 5005; Temper H-14.

C. Stainless-Steel Corner Angles:  0.024 inch (0.61 mm) thick, minimum 1 by 1 inch (25 by 25 mm), stainless steel according to ASTM A 167 or ASTM A 240/A 240M, Type [304] [316] [304 or 316].

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and conditions for compliance with requirements for installation and other conditions affecting performance of insulation application.

1. Verify that systems and equipment to be insulated have been tested and are free of defects.

2. Verify that surfaces to be insulated are clean and dry.

3. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

Retain one of first two paragraphs below.  Corrosion of equipment and pipe under insulation, while not typically caused by insulation, is an issue that must be considered during design of any plumbing insulation system.  The potential for corrosion depends on many factors.  Requirements cited in second paragraph represent added measures of protection but are not meant to take the place of proper system design and specification.

A. Surface Preparation:  Clean and dry surfaces to receive insulation.  Remove materials that will adversely affect insulation application.

B. Surface Preparation:  Clean and prepare surfaces to be insulated.  Before insulating, apply a corrosion coating to insulated surfaces as follows:

1. Stainless Steel:  Coat 300 series stainless steel with an epoxy primer 5 mils (0.127 mm) thick and an epoxy finish 5 mils (0.127 mm) thick if operating in a temperature range between 140 and 300 deg F (60 and 149 deg C).  Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

2. Carbon Steel:  Coat carbon steel operating at a service temperature between 32 and 300 deg F (0 and 149 deg C) with an epoxy coating.  Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

C. Coordinate insulation installation with the trade installing heat tracing.  Comply with requirements for heat tracing that apply to insulation.

D. Mix insulating cements with clean potable water; if insulating cements are to be in contact with stainless-steel surfaces, use demineralized water.

3.3 GENERAL INSTALLATION REQUIREMENTS

A. Install insulation materials, accessories, and finishes with smooth, straight, and even surfaces; free of voids throughout the length of equipment and piping including fittings, valves, and specialties.

B. Install insulation materials, forms, vapor barriers or retarders, jackets, and thicknesses required for each item of equipment and pipe system as specified in insulation system schedules.

C. Install accessories compatible with insulation materials and suitable for the service.  Install accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

D. Install insulation with longitudinal seams at top and bottom of horizontal runs.

E. Install multiple layers of insulation with longitudinal and end seams staggered.

F. Do not weld brackets, clips, or other attachment devices to piping, fittings, and specialties.

G. Keep insulation materials dry during application and finishing.

H. Install insulation with tight longitudinal seams and end joints.  Bond seams and joints with adhesive recommended by insulation material manufacturer.

I. Install insulation with least number of joints practical.

J. Where vapor barrier is indicated, seal joints, seams, and penetrations in insulation at hangers, supports, anchors, and other projections with vapor-barrier mastic.

1. Install insulation continuously through hangers and around anchor attachments.

2. For insulation application where vapor barriers are indicated, extend insulation on anchor legs from point of attachment to supported item to point of attachment to structure.  Taper and seal ends at attachment to structure with vapor-barrier mastic.

3. Install insert materials and install insulation to tightly join the insert.  Seal insulation to insulation inserts with adhesive or sealing compound recommended by insulation material manufacturer.

4. Cover inserts with jacket material matching adjacent pipe insulation.  Install shields over jacket, arranged to protect jacket from tear or puncture by hanger, support, and shield.

K. Apply adhesives, mastics, and sealants at manufacturer's recommended coverage rate and wet and dry film thicknesses.

L. Install insulation with factory-applied jackets as follows:

1. Draw jacket tight and smooth.

2. Cover circumferential joints with 3-inch- (75-mm-) wide strips, of same material as insulation jacket.  Secure strips with adhesive and outward clinching staples along both edges of strip, spaced 4 inches (100 mm) o.c.

3. Overlap jacket longitudinal seams at least 1-1/2 inches (38 mm).  Install insulation with longitudinal seams at bottom of pipe.  Clean and dry surface to receive self-sealing lap.  Staple laps with outward clinching staples along edge at [2 inches (50 mm)] [4 inches (100 mm)] o.c.

a. For below ambient services, apply vapor-barrier mastic over staples.

4. Cover joints and seams with tape as recommended by insulation material manufacturer to maintain vapor seal.

5. Where vapor barriers are indicated, apply vapor-barrier mastic on seams and joints and at ends adjacent to pipe flanges and fittings.

M. Cut insulation in a manner to avoid compressing insulation more than 75 percent of its nominal thickness.

N. Finish installation with systems at operating conditions.  Repair joint separations and cracking due to thermal movement.

O. Repair damaged insulation facings by applying same facing material over damaged areas.  Extend patches at least 4 inches (100 mm) beyond damaged areas.  Adhere, staple, and seal patches similar to butt joints.

P. For above ambient services, do not install insulation to the following:

1. Vibration-control devices.

2. Testing agency labels and stamps.

3. Nameplates and data plates.

4. Manholes.

5. Handholes.

6. Cleanouts.

3.4 PENETRATIONS

A. Insulation Installation at Roof Penetrations:  Install insulation continuously through roof penetrations.

1. Seal penetrations with flashing sealant.

2. For applications requiring only indoor insulation, terminate insulation above roof surface and seal with joint sealant.  For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends.  Seal joint with joint sealant.

3. Extend jacket of outdoor insulation outside roof flashing at least 2 inches (50 mm) below top of roof flashing.

4. Seal jacket to roof flashing with flashing sealant.

B. Insulation Installation at Underground Exterior Wall Penetrations:  Terminate insulation flush with sleeve seal.  Seal terminations with flashing sealant.

C. Insulation Installation at Aboveground Exterior Wall Penetrations:  Install insulation continuously through wall penetrations.

1. Seal penetrations with flashing sealant.

2. For applications requiring only indoor insulation, terminate insulation inside wall surface and seal with joint sealant.  For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends.  Seal joint with joint sealant.

3. Extend jacket of outdoor insulation outside wall flashing and overlap wall flashing at least 2 inches (50 mm).

4. Seal jacket to wall flashing with flashing sealant.

D. Insulation Installation at Interior Wall and Partition Penetrations (That Are Not Fire Rated):  Install insulation continuously through walls and partitions.

E. Insulation Installation at Fire-Rated Wall and Partition Penetrations:  Install insulation continuously through penetrations of fire-rated walls and partitions.

1. Comply with requirements in Division 7 Section "Through-Penetration Firestop Systems" for firestopping and fire-resistive joint sealers.

F. Insulation Installation at Floor Penetrations:

1. Pipe:  Install insulation continuously through floor penetrations.

2. Seal penetrations through fire-rated assemblies.  Comply with requirements in Division 7 Section "Through-Penetration Firestop Systems."

3.5 EQUIPMENT, TANK, AND VESSEL INSULATION INSTALLATION

A. Mineral Fiber, Pipe and Tank Insulation Installation for Tanks and Vessels:  Secure insulation with adhesive and anchor pins and speed washers.

In first subparagraph below, many manufacturers do not recommend 100 percent coverage of adhesive because of the effect on the overall insulation system's fire-performance characteristics.  Verify application coverage recommendations with insulation manufacturer.

1. Apply adhesives according to manufacturer's recommended coverage rates per unit area, for [100] [50] <Insert percentage> percent coverage of tank and vessel surfaces.

2. Groove and score insulation materials to fit as closely as possible to equipment, including contours.  Bevel insulation edges for cylindrical surfaces for tight joints.  Stagger end joints.

3. Protect exposed corners with secured corner angles.

4. Install adhesively attached or self-sticking insulation hangers and speed washers on sides of tanks and vessels as follows:

a. Do not weld anchor pins to ASME-labeled pressure vessels.

b. Select insulation hangers and adhesive that are compatible with service temperature and with substrate.

c. On tanks and vessels, maximum anchor-pin spacing is 3 inches (75 mm) from insulation end joints, and 16 inches (400 mm) o.c. in both directions.

d. Do not overcompress insulation during installation.

e. Cut and miter insulation segments to fit curved sides and domed heads of tanks and vessels.

f. Impale insulation over anchor pins and attach speed washers.

g. Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface.  Cover exposed pins and washers with tape matching insulation facing.

5. Secure each layer of insulation with stainless-steel or aluminum bands.  Select band material compatible with insulation materials.

6. Where insulation hangers on equipment and vessels are not permitted or practical and where insulation support rings are not provided, install a girdle network for securing insulation.  Stretch prestressed aircraft cable around the diameter of vessel and make taut with clamps, turnbuckles, or breather springs.  Place one circumferential girdle around equipment approximately 6 inches (150 mm) from each end.  Install wire or cable between two circumferential girdles 12 inches (300 mm) o.c.  Install a wire ring around each end and around outer periphery of center openings, and stretch prestressed aircraft cable radially from the wire ring to nearest circumferential girdle.  Install additional circumferential girdles along the body of equipment or tank at a minimum spacing of 48 inches (1200 mm) o.c.  Use this network for securing insulation with tie wire or bands.

7. Stagger joints between insulation layers at least 3 inches (75 mm).

8. Install insulation in removable segments on equipment access doors, manholes, handholes, and other elements that require frequent removal for service and inspection.

9. Bevel and seal insulation ends around manholes, handholes, ASME stamps, and nameplates.

10. For equipment with surface temperatures below ambient, apply mastic to open ends, joints, seams, breaks, and punctures in insulation.

B. Flexible Elastomeric Thermal Insulation Installation for Tanks and Vessels:  Install insulation over entire surface of tanks and vessels.

1. Apply 100 percent coverage of adhesive to surface with manufacturer's recommended adhesive.

2. Seal longitudinal seams and end joints.

C. Insulation Installation on Pumps:

1. Fabricate metal boxes lined with insulation.  Fit boxes around pumps and coincide box joints with splits in pump casings.  Fabricate joints with outward bolted flanges.  Bolt flanges on 6-inch (150-mm) centers, starting at corners.  Install 3/8-inch- (10-mm-) diameter fasteners with wing nuts.  Alternatively, secure the box sections together using a latching mechanism.

2. Fabricate boxes from [galvanized steel] [aluminum] [stainless steel], at least [0.040 inch (1.0 mm)] [0.050 inch (1.3 mm)] [0.060 inch (1.6 mm)] thick.

3. For below ambient services, install a vapor barrier at seams, joints, and penetrations.  Seal between flanges with replaceable gasket material to form a vapor barrier.

3.6 GENERAL PIPE INSULATION INSTALLATION

A. Requirements in this article generally apply to all insulation materials except where more specific requirements are specified in various pipe insulation material installation articles.

Where pipe expansion is anticipated, detail expansion compensation for insulation on Drawings and indicate intervals for its occurrence.  See MICA's "National Commercial & Industrial Insulation Standards," Plate No. 41A.

B. Insulation Installation on Fittings, Valves, Strainers, Flanges, and Unions:

1. Install insulation over fittings, valves, strainers, flanges, unions, and other specialties with continuous thermal and vapor-retarder integrity, unless otherwise indicated.

2. Insulate pipe elbows using preformed fitting insulation or mitered fittings made from same material and density as adjacent pipe insulation.  Each piece shall be butted tightly against adjoining piece and bonded with adhesive.  Fill joints, seams, voids, and irregular surfaces with insulating cement finished to a smooth, hard, and uniform contour that is uniform with adjoining pipe insulation.

3. Insulate tee fittings with preformed fitting insulation or sectional pipe insulation of same material and thickness as used for adjacent pipe.  Cut sectional pipe insulation to fit.  Butt each section closely to the next and hold in place with tie wire.  Bond pieces with adhesive.

4. Insulate valves using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.  For valves, insulate up to and including the bonnets, valve stuffing-box studs, bolts, and nuts.  Fill joints, seams, and irregular surfaces with insulating cement.

5. Insulate strainers using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.  Fill joints, seams, and irregular surfaces with insulating cement.  Insulate strainers so strainer basket flange or plug can be easily removed and replaced without damaging the insulation and jacket.  Provide a removable reusable insulation cover.  For below ambient services, provide a design that maintains vapor barrier.

6. Insulate flanges and unions using a section of oversized preformed pipe insulation.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.

7. Cover segmented insulated surfaces with a layer of finishing cement and coat with a mastic.  Install vapor-barrier mastic for below ambient services and a breather mastic for above ambient services.  Reinforce the mastic with fabric-reinforcing mesh.  Trowel the mastic to a smooth and well-shaped contour.

8. For services not specified to receive a field-applied jacket except for flexible elastomeric and polyolefin, install fitted PVC cover over elbows, tees, strainers, valves, flanges, and unions.  Terminate ends with PVC end caps.  Tape PVC covers to adjoining insulation facing using PVC tape.

9. Stencil or label the outside insulation jacket of each union with the word "UNION."  Match size and color of pipe labels.

C. Insulate instrument connections for thermometers, pressure gages, pressure temperature taps, test connections, flow meters, sensors, switches, and transmitters on insulated pipes, vessels, and equipment.  Shape insulation at these connections by tapering it to and around the connection with insulating cement and finish with finishing cement, mastic, and flashing sealant.

Coordinate paragraph below with Drawings.

D. Install removable insulation covers at locations indicated.  Installation shall conform to the following:

1. Make removable flange and union insulation from sectional pipe insulation of same thickness as that on adjoining pipe.  Install same insulation jacket as adjoining pipe insulation.

2. When flange and union covers are made from sectional pipe insulation, extend insulation from flanges or union long at least two times the insulation thickness over adjacent pipe insulation on each side of flange or union.  Secure flange cover in place with stainless-steel or aluminum bands.  Select band material compatible with insulation and jacket.

3. Construct removable valve insulation covers in same manner as for flanges except divide the two-part section on the vertical center line of valve body.

4. When covers are made from block insulation, make two halves, each consisting of mitered blocks wired to stainless-steel fabric.  Secure this wire frame, with its attached insulation, to flanges with tie wire.  Extend insulation at least 2 inches (50 mm) over adjacent pipe insulation on each side of valve.  Fill space between flange or union cover and pipe insulation with insulating cement.  Finish cover assembly with insulating cement applied in two coats.  After first coat is dry, apply and trowel second coat to a smooth finish.

5. Unless a PVC jacket is indicated in field-applied jacket schedules, finish exposed surfaces with a metal jacket.

3.7 CALCIUM SILICATE INSULATION INSTALLATION

A. Insulation Installation on Domestic Water Boiler Breechings:

1. Secure single-layer insulation with stainless-steel bands at 12-inch (300-mm) intervals and tighten bands without deforming insulation material.

2. Install 2-layer insulation with joints tightly butted and staggered at least 3 inches (75 mm).  Secure inner layer with wire spaced at 12-inch (300-mm) intervals.  Secure outer layer with stainless-steel bands at 12-inch (300-mm) intervals.

3. On exposed applications without metal jacket, finish insulation surface with a skim coat of mineral-fiber, hydraulic-setting cement.  When cement is dry, apply flood coat of lagging adhesive and press on one layer of glass cloth.  Overlap edges at least 1 inch (25 mm).  Apply finish coat of lagging adhesive over glass cloth.  Thin finish coat to achieve smooth, uniform finish.

B. Insulation Installation on Straight Pipes and Tubes:

1. Secure single-layer insulation with stainless-steel bands at 12-inch (300-mm) intervals and tighten bands without deforming insulation materials.

2. Install 2-layer insulation with joints tightly butted and staggered at least 3 inches (75 mm).  Secure inner layer with wire spaced at 12-inch (300-mm) intervals.  Secure outer layer with stainless-steel bands at 12-inch (300-mm) intervals.

3. Apply a skim coat of mineral-fiber, hydraulic-setting cement to insulation surface.  When cement is dry, apply flood coat of lagging adhesive and press on one layer of glass cloth or tape.  Overlap edges at least 1 inch (25 mm).  Apply finish coat of lagging adhesive over glass cloth or tape.  Thin finish coat to achieve smooth, uniform finish.

C. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of block insulation of same material and thickness as pipe insulation.

4. Finish flange insulation same as pipe insulation.

D. Insulation Installation on Pipe Fittings and Elbows:

1. Install preformed sections of same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When preformed insulation sections of insulation are not available, install mitered sections of calcium silicate insulation.  Secure insulation materials with wire or bands.

3. Finish fittings insulation same as pipe insulation.

E. Insulation Installation on Valves and Pipe Specialties:

1. Install mitered segments of calcium silicate insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

2. Install insulation to flanges as specified for flange insulation application.

3. Finish valve and specialty insulation same as pipe insulation.

3.8 CELLULAR-GLASS INSULATION INSTALLATION

A. Insulation Installation on Straight Pipes and Tubes:

1. Secure each layer of insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

2. Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

3. For insulation with factory-applied jackets on above ambient services, secure laps with outward clinched staples at 6 inches (150 mm) o.c.

4. For insulation with factory-applied jackets on below ambient services, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

B. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of cellular-glass block insulation of same thickness as pipe insulation.

4. Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

C. Insulation Installation on Pipe Fittings and Elbows:

1. Install preformed sections of same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

2. When preformed sections of insulation are not available, install mitered sections of cellular-glass insulation.  Secure insulation materials with wire or bands.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed sections of cellular-glass insulation to valve body.

2. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

3.9 FLEXIBLE ELASTOMERIC INSULATION INSTALLATION

A. Seal longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

B. Insulation Installation on Pipe Flanges:

1. Install pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of sheet insulation of same thickness as pipe insulation.

4. Secure insulation to flanges and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

C. Insulation Installation on Pipe Fittings and Elbows:

1. Install mitered sections of pipe insulation.

2. Secure insulation materials and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed valve covers manufactured of same material as pipe insulation when available.

2. When preformed valve covers are not available, install cut sections of pipe and sheet insulation to valve body.  Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

4. Secure insulation to valves and specialties and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

3.10 MINERAL-FIBER INSULATION INSTALLATION

A. Insulation Installation on Straight Pipes and Tubes:

1. Secure each layer of preformed pipe insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

2. Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

3. For insulation with factory-applied jackets on above ambient surfaces, secure laps with outward clinched staples at 6 inches (150 mm) o.c.

4. For insulation with factory-applied jackets on below ambient surfaces, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

B. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with mineral-fiber blanket insulation.

4. Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

C. Insulation Installation on Pipe Fittings and Elbows:

1. Install preformed sections of same material as straight segments of pipe insulation when available.

2. When preformed insulation elbows and fittings are not available, install mitered sections of pipe insulation, to a thickness equal to adjoining pipe insulation.  Secure insulation materials with wire or bands.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed sections of same material as straight segments of pipe insulation when available.

2. When preformed sections are not available, install mitered sections of pipe insulation to valve body.

3. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

4. Install insulation to flanges as specified for flange insulation application.

3.11 PHENOLIC INSULATION INSTALLATION

A. General Installation Requirements:

1. Secure single-layer insulation with stainless-steel bands at 12-inch (300-mm) intervals and tighten bands without deforming insulation materials.

2. Install 2-layer insulation with joints tightly butted and staggered at least 3 inches (75 mm).  Secure inner layer with 0.062-inch (1.6-mm) wire spaced at 12-inch (300-mm) intervals.  Secure outer layer with stainless-steel bands at 12-inch (300-mm) intervals.

B. Insulation Installation on Straight Pipes and Tubes:

1. Secure each layer of insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

2. Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

3. For insulation with factory-applied jackets on above ambient services, secure laps with outward clinched staples at 6 inches (150 mm) o.c.

4. For insulation with factory-applied jackets with vapor retarders on below ambient services, do not staple longitudinal tabs but secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

C. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of block insulation of same material and thickness as pipe insulation.

D. Insulation Installation on Pipe Fittings and Elbows:

1. Install preformed insulation sections of same material as straight segments of pipe insulation.  Secure according to manufacturer's written instructions.

E. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed insulation sections of same material as straight segments of pipe insulation.  Secure according to manufacturer's written instructions.

2. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

3.12 POLYISOCYANURATE INSULATION INSTALLATION

A. Insulation Installation on Straight Pipes and Tubes:

1. Secure each layer of insulation to pipe with tape or bands and tighten without deforming insulation materials.  Orient longitudinal joints between half sections in 3 and 9 o'clock positions on the pipe.

2. For insulation with factory-applied jackets with vapor barriers, do not staple longitudinal tabs but secure tabs with additional adhesive or tape as recommended by insulation material manufacturer and seal with vapor-barrier mastic.

3. All insulation shall be tightly butted and free of voids and gaps at all joints.  Vapor barrier must be continuous.  Before installing jacket material, install vapor-barrier system.

B. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, same thickness of adjacent pipe insulation, not to exceed 1-1/2-inch (38-mm) thickness.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of polyisocyanurate block insulation of same thickness as pipe insulation.

C. Insulation Installation on Fittings and Elbows:

1. Install preformed sections of same material as straight segments of pipe insulation.  Secure according to manufacturer's written instructions.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed sections of polyisocyanurate insulation to valve body.

2. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

3.13 POLYOLEFIN INSULATION INSTALLATION

A. Insulation Installation on Straight Pipes and Tubes:

1. Seal split-tube longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

B. Insulation Installation on Pipe Flanges:

1. Install pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of polyolefin sheet insulation of same thickness as pipe insulation.

4. Secure insulation to flanges and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

C. Insulation Installation on Pipe Fittings and Elbows:

1. Install mitered sections of polyolefin pipe insulation.

2. Secure insulation materials and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install cut sections of polyolefin pipe and sheet insulation to valve body.

2. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

4. Secure insulation to valves and specialties, and seal seams with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

3.14 POLYSTYRENE INSULATION INSTALLATION

A. Insulation Installation on Straight Pipes and Tubes:

1. Secure each layer of insulation with tape or bands and tighten bands without deforming insulation materials.  Orient longitudinal joints between half sections in 3 and 9 o'clock positions on the pipe.

2. For insulation with factory-applied jackets with vapor barriers, do not staple longitudinal tabs but secure tabs with additional adhesive or tape as recommended by insulation material manufacturer and seal with vapor-barrier mastic.

3. All insulation shall be tightly butted and free of voids and gaps at all joints.  Vapor barrier must be continuous.  Before installing jacket material, install vapor-barrier system.

B. Insulation Installation on Pipe Flanges:

1. Install preformed pipe insulation to outer diameter of pipe flange.

2. Make width of insulation section same as overall width of flange and bolts, same thickness of adjacent pipe insulation, not to exceed 1-1/2-inch (38-mm) thickness.

3. Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of polystyrene block insulation of same thickness as pipe insulation.

C. Insulation Installation on Pipe Fittings and Elbows:

1. Install preformed insulation sections of same material as straight segments of pipe insulation.  Secure according to manufacturer's written instructions.

D. Insulation Installation on Valves and Pipe Specialties:

1. Install preformed section of polystyrene insulation to valve body.

2. Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

3. Install insulation to flanges as specified for flange insulation application.

3.15 FIELD-APPLIED JACKET INSTALLATION

A. Where glass-cloth jackets are indicated, install directly over bare insulation or insulation with factory-applied jackets.

1. Draw jacket smooth and tight to surface with 2-inch (50-mm) overlap at seams and joints.

2. Embed glass cloth between two 0.062-inch- (1.6-mm-) thick coats of lagging adhesive.

3. Completely encapsulate insulation with coating, leaving no exposed insulation.

B. Where FSK jackets are indicated, install as follows:

1. Draw jacket material smooth and tight.

2. Install lap or joint strips with same material as jacket.

3. Secure jacket to insulation with manufacturer's recommended adhesive.

4. Install jacket with 1-1/2-inch (38-mm) laps at longitudinal seams and 3-inch- (75-mm-) wide joint strips at end joints.

5. Seal openings, punctures, and breaks in vapor-retarder jackets and exposed insulation with vapor-barrier mastic.

C. Where PVC jackets are indicated, install with 1-inch (25-mm) overlap at longitudinal seams and end joints; for horizontal applications, install with longitudinal seams along top and bottom of tanks and vessels.  Seal with manufacturer's recommended adhesive.

1. Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along seam and joint edge.

D. Where metal jackets are indicated, install with 2-inch (50-mm) overlap at longitudinal seams and end joints.  Overlap longitudinal seams arranged to shed water.  Seal end joints with weatherproof sealant recommended by insulation manufacturer.  Secure jacket with stainless-steel bands 12 inches (300 mm) o.c. and at end joints.

E. Where PVDC jackets are indicated, install as follows:

1. Apply three separate wraps of filament tape per insulation section to secure pipe insulation to pipe prior to installation of PVDC jacket.

2. Wrap factory-presized jackets around individual pipe insulation sections with one end overlapping the previously installed sheet.  Install presized jacket with an approximate overlap at butt joint of 2 inches (50 mm) over the previous section.  Adhere lap seal using adhesive or SSL, and then apply 1-1/4 circumferences of appropriate PVDC tape around overlapped butt joint.

3. Continuous jacket can be spiral wrapped around a length of pipe insulation.  Apply adhesive or PVDC tape at overlapped spiral edge.  When electing to use adhesives, refer to manufacturer's written instructions for application of adhesives along this spiral edge to maintain a permanent bond.

4. Jacket can be wrapped in cigarette fashion along length of roll for insulation systems with an outer circumference of 33-1/2 inches (850 mm) or less.  The 33-1/2-inch- (850-mm-) circumference limit allows for 2-inch- (50-mm-) overlap seal.  Using the length of roll allows for longer sections of jacket to be installed at one time.  Use adhesive on the lap seal.  Visually inspect lap seal for "fishmouthing," and use PVDC tape along lap seal to secure joint.

5. Repair holes or tears in PVDC jacket by placing PVDC tape over the hole or tear and wrapping a minimum of 1-1/4 circumferences to avoid damage to tape edges.

3.16 FINISHES

Coordinate first paragraph below with Division 9 painting Sections.  If PVC jackets are specified, consult jacket manufacturers to determine suitable paint products and revise painting Sections to suit Project.

A. Equipment and Pipe Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material:  Paint jacket with paint system identified below and as specified in Division 9 painting Sections.

Retain paint system in subparagraph and associated subparagraph below for a flat, latex-emulsion size over insulation covering an exterior that is subject to normal use and moderate environments.

1. Flat Acrylic Finish:  [Two] <Insert number> finish coats over a primer that is compatible with jacket material and finish coat paint.  Add fungicidal agent to render fabric mildew proof.

a. Finish Coat Material:  Interior, flat, latex-emulsion size.

B. Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

C. Color:  Final color as selected by Architect.  Vary first and second coats to allow visual inspection of the completed Work.

D. Do not field paint aluminum or stainless-steel jackets.

3.17 FIELD QUALITY CONTROL

Inspections in this article are destructive.  Retain if workmanship quality is an important requirement.  Architect should be prepared to reject all work if defective work is discovered in sample inspection.

Retain first paragraph below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Inspect field-insulated equipment, randomly selected by Architect, by removing field-applied jacket and insulation in layers in reverse order of their installation.  Extent of inspection shall be limited to [one] <Insert number> location(s) for each type of equipment defined in the "Equipment Insulation Schedule" Article.  For large equipment, remove only a portion adequate to determine compliance.

2. Inspect pipe, fittings, strainers, and valves, randomly selected by Architect, by removing field-applied jacket and insulation in layers in reverse order of their installation.  Extent of inspection shall be limited to [three] <Insert number> locations of straight pipe, [three] <Insert number> locations of threaded fittings, [three] <Insert number> locations of welded fittings, [two] <Insert number> locations of threaded strainers, [two] <Insert number> locations of welded strainers, [three] <Insert number> locations of threaded valves, and [three] <Insert number> locations of flanged valves for each pipe service defined in the "Piping Insulation Schedule, General" Article.

D. All insulation applications will be considered defective Work if sample inspection reveals noncompliance with requirements.

Materials and thicknesses in schedules below are for single-layer applications.  If multilayer applications are needed, insert additional requirements.

3.18 DOMESTIC WATER BOILER BREECHING INSULATION SCHEDULE

Retain "one of" option in paragraphs in this article to allow Contractor to select piping materials from those retained.

A. Round, exposed breeching and connector insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Calcium Silicate:  4 inches (100 mm) thick.

2. High-Temperature Mineral-Fiber Blanket:  3 inches (75 mm) thick and 3-lb/cu. ft. (48-kg/cu. m) nominal density.

3. High-Temperature Mineral-Fiber Board:  3 inches (75 mm) thick and [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

B. Round, concealed breeching and connector insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Calcium Silicate:  4 inches (100 mm) thick.

2. High-Temperature Mineral-Fiber Blanket:  3 inches (75 mm) thick and 3-lb/cu. ft. (48-kg/cu. m) nominal density.

3. High-Temperature Mineral-Fiber Board:  3 inches (75 mm) thick and [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

C. Rectangular, exposed breeching and connector insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Calcium Silicate:  4 inches (100 mm) thick.

2. High-Temperature Mineral-Fiber Blanket:  3 inches (75 mm) thick and 3-lb/cu. ft. (48-kg/cu. m) nominal density.

3. High-Temperature Mineral-Fiber Board:  3 inches (75 mm) thick and [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

D. Rectangular, concealed breeching and connector insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Calcium Silicate:  4 inches (100 mm) thick.

2. High-Temperature Mineral-Fiber Blanket:  3 inches (75 mm) thick and 3-lb/cu. ft. (48-kg/cu. m) nominal density.

3. High-Temperature Mineral-Fiber Board:  3 inches (75 mm) thick and [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3.19 EQUIPMENT INSULATION SCHEDULE

Equipment insulation schedules in this article specify commonly used insulation materials and thicknesses for each equipment type.  LEED-NC Prerequisite EA 2 requires that water heater insulation R-value comply with ASHRAE/IESNA 90.1-2004.  Not all materials and thicknesses may be suitable for a specific project.  Revise to suit Project after considering all parameters that impact selection.  See Evaluations for more information and guidance.

Because cellular glass is brittle, the minimum thickness recommended is 1-1/2 inches (38 mm).  Potential for breakage increases if thinner insulation is used.

Polyisocyanurate thickness is limited to 1-1/2 inches (38 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

Flexible elastomeric and polyolefin thicknesses are limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

Consider the exposure of installed insulation to damage.  Concealed applications have less risk than exposed.

Retain "one of" option in paragraphs in this article to allow Contractor to select piping materials from those retained.

A. Insulation materials and thicknesses are identified below.  If more than one material is listed for a type of equipment, selection from materials listed is Contractor's option.

B. Insulate indoor and outdoor equipment in paragraphs below that is not factory insulated.

C. Heat-exchanger (water-to-water for domestic water heating service) insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Calcium Silicate:  [3 inches (75 mm)] <Insert thickness> thick.

2. Cellular Glass:  [3 inches (75 mm)] <Insert thickness> thick.

3. Mineral-Fiber Board:  [2 inches (50 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank:  [2 inches (50 mm)] <Insert thickness> thick.

D. Steam-to-hot-water converter insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Calcium Silicate:  [3 inches (75 mm)] <Insert thickness> thick.

2. Cellular Glass:  [3 inches (75 mm)] <Insert thickness> thick.

3. Mineral-Fiber Board:  [2 inches (50 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank:  [2 inches (50 mm)] <Insert thickness> thick.

E. Domestic water pump insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

2. Mineral-Fiber Board:  [1 inch (25 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

4. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

F. Domestic chilled-water (potable) pump insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Cellular Glass:  [3 inches (75 mm)] <Insert thickness> thick.

2. Mineral-Fiber Board:  [2 inches (50 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

4. Polyisocyanurate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

G. Domestic hot-water pump insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

1. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

2. Mineral-Fiber Board:  [1 inch (25 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

4. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

H. Domestic water, domestic chilled-water (potable), and domestic hot-water hydropneumatic tank insulation shall be[ one of] the following:

Retain one or more of seven subparagraphs below.

1. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

2. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

3. Mineral-Fiber Board:  [1 inch (25 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank:  [1 inch (25 mm)] <Insert thickness> thick.

5. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

6. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

7. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

ASHRAE/IESNA 90.1 requires an R-value of 12.5 for domestic hot-water storage tanks.

I. Domestic hot-water storage tank insulation shall be[ one of] the following, of thickness to provide an R-value of [12.5] <Insert value>:

1. Cellular glass.

2. Mineral-Fiber Board:  [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Mineral-fiber pipe and tank.

4. Phenolic.

Retain first paragraph below if required to control condensation.

J. Domestic water storage tank insulation shall be[ one of] the following:

Retain one or more of seven subparagraphs below.

1. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

2. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

3. Mineral-Fiber Board:  [1 inch (25 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank:  [1 inch (25 mm)] <Insert thickness> thick.

5. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

6. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

7. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

K. Domestic chilled-water (potable) storage tank insulation shall be[ one of] the following:

Retain one or more of seven subparagraphs below.

1. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

2. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

3. Mineral-Fiber Board:  [1 inch (25 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

4. Mineral-Fiber Pipe and Tank:  [1 inch (25 mm)] <Insert thickness> thick.

5. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

6. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

7. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

L. Piping system filter-housing insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

1. Cellular Glass:  [3 inches (75 mm)] <Insert thickness> thick.

2. Mineral-Fiber Board:  [2 inches (50 mm)] <Insert thickness> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

3. Mineral-Fiber Pipe and Tank:  [2 inches (50 mm)] <Insert thickness> thick.

3.20 PIPING INSULATION SCHEDULE, GENERAL

A. Acceptable preformed pipe and tubular insulation materials and thicknesses are identified for each piping system and pipe size range.  If more than one material is listed for a piping system, selection from materials listed is Contractor's option.

B. Items Not Insulated:  Unless otherwise indicated, do not install insulation on the following:

1. Drainage piping located in crawl spaces.

2. Underground piping.

3. Chrome-plated pipes and fittings unless there is a potential for personnel injury.

Piping insulation schedules in first three articles below specify commonly used insulation materials and thicknesses by pipe size range for each service.  LEED-NC Prerequisite EA 2 requires that pipe insulation thickness comply with ASHRAE/IESNA 90.1-2004 table titled "Minimum Pipe Insulation Thickness."  Not all materials and thicknesses may be suitable for a specific project.  Revise to suit Project after considering all parameters that impact selection.  Do not duplicate requirements inserted in Part 2.  See Evaluations for more information and guidance.

Because cellular glass is brittle, the minimum thickness recommended is 1-1/2 inches (38 mm).  Potential for breakage increases if thinner insulation is used.

Polyisocyanurate thickness is limited to 1-1/2 inches (38 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

Tubular flexible elastomeric is not available in sizes larger than NPS 6 (DN 150).  Larger pipe sizes require sheets to be cut to size.  Thickness is limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

Tubular polyolefin is not available in sizes larger than NPS 4 (DN 100).  Larger pipe sizes require sheets to be cut to size.  Thickness is limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

3.21 INDOOR PIPING INSULATION SCHEDULE

Retain "one of" option in subparagraphs in this article to allow Contractor to select piping materials from those retained.

Evaluate the need to insulate domestic water for condensation and sound control.

A. Domestic Cold Water:

1. [NPS 1 (DN 25)] <Insert pipe size> and Smaller:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

2. [NPS 1-1/4 (DN 32)] <Insert pipe size> and Larger:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

B. Domestic Hot and Recirculated Hot Water:

1. [NPS 1-1/4 (DN 32)] <Insert pipe size> and Smaller:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

2. [NPS 1-1/2 (DN 40)] <Insert pipe size> and Larger:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

C. Domestic Chilled Water (Potable):

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

D. Stormwater and Overflow:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

E. Roof Drain and Overflow Drain Bodies:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [1 inch (25 mm)] <Insert thickness> thick.

Retain first paragraph below for personnel protection.

F. Exposed Sanitary Drains, Domestic Water, Domestic Hot Water, and Stops for Plumbing Fixtures for People with Disabilities:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

a. Flexible Elastomeric:  [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

b. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

c. Polyolefin:  [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

G. Sanitary Waste Piping Where Heat Tracing Is Installed:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

a. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

b. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

c. Phenolic:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

d. Polyisocyanurate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

H. Condensate and Equipment Drain Water below 60 Deg F (16 Deg C):

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

I. Floor Drains, Traps, and Sanitary Drain Piping within [10 Feet (3 m)] <Insert distance> of Drain Receiving Condensate and Equipment Drain Water below 60 Deg F (16 Deg C):

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

d. Phenolic:  [1 inch (25 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [1 inch (25 mm)] <Insert thickness> thick.

f. Polyolefin:  [3/4 inch (19 mm)] [1 inch (25 mm)] <Insert thickness> thick.

J. Hot Service Drains:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

a. Calcium Silicate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe, Type I or II:  [1 inch (25 mm)] <Insert thickness> thick.

K. Hot Service Vents:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

a. Calcium Silicate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe, Type I or II:  [1 inch (25 mm)] <Insert thickness> thick.

3.22 OUTDOOR, ABOVEGROUND PIPING INSULATION SCHEDULE

In addition to other criteria, insulate outdoor piping for freeze protection.

Retain "one of" option in subparagraphs in this article to allow Contractor to select piping materials from those retained.

A. Domestic Water Piping:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of seven subparagraphs below.

a. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [2 inches (50 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [2 inches (50 mm)] <Insert thickness> thick.

d. Phenolic:  [2 inches (50 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [2 inches (50 mm)] <Insert thickness> thick.

f. Polyolefin:  [2 inches (50 mm)] <Insert thickness> thick.

g. Polystyrene:  [2 inches (50 mm)] <Insert thickness> thick.

B. Domestic Hot and Recirculated Hot Water:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of six subparagraphs below.

a. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

b. Flexible Elastomeric:  [2 inches (50 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [2 inches (50 mm)] <Insert thickness> thick.

d. Phenolic:  [2 inches (50 mm)] <Insert thickness> thick.

e. Polyisocyanurate:  [2 inches (50 mm)] <Insert thickness> thick.

f. Polyolefin:  [2 inches (50 mm)] <Insert thickness> thick.

C. Sanitary Waste Piping Where Heat Tracing Is Installed:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of four subparagraphs below.

a. Cellular Glass:  [2 inches (50 mm)] <Insert thickness> thick.

b. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [2 inches (50 mm)] <Insert thickness> thick.

c. Phenolic:  [2 inches (50 mm)] <Insert thickness> thick.

d. Polyisocyanurate:  [2 inches (50 mm)] <Insert thickness> thick.

D. Hot Service Drains:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

a. Calcium Silicate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type I:  [1 inch (25 mm)] <Insert thickness> thick.

E. Hot Service Vents:

1. All Pipe Sizes:  Insulation shall be[ one of] the following:

Retain one or more of three subparagraphs below.

a. Calcium Silicate:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

b. Cellular Glass:  [1-1/2 inches (38 mm)] <Insert thickness> thick.

c. Mineral-Fiber, Preformed Pipe Insulation, Type II:  [1 inch (25 mm)] <Insert thickness> thick.

3.23 OUTDOOR, UNDERGROUND PIPING INSULATION SCHEDULE

Insulation specified in this article is limited to those insulation types that have high compressive strength.  Other insulation types may be considered acceptable and should be evaluated on a project basis.  Cellular glass is best suited for applications below 250 deg F (121 deg C) because of its moisture-resistant properties.

A. Loose-fill insulation, for belowground piping, is specified in Division 2 piping distribution Sections.

B. Sanitary Waste Piping, All Sizes, Where Heat Tracing Is Installed:  Cellular glass, [2 inches (50 mm)] <Insert thickness> thick.

C. Chilled Water, All Sizes:  Cellular glass, [2 inches (50 mm)] <Insert thickness> thick.

3.24 INDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless.  This article specifies locations in two broad categories:  concealed and exposed.  Revise if additional delineation is necessary.

A. Install jacket over insulation material.  For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

B. If more than one material is listed, selection from materials listed is Contractor's option.

C. Equipment, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

D. Equipment, Exposed, up to 48 Inches (1200 mm) in Diameter or with Flat Surfaces up to 72 Inches (1800 mm):

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

E. Equipment, Exposed, Larger Than 48 Inches (1200 mm) in Diameter or with Flat Surfaces Larger Than 72 Inches (1800 mm):

Retain one of four subparagraphs below.

1. None.

2. [Painted ]Aluminum, [Smooth] [Stucco Embossed] with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]:  [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

3. Stainless Steel, Type [304] [316] [304 or 316], [Smooth] [Stucco Embossed], with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]:  [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

4. <Insert jacket type.>

F. Piping, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

G. Piping, Exposed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

3.25 OUTDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless.  This article specifies locations in two broad categories:  concealed and exposed.  Revise if additional delineation is necessary.

30-mil (0.8-mm) or heavier PVC is recommended for outdoor applications.  40-mil (1.0-mm) PVC does not meet a flame-spread index of 25 and a smoke-developed index of 50; however, a flame-spread or smoke-developed index is not a requirement for outdoor applications.

0.024-inch (0.61-mm) or heavier aluminum is recommended for outdoor applications.

Painted aluminum increases surface emissivity and provides added chemical resistance.  See Evaluations for discussion of emissivity.

0.016-inch (0.41-mm) or heavier stainless steel is recommended for outdoor applications.

Z-shaped locking seam is recommended for metal jackets located in unprotected applications that are exposed to severe weather.

A. Install jacket over insulation material.  For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

B. If more than one material is listed, selection from materials listed is Contractor's option.

C. Equipment, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

D. Equipment, Exposed, up to 48 Inches (1200 mm) in Diameter or with Flat Surfaces up to 72 Inches (1800 mm):

Retain one of three subparagraphs below.

1. [Painted ]Aluminum, [Smooth] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

2. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

3. <Insert jacket type.>

E. Equipment, Exposed, Larger Than 48 Inches (1200 mm) in Diameter or with Flat Surfaces Larger Than 72 Inches (1800 mm):

Retain one of three subparagraphs below.

1. [Painted ]Aluminum, [Smooth] [Stucco Embossed] with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]:  [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

2. Stainless Steel, Type [304] [316] [304 or 316], [Smooth] [Stucco Embossed], with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]:  [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

3. <Insert jacket type.>

F. Piping, Concealed:

Retain one of six subparagraphs below.

1. None.

2. [PVC] [PVC, Color-Coded by System]:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

3. Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

4. Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

5. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

6. <Insert jacket type.>

G. Piping, Exposed:

Retain one of four subparagraphs below.

1. PVC:  [20 mils (0.5 mm)] [30 mils (0.8 mm)] [40 mils (1.0 mm)] thick.

2. [Painted ]Aluminum, [Smooth] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]:  [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

3. Stainless Steel, Type [304] [316] [304 or 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed] [with Z-Shaped Locking Seam]:  [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

4. <Insert jacket type.>

3.26 UNDERGROUND, FIELD-INSTALLED INSULATION JACKET

A. For underground direct-buried piping applications, install underground direct-buried jacket over insulation material.

END OF SECTION 15082

PLUMBING INSULATION
15082 - 1

