Copyright 2005 AIA
MASTERSPEC
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15127 - METERS AND GAGES FOR HVAC PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Thermometers.

2. Gages.

3. Test plugs.

4. Flowmeters.

5. Thermal-energy meters.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 15 Section "Steam and Condensate Piping" for steam and condensate meters.

2. Division 15 Section "Facility Natural-Gas Piping" for gas meters.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. CR:  Chlorosulfonated polyethylene synthetic rubber.

B. EPDM:  Ethylene-propylene-diene terpolymer rubber.

1.4 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated; include performance curves.

B. Shop Drawings:  Schedule for [thermometers] [gages] [flowmeters] [and] [thermal-energy meters] indicating manufacturer's number, scale range, and location for each.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below for material or product certificates from manufacturers.

C. Product Certificates:  For each type of [thermometer] [gage] [flowmeter] [and] [thermal-energy meter], signed by product manufacturer.

D. Operation and Maintenance Data:  For [flowmeters] [and] [thermal-energy meters] to include in emergency, operation, and maintenance manuals.

PART 2 -  PRODUCTS

2.1 METAL-CASE, LIQUID-IN-GLASS THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Palmer - Wahl Instruments Inc.

2. Trerice, H. O. Co.

3. Weiss Instruments, Inc.

4. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

5. <Insert manufacturer's name.>

C. Case:  [Die-cast aluminum] [Die-cast aluminum or brass] [Brass] [Chrome-plated brass], [7 inches (178 mm)] [9 inches (229 mm)] <Insert other> long.

D. Tube:  Red or blue reading, [mercury] [mercury or organic-liquid] [organic-liquid] filled, with magnifying lens.

E. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

G. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

H. Stem:  Copper-plated steel, aluminum, or brass for thermowell installation and of length to suit installation.

I. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.2 PLASTIC-CASE, LIQUID-IN-GLASS THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ernst Gage Co.

2. Eugene Ernst Products Co.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Trerice, H. O. Co.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. Winters Instruments.

8. <Insert manufacturer's name.>

C. Case:  Plastic, [7 inches (178 mm)] [9 inches (229 mm)] <Insert other> long.

D. Tube:  Red or blue reading, mercury or organic-liquid filled, with magnifying lens.

E. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Window:  Glass or plastic.

G. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

H. Stem:  Metal, for thermowell installation and of length to suit installation.

I. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.3 DUCT-TYPE, LIQUID-IN-GLASS THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Miljoco Corp.

2. Palmer - Wahl Instruments Inc.

3. Trerice, H. O. Co.

4. Weiss Instruments, Inc.

5. <Insert manufacturer's name.>

C. Case:  [Die-cast aluminum] [Metal or plastic], [7 inches (178 mm)] <Insert other> long.

D. Tube:  Red or blue reading, mercury or organic filled, with magnifying lens.

E. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Window:  [Glass or plastic] <Insert other>.

G. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, angle type].

H. Stem:  Metal, for installation in mounting bracket and of length to suit installation.

I. Mounting Bracket:  Flanged fitting for attachment to duct and made to hold thermometer stem.

J. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.4 DIRECT-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

2. KOBOLD Instruments, Inc.

3. Marsh Bellofram.

4. Trerice, H. O. Co.

5. Weiss Instruments, Inc.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. <Insert manufacturer's name.>

C. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [4-1/2-inch (114-mm)] [5-inch (127-mm)] [6-inch (152-mm)] <Insert other> diameter.

D. Element:  Bourdon tube or other type of pressure element.

E. Movement:  Mechanical, connecting element and pointer.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

J. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, bottom type] [Rigid, back type].

K. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.5 REMOTE-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Palmer - Wahl Instruments Inc.

6. REO TEMP Instrument Corporation.

7. Tel-Tru Manufacturing Company.

8. Trerice, H. O. Co.

9. Weiss Instruments, Inc.

10. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

11. Winters Instruments.

12. <Insert manufacturer's name.>

C. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

D. Element:  Bourdon tube or other type of pressure element.

E. Movement:  Mechanical, connecting element and pointer.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  [Metal] [Brass] [Stainless steel].

J. Connector:  [Bottom] [Back] union type.

K. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.6 BIMETALLIC-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

2. Ernst Gage Co.

3. Eugene Ernst Products Co.

4. Marsh Bellofram.

5. Miljoco Corp.

6. NANMAC Corporation.

7. Noshok, Inc.

8. Palmer - Wahl Instruments Inc.

9. REO TEMP Instrument Corporation.

10. Tel-Tru Manufacturing Company.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

C. Description:  Direct-mounting, bimetallic-actuated dial thermometers complying with ASME B40.3.

D. Case:  [Dry] [Liquid-filled] type, stainless steel with [3-inch (76-mm)] [5-inch (127-mm)] diameter.

E. Element:  Bimetal coil.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  Stainless steel.

J. Connector:  [Adjustable angle] [Rigid, back] [Rigid, bottom] <Insert other> type.

K. Stem:  Metal, for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.7 THERMOWELLS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Marsh Bellofram.

5. Miljoco Corp.

6. NANMAC Corporation.

7. Noshok, Inc.

8. Palmer - Wahl Instruments Inc.

9. REO TEMP Instrument Corporation.

10. Tel-Tru Manufacturing Company.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

Retain one of two paragraphs and list above or first paragraph below.

C. Manufacturers:  Same as manufacturer of thermometer being used.

D. Description:  Pressure-tight, socket-type metal fitting made for insertion into piping and of type, diameter, and length required to hold thermometer.

2.8 PRESSURE GAGES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Eugene Ernst Products Co.

5. KOBOLD Instruments, Inc.

6. Marsh Bellofram.

7. Miljoco Corp.

8. Noshok, Inc.

9. Palmer - Wahl Instruments Inc.

10. REO TEMP Instrument Corporation.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

C. Direct-Mounting, Dial-Type Pressure Gages:  Indicating-dial type complying with ASME B40.100.

1. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, NPS 1/4 (DN 8), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  30-in. Hg of vacuum to 15 psig of pressure (100 kPa of vacuum to 103 kPa of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

D. Remote-Mounting, Dial-Type Pressure Gages:  ASME B40.100, indicating-dial type.

1. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, NPS 1/4 (DN 8), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  30-in. Hg of vacuum to 15 psig of pressure (100 kPa of vacuum to 103 kPa of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

E. Pressure-Gage Fittings:

1. Valves:  NPS 1/4 (DN 8) brass or stainless-steel needle type.

2. Syphons:  NPS 1/4 (DN 8) coil of brass tubing with threaded ends.

3. Snubbers:  ASME B40.5, NPS 1/4 (DN 8) brass bushing with corrosion-resistant, porous-metal disc of material suitable for system fluid and working pressure.

2.9 TEST PLUGS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Flow Design, Inc.

2. MG Piping Products Co.

3. National Meter, Inc.

4. Peterson Equipment Co., Inc.

5. Sisco Manufacturing Co.

6. Trerice, H. O. Co.

7. Watts Industries, Inc.; Water Products Div.

8. <Insert manufacturer's name.>

C. Description:  Corrosion-resistant brass or stainless-steel body with core inserts and gasketed and threaded cap, with extended stem for units to be installed in insulated piping.

D. Minimum Pressure and Temperature Rating:  [500 psig at 200 deg F (3450 kPa at 93 deg C)] <Insert other>.

E. Core Inserts:  One or two self-sealing rubber valves.

1. Insert material for air, water, oil, or gas service at 20 to 200 deg F (minus 7 to plus 93 deg C) shall be CR.

2. Insert material for air or water service at minus 30 to plus 275 deg F (minus 35 to plus 136 deg C) shall be EPDM.

Retain paragraph below if required.

F. Test Kit:  Furnish [one] <Insert other> test kit(s) containing one pressure gage and adaptor, [one] [two] thermometer(s), and carrying case.  Pressure gage, adapter probes, and thermometer sensing elements shall be of diameter to fit test plugs and of length to project into piping.

1. Pressure Gage:  Small bourdon-tube insertion type with [2- to 3-inch- (51- to 76-mm-)] <Insert other> diameter dial and probe.  Dial range shall be [0 to 200 psig (0 to 1380 kPa)] <Insert other>.

Retain one of first two subparagraphs below.  If both are required, indicate location of each on Drawings.

2. Low-Range Thermometer:  Small bimetallic insertion type with [1- to 2-inch- (25- to 51-mm-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [25 to 125 deg F (minus 4 to plus 52 deg C)] <Insert other>.

3. High-Range Thermometer:  Small bimetallic insertion type with [1- to 2-inch- (25- to 51-mm-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [0 to 220 deg F (minus 18 to plus 104 deg C)] <Insert other>.

4. Carrying case shall have formed instrument padding.

2.10 WAFER-ORIFICE FLOWMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. ABB, Inc.; ABB Instrumentation.

2. Armstrong Pumps, Inc.

3. Badger Meter, Inc.; Industrial Div.

4. Bell & Gossett; ITT Industries.

5. Meriam Instruments Div.; Scott Fetzer Co.

6. <Insert manufacturer's name.>

C. Description:  Differential-pressure-design orifice insert for installation between pipe flanges; with calibrated flow-measuring element, separate flowmeter, hoses or tubing, valves, fittings, and conversion chart compatible with flow-measuring element, flowmeter, and system fluid.

D. Construction:  Cast-iron body, brass valves with integral check valves and caps, and calibrated nameplate.

E. Pressure Rating:  [300 psig (2070 kPa)] <Insert other>.

F. Temperature Rating:  [250 deg F (121 deg C)] <Insert other>.

G. Range:  Flow range of flow-measuring element and flowmeter shall cover operating range of equipment or system served.

Retain one of first two paragraphs below.

H. Permanent Indicators:  Suitable for wall or bracket mounting, calibrated for connected flowmeter element, and having 6-inch- (150-mm-) diameter, or equivalent, dial with fittings and copper tubing for connecting to flowmeter element.

1. Scale:  Gallons per minute (Liters per second).

2. Accuracy:  Plus or minus 1 percent between 20 and 80 percent of range.

I. Portable Indicators:  Differential-pressure type calibrated for connected flowmeter element and having two 12-foot (3.7-m) hoses in carrying case.

1. Scale:  Gallons per minute (Liters per second).

2. Accuracy:  Plus or minus 2 percent between 20 and 80 percent of range.

J. Operating Instructions:  Include complete instructions with each flowmeter.

2.11 VENTURI FLOWMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Armstrong Pumps, Inc.

2. Badger Meter, Inc.; Industrial Div.

3. Bailey-Fischer & Porter Co.

4. Flow Design, Inc.

5. Gerand Engineering Co.

6. Hyspan Precision Products, Inc.

7. Leeds & Northrup.

8. McCrometer, Inc.

9. Preso Meters Corporation.

10. Victaulic Co. of America.

11. <Insert manufacturer's name.>

C. Description:  Differential-pressure design for installation in piping; with calibrated flow-measuring element, separate flowmeter, hoses or tubing, valves, fittings, and conversion chart compatible with flow-measuring element, flowmeter, and system fluid.

D. Construction:  Bronze, brass, or factory-primed steel; with brass fittings and attached tag with flow conversion data.

E. Pressure Rating:  [250 psig (1725 kPa)] <Insert other>.

F. Temperature Rating:  [250 deg F (121 deg C)] <Insert other>.

G. End Connections for NPS 2 (DN 50) and Smaller:  Threaded.

H. End Connections for NPS 2-1/2 (DN 65) and Larger:  Flanged or welded.

I. Range:  Flow range of flow-measuring element and flowmeter shall cover operating range of equipment or system served.

Retain one of first two paragraphs below.

J. Permanent Indicators:  Suitable for wall or bracket mounting, calibrated for connected flowmeter element, and having 6-inch- (150-mm-) diameter, or equivalent, dial with fittings and copper tubing for connecting to flowmeter element.

1. Scale:  Gallons per minute (Liters per second).

2. Accuracy:  Plus or minus 1 percent between 20 and 80 percent of range.

K. Portable Indicators:  Differential-pressure type calibrated for connected flowmeter element and having two 12-foot (3.7-m) hoses in carrying case.

1. Scale:  Gallons per minute (Liters per second).

2. Accuracy:  Plus or minus 2 percent between 20 and 80 percent of range.

L. Operating Instructions:  Include complete instructions with each flowmeter.

2.12 TURBINE FLOWMETERS

Turbine flowmeters can be used with a transmitter to send signals to a remote meter terminal.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Badger Meter, Inc.; Industrial Div.

2. Bailey-Fischer & Porter Co.

3. Data Industrial Corp.

4. Engineering Measurements Company.

5. ERDCO Engineering Corp.

6. Fischer, George Inc.

7. Hoffer Flow Controls, Inc.

8. ISTEC Corporation.

9. Midwest Instruments & Controls Corp.

10. ONICON Incorporated.

11. SeaMetrics Inc.

12. Sponsler Company, Inc.

13. Thermo Measurement Ltd.

14. Venture Measurement.

15. <Insert manufacturer's name.>

C. Description:  Insertion type for inserting turbine into piping and measuring flow directly in gallons per minute (liters per second).

D. Construction:  Bronze or stainless-steel body; with plastic turbine or impeller and integral direct-reading scale.

E. Pressure Rating:  [150 psig (1035 kPa)] <Insert other> minimum.

F. Temperature Rating:  [180 deg F (82 deg C)] <Insert other> minimum.

G. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in gallons (liters)].

H. Accuracy:  Plus or minus 2-1/2 percent.

2.13 VORTEX-SHEDDING FLOWMETERS

Vortex-shedding flowmeters can be used with a transmitter to send signals to a remote meter terminal.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bailey-Fischer & Porter Co.

2. Engineering Measurements Company.

3. ISTEC Corporation.

4. MCO/Eastech, Inc.

5. Schlumberger Limited; Measurement Div.

6. Venture Measurement.

7. <Insert manufacturer's name.>

C. Description:  Inline type for installing between pipe flanges and measuring flow directly in gallons per minute (liters per second).

D. Construction:  Stainless-steel body; with integral transmitter and direct-reading scale.

E. Pressure Rating:  [1000 psig (6900 kPa)] <Insert other> minimum.

F. Temperature Rating:  [500 deg F (260 deg C)] <Insert other> minimum.

G. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in gallons (liters)].

H. Integral Transformer:  For low-voltage power operation.

I. Accuracy:  Plus or minus 7/10 percent for liquids and 1-1/4 percent for gases.

2.14 PITOT-TUBE FLOWMETERS

Pitot-tube flowmeters can be used with a transmitter to send signals to a remote meter terminal.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Dieterich Standard Inc.

2. Meriam Instruments Div.; Scott Fetzer Co.

3. Preso Meters Corporation.

4. Taco, Inc.

5. Veris Industries.

6. <Insert manufacturer's name.>

C. Description:  Insertion-type, differential-pressure design for inserting probe into piping and measuring flow directly in gallons per minute (liters per second).

D. Construction:  Stainless-steel probe of length to span inside of pipe; with integral transmitter and direct-reading scale.

E. Pressure Rating:  [150 psig (1035 kPa)] <Insert other> minimum.

F. Temperature Rating:  [250 deg F (121 deg C)] <Insert other> minimum.

G. Display:  Visual instantaneous rate of flow[, with register to indicate total volume in gallons (liters)].

H. Integral Transformer:  For low-voltage power connection.

I. Accuracy:  Plus or minus 1 percent for liquids and gases.

2.15 FLOW INDICATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Brooks Instrument Div.; Emerson Electric Co.

2. Dwyer Instruments, Inc.

3. Ernst Gage Co.

4. Eugene Ernst Products Co.

5. McCrometer, Inc.

6. OPW Engineered Systems; Dover Corp.

7. Penberthy, Inc.

8. <Insert manufacturer's name.>

C. Description:  Instrument for installation in piping systems for visual verification of flow.

D. Construction:  Bronze or stainless-steel body; with sight glass and [plastic pelton-wheel] <Insert other> indicator, and threaded or flanged ends.

E. Pressure Rating:  [125 psig (860 kPa)] <Insert other>.

F. Temperature Rating:  [200 deg F (93 deg C)] <Insert other>.

G. End Connections for NPS 2 (DN 50) and Smaller:  Threaded.

H. End Connections for NPS 2-1/2 (DN 65) and Larger:  Flanged.

2.16 INSERTION-TURBINE, THERMAL-ENERGY METER SYSTEMS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Data Industrial Corp.

2. ONICON Incorporated.

3. Thermo Measurement Ltd.

4. <Insert manufacturer's name.>

C. Description:  Flow sensor,[ strainer,] two temperature sensors, transmitter, meter, and connecting wiring.

D. Flow Sensor:  Insertion-type turbine or paddle-wheel element with corrosion-resistant-metal body and transmitter.

1. Pressure Rating:  [125 psig (860 kPa)] <Insert other>.

2. Temperature Range:  [40 to 250 deg F (5 to 121 deg C)] <Insert other>.

E. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or British thermal units (joules).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

F. Strainer:  Full size of main line piping.

2.17 INLINE-TURBINE, THERMAL-ENERGY METER SYSTEMS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Engineering Measurements Company.

2. Hoffer Flow Controls, Inc.

3. ISTEC Corporation.

4. Thermo Measurement Ltd.

5. Venture Measurement.

6. <Insert manufacturer's name.>

C. Description:  Flow sensor,[ strainer,] two temperature sensors, transmitter, meter, and connecting wiring.

D. Flow Sensor:  Turbine-type water meter with corrosion-resistant-metal body and transmitter.

1. Pressure Rating:  [150-psig (1035-kPa)] <Insert other> minimum working-pressure rating.

2. Temperature Range:  [40 to 250 deg F (5 to 121 deg C)] <Insert other>.

E. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or British thermal units (joules).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

F. Strainer:  Full size of main line piping.

2.18 ULTRASONIC, THERMAL-ENERGY METER SYSTEMS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Controlotron Corporation.

2. Engineering Measurements Company.

3. Mesa Laboratories, Inc.; Nusonics Div.

4. <Insert manufacturer's name.>

C. Description:  Flow sensor, two temperature sensors, transmitter, meter, and connecting wiring.

D. Flow Sensor:  Strap-on or integral ultrasonic type with transmitter.

E. Meter:  Solid-state integrating type[ with integral battery pack].

1. Data Output:  Six-digit electromechanical counter with readout in kilowatts per hour or British thermal units (joules).

2. Accuracy:  Plus or minus [1] <Insert other> percent.

3. Battery Pack:  Five-year lithium battery.

F. Strainer:  Full size of main line piping.

PART 3 -  EXECUTION

3.1 THERMOMETER APPLICATIONS

A. Install liquid-in-glass thermometers in the following locations:

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each hydronic boiler and chiller.

3. Inlet and outlet of each hydronic coil in air-handling units and built-up central systems.

4. Inlet and outlet of each hydronic heat exchanger.

5. Inlet and outlet of each hydronic heat-recovery unit.

6. Inlet and outlet of each thermal storage tank.

7. Outside-air, return-air, and mixed-air ducts.

B. Install direct-mounting, vapor-actuated dial thermometers in the following locations:

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each hydronic boiler and chiller.

3. Inlet and outlet of each hydronic coil in air-handling units and built-up central systems.

4. Inlet and outlet of each hydronic heat exchanger.

5. Inlet and outlet of each hydronic heat-recovery unit.

6. Inlet and outlet of each thermal storage tank.

C. Install remote-mounting, vapor-actuated dial thermometers in the following locations:

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each hydronic boiler and chiller.

3. Inlet and outlet of each hydronic coil in air-handling units and built-up central systems.

4. Inlet and outlet of each hydronic heat exchanger.

5. Inlet and outlet of each hydronic heat-recovery unit.

6. Inlet and outlet of each thermal storage tank.

D. Install bimetallic-actuated dial thermometers in the following locations:

1. Inlet and outlet of each hydronic zone.

2. Inlet and outlet of each hydronic boiler and chiller.

3. Inlet and outlet of each hydronic coil in air-handling units and built-up central systems.

4. Inlet and outlet of each hydronic heat exchanger.

5. Inlet and outlet of each hydronic heat-recovery unit.

6. Inlet and outlet of each thermal storage tank.

E. Install [dry] [liquid-filled]-case-type, [vapor] [bimetallic]-actuated dial thermometers at suction and discharge of each pump.

F. Provide the following temperature ranges for thermometers:

Other temperature ranges and units with both Fahrenheit and Celsius scales are available.

1. Heating Hot Water:  [30 to 240 deg F, with 2-degree scale divisions (Minus 1 to plus 115 deg C, with 1-degree scale divisions)] [50 to 400 deg F, with 5-degree scale divisions (10 to 205 deg C, with 2-degree scale divisions)] <Insert other>.

2. Condenser Water:  [0 to 160 deg F, with 2-degree scale divisions (Minus 18 to plus 71 deg C, with 1-degree scale divisions)] [30 to 240 deg F, with 2-degree scale divisions (Minus 1 to plus 115 deg C, with 1-degree scale divisions)] <Insert other>.

3. Chilled Water:  [0 to 100 deg F, with 2-degree scale divisions (Minus 18 to plus 38 deg C, with 1-degree scale divisions)] [0 to 160 deg F, with 2-degree scale divisions (Minus 18 to plus 71 deg C, with 1-degree scale divisions)] <Insert other>.

4. Steam and Condensate:  [30 to 300 deg F, with 5-degree scale divisions (Minus 1 to plus 150 deg C, with 2-degree scale divisions)] [50 to 400 deg F, with 5-degree scale divisions (10 to 205 deg C, with 3-degree scale divisions)] <Insert other>.

5. Air Ducts:  [Minus 40 to plus 110 deg F, with 2-degree scale divisions (Minus 40 to plus 43 deg C, with 2-degree scale divisions)] [30 to 240 deg F, with 2-degree scale divisions (Minus 1 to plus 115 deg C, with 1-degree scale divisions)] [50 to 400 deg F, with 5-degree scale divisions (10 to 205 deg C, with 3-degree scale divisions)] <Insert other>.

3.2 GAGE APPLICATIONS

A. Install dry-case-type pressure gages for discharge of each pressure-reducing valve.

B. Install [dry] [liquid-filled]-case-type pressure gages at chilled- and condenser-water inlets and outlets of chillers.

C. Install [dry] [liquid-filled]-case-type pressure gages at suction and discharge of each pump.

3.3 INSTALLATIONS

A. Install direct-mounting thermometers and adjust vertical and tilted positions.

B. Install remote-mounting dial thermometers on panel, with tubing connecting panel and thermometer bulb supported to prevent kinks.  Use minimum tubing length.

C. Install thermowells with socket extending [a minimum of 2 inches (51 mm) into fluid] [one-third of diameter of pipe] [to center of pipe] and in vertical position in piping tees where thermometers are indicated.

D. Duct Thermometer Support Flanges:  Install in wall of duct where duct thermometers are indicated.  Attach to duct with screws.

E. Install direct-mounting pressure gages in piping tees with pressure gage located on pipe at most readable position.

F. Install remote-mounting pressure gages on panel.

G. Install needle-valve and snubber fitting in piping for each pressure gage for fluids (except steam).

H. Install needle-valve and syphon fitting in piping for each pressure gage for steam.

I. Install test plugs in tees in piping.

J. Install flow indicators, in accessible positions for easy viewing, in piping systems.

K. Assemble and install connections, tubing, and accessories between flow-measuring elements and flowmeters as prescribed by manufacturer's written instructions.

L. Install flowmeter elements in accessible positions in piping systems.

M. Install differential-pressure-type flowmeter elements with at least minimum straight lengths of pipe upstream and downstream from element as prescribed by manufacturer's written instructions.

N. Install wafer-orifice flowmeter elements between pipe flanges.

O. Install permanent indicators on walls or brackets in accessible and readable positions.

P. Install connection fittings for attachment to portable indicators in accessible locations.

Q. Install flowmeters at discharge of hydronic system pumps and at inlet of hydronic air coils.

R. Assemble components and install thermal-energy meters.

S. Mount meters on wall if accessible; if not, provide brackets to support meters.

3.4 CONNECTIONS

A. Install meters and gages adjacent to machines and equipment to allow service and maintenance for meters, gages, machines, and equipment.

B. Connect flowmeter-system elements to meters.

C. Connect flowmeter transmitters to meters.

D. Connect thermal-energy-meter transmitters to meters.

3.5 ADJUSTING

A. Calibrate meters according to manufacturer's written instructions, after installation.

B. Adjust faces of meters and gages to proper angle for best visibility.

END OF SECTION 15127

METERS AND GAGES FOR HVAC PIPING
15127 - 1

