Copyright 2005 AIA
MASTERSPEC
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15155 - SANITARY WASTE PIPING SPECIALTIES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following sanitary drainage piping specialties:

Adjust list below to suit Project.

1. Backwater valves.

2. Cleanouts.

3. Floor drains.

4. Trench drains.

5. Channel drainage systems.

6. Air-admittance valves.

7. Roof flashing assemblies.

8. Through-penetration firestop assemblies.

9. Miscellaneous sanitary drainage piping specialties.

10. Flashing materials.

11. FOG disposal systems.

12. Grease interceptors.

13. Grease removal devices.

14. Oil interceptors.

15. Solids interceptors.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Storm Drainage Piping Specialties" for trench drains for storm water, channel drainage systems for storm water, roof drains, and catch basins.

2. Division 15 Section "Plumbing Fixtures" for hair interceptors.

3. Division 15 Section "Medical Plumbing Fixtures" for plaster sink interceptors.

1.3 DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. FOG:  Fats, oils, and greases.

C. FRP:  Fiberglass-reinforced plastic.

D. HDPE:  High-density polyethylene plastic.

E. PE:  Polyethylene plastic.

F. PP:  Polypropylene plastic.

G. PVC:  Polyvinyl chloride plastic.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, and accessories for the following:

1. FOG disposal systems.

2. Grease interceptors.

3. Grease removal devices.

4. Oil interceptors.

Retain paragraph below if retaining "Frost-Resistant Vent Terminals" Paragraph in Part 2 "Miscellaneous Sanitary Drainage Piping Specialties" Article.

B. Shop Drawings:  Show fabrication and installation details for frost-resistant vent terminals.

Retain subparagraph below if retaining Part 2 "FOG Disposal Systems" or "Grease Removal Devices" Article.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

C. Manufacturer Seismic Qualification Certification:  Submit certification that [FOG disposal systems,] [grease interceptors,] [grease removal devices,] [oil interceptors,] accessories, and components will withstand seismic forces defined in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For drainage piping specialties to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Drainage piping specialties shall bear label, stamp, or other markings of specified testing agency.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NSF 14, "Plastics Piping Components and Related Materials," for plastic sanitary piping specialty components.

1.6 COORDINATION

Retain first paragraph below if retaining base-mounting equipment.

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate size and location of roof penetrations.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

Retain this Article if retaining Part 2 "FOG Disposal Systems" Article.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Cultures:  Provide 1-gal. (3.8-L) bottles of bacteria culture recommended by manufacturer of FOG disposal systems equal to [200] <Insert number> percent of amount installed, but no fewer than [2] <Insert number> 1-gal. (3.8-L) bottles.

PART 2 -  PRODUCTS

2.1 BACKWATER VALVES

Copy and edit paragraph and subparagraphs below for each type of horizontal, cast-iron backwater valve required.  If only one type is required, drawing designation may be omitted.

A. Horizontal, Cast-Iron Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.14.1.

5. Size:  Same as connected piping.

6. Body:  Cast iron.

7. Cover:  Cast iron with [bolted] [or] [threaded] access check valve.

8. End Connections:  [Hub and spigot] [Hub and spigot or hubless] [Hubless].

9. Type Check Valve:  Removable, bronze, swing check, factory assembled or field modified to hang [closed] [open for airflow unless subject to backflow condition].

10. Extension:  ASTM A 74, Service class; full-size, cast-iron, soil-pipe extension to field-installed cleanout at floor; replaces backwater valve cover.

Copy and edit paragraph and subparagraphs below for each type of drain-outlet backwater valve required.  If only one type is required, drawing designation may be omitted.

B. Drain-Outlet Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company; Josam Div.

b. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

c. Watts Drainage Products Inc.

d. Zurn Plumbing Products Group; Specification Drainage Operation.

e. <Insert manufacturer's name.>

3. Size:  Same as floor drain outlet.

4. Body:  Cast iron or bronze made for vertical installation in bottom outlet of floor drain.

5. Check Valve:  Removable ball float.

6. Inlet:  Threaded.

7. Outlet:  Threaded or spigot.

Floor drains with integral backwater valves are specified as floor drains.

Copy and edit paragraph and subparagraphs below for each type of horizontal, plastic backwater valve required.  If only one type is required, drawing designation may be omitted.

Plastic backwater valves in paragraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150).  Most are made of PVC.

C. Horizontal, Plastic Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. NDS Inc.

d. Oatey.

e. Plastic Oddities; a division of Diverse Corporate Technologies.

f. Sioux Chief Manufacturing Company, Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. <Insert manufacturer's name.>

3. Size:  Same as connected piping.

4. Body:  [ABS] [PVC].

5. Cover:  Same material as body with threaded access to check valve.

6. Check Valve:  Removable swing check.

7. End Connections:  Socket type.

2.2 CLEANOUTS

Copy and edit paragraph and subparagraphs below for each type of exposed metal cleanout required.  If only one type is required, drawing designation may be omitted.

A. Exposed Metal Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for ASME A112.36.2M, cast-iron cleanouts.

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.3.1, stainless-steel cleanouts.

h. Josam Company; Blucher-Josam Div.

i. <Insert manufacturer's name.>

4. Standard:  [ASME A112.36.2M for cast iron] [ASME A112.3.1 for stainless steel] <Insert standard> for cleanout test tee.

5. Size:  Same as connected drainage piping

6. Body Material:  [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] [Stainless-steel tee with side cleanout] as required to match connected piping.

7. Closure:  [Countersunk] [Countersunk or raised-head] [Raised-head], [brass] [cast-iron] [plastic] plug.

8. Closure Plug Size:  Same as or not more than one size smaller than cleanout size.

Retain last two subparagraphs above for ASME A112.36.2M cleanouts or subparagraph below for ASME A112.3.1, stainless-steel cleanouts.

9. Closure:  Stainless-steel plug with seal.

Copy and edit paragraph and subparagraphs below for each type of metal floor cleanout required.  If only one type is required, drawing designation may be omitted.

B. Metal Floor Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists of manufacturers below.

Manufacturers in list below are for ASME A112.36.2M, cast-iron cleanouts.

a. Josam Company; Josam Div.

b. Oatey.

c. Sioux Chief Manufacturing Company, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. Zurn Plumbing Products Group; Specification Drainage Operation.

i. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.36.2M, stainless-steel cleanouts.

j. Josam Company; Josam Div.

k. Kusel Equipment Co.

l. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

m. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.3.1, stainless-steel cleanouts.

n. Josam Company; Blucher-Josam Div.

o. <Insert manufacturer's name.>

Retain 12 subparagraphs below for cast-iron or stainless-steel cleanouts complying with ASME A112.36.2M.

4. Standard:  ASME A112.36.2M for [adjustable housing] [cast-iron soil pipe with cast-iron ferrule] [heavy-duty, adjustable housing] [threaded, adjustable housing] cleanout.

5. Size:  Same as connected branch.

6. Type:  [Adjustable housing] [Cast-iron soil pipe with cast-iron ferrule] [Heavy-duty, adjustable housing] [Threaded, adjustable housing].

7. Body or Ferrule:  [Cast iron] [Stainless steel] <Insert material>.

8. Clamping Device:  [Not required] [Required].

9. Outlet Connection:  [Inside calk] [Spigot] [Threaded].

10. Closure:  [Brass plug with straight threads and gasket] [Brass plug with tapered threads] [Cast-iron plug] [Plastic plug].

11. Adjustable Housing Material:  [Cast iron] [Plastic] <Insert material> with [threads] [set-screws or other device].

12. Frame and Cover Material and Finish:  [Nickel-bronze, copper alloy] [Painted cast iron] [Polished bronze] [Rough bronze] [Stainless steel] <Insert material and finish>.

13. Frame and Cover Shape:  [Round] [Square] <Insert shape>.

14. Top Loading Classification:  [Extra Heavy] [Heavy] [Light] [Medium] Duty.

15. Riser:  ASTM A 74, [Extra-Heavy] [Service] class, cast-iron drainage pipe fitting and riser to cleanout.

Retain five subparagraphs below for stainless-steel cleanouts complying with ASME A112.3.1.

16. Standard:  ASME A112.3.1.

17. Size:  Same as connected branch.

18. Housing:  Stainless steel.

19. Closure:  Stainless steel with seal.

20. Riser:  Stainless-steel drainage pipe fitting to cleanout.

Copy and edit paragraph and subparagraphs below for each type of cast-iron wall cleanout required.  If only one type is required, drawing designation may be omitted.

C. Cast-Iron Wall Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.36.2M.  Include wall access.

5. Size:  Same as connected drainage piping.

6. Body:  [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] as required to match connected piping.

Option for drilled-and-threaded plug in first subparagraph below is for a screw for a wall cover plate.

7. Closure:  [Countersunk] [Countersunk or raised-head] [Raised-head], [drilled-and-threaded] [brass] [cast-iron] plug.

8. Closure Plug Size:  Same as or not more than one size smaller than cleanout size.

9. Wall Access:  Round, [deep, chrome-plated bronze] [flat, chrome-plated brass or stainless-steel] cover plate with screw.

Retain subparagraph above for cover plate or subparagraph below for frame and cover to be installed in drywall.

10. Wall Access:  [Round] [Square], [nickel-bronze, copper-alloy, or stainless-steel] <Insert material> wall-installation frame and cover.

Copy and edit paragraph and subparagraphs below for each type of plastic floor cleanout required.  If only one type is required, drawing designation may be omitted.

D. Plastic Floor Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. NDS Inc.

d. Plastic Oddities; a division of Diverse Corporate Technologies.

e. Sioux Chief Manufacturing Company, Inc.

f. Zurn Plumbing Products Group; Light Commercial Operation.

g. <Insert manufacturer's name.>

3. Size:  Same as connected branch.

4. Body:  PVC.

5. Closure Plug:  PVC.

6. Riser:  Drainage pipe fitting and riser to cleanout of same material as drainage piping.

2.3 FLOOR DRAINS

Copy and edit paragraph and subparagraphs below for each type of cast-iron floor drain required.  If only one type is required, drawing designation may be omitted.

A. Cast-Iron Floor Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Commercial Enameling Co.

b. Josam Company; Josam Div.

c. MIFAB, Inc.

d. Prier Products, Inc.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Tyler Pipe; Wade Div.

g. Watts Drainage Products Inc.

h. Zurn Plumbing Products Group; Light Commercial Operation.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

4. Standard:  ASME A112.6.3[ with backwater valve].

5. Pattern:  [Area] [Floor] [Funnel floor] [Sanitary] <Insert pattern> drain.

6. Body Material:  [Gray iron] <Insert material>.

7. Seepage Flange:  [Not required] [Required].

8. Anchor Flange:  [Not required] [Required].

9. Clamping Device:  [Not required] [Required].

10. Outlet:  [Bottom] [Side] <Insert type>.

11. Backwater Valve:  [Drain-outlet type] [Integral, ASME A112.14.1, swing-check type] [Not required].

Coating in first subparagraph below is usually used only on sanitary floor drains.

12. Coating on Interior and Exposed Exterior Surfaces:  [Acid-resistant enamel] [Not required] <Insert material>.

13. Sediment Bucket:  [Not required] <Insert description>.

14. Top or Strainer Material:  [Bronze] [Gray iron] [Nickel bronze] [Stainless steel] <Insert material>.

15. Top of Body and Strainer Finish:  [Nickel bronze] [Polished bronze] [Rough bronze] [Stainless steel] <Insert finish>.

16. Top Shape:  [Round] [Square] <Insert shape>.

17. Dimensions of Top or Strainer:  <Insert dimensions and describe body, sump, and grate.>

18. Top Loading Classification:  [Extra Heavy-Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

19. Funnel:  [Not required] [Required] <Insert description and dimensions>.

20. Inlet Fitting:  [Not required] [Gray iron, with threaded inlet and threaded or spigot outlet, and trap-seal primer valve connection].

21. Trap Material:  [Bronze] [Cast iron] [Copper] [Not required] <Insert material>.

22. Trap Pattern:  [Deep-seal P-trap] [Standard P-trap] [Not required] <Insert pattern>.

23. Trap Features:  [Cleanout] [Trap-seal primer valve drain connection] [Cleanout and trap-seal primer valve drain connection] [Not required] <Insert type>.

Copy and edit paragraph and subparagraphs below for each type of stainless-steel floor drain required.  If only one type is required, drawing designation may be omitted.

B. Stainless-Steel Floor Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for ASME A112.3.1, stainless-steel floor drains.

a. Josam Company; Blucher-Josam Div.

b. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.6.3, stainless-steel floor drains.  Patterns and features are limited.

c. Josam Company; Josam Div.

d. Kusel Equipment Co.

e. Scherping Systems, Inc.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. Tyler Pipe; Wade Div.

h. Watts Drainage Products Inc.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

4. Standard:  [ASME A112.3.1] [ASME A112.6.3].

5. Outlet:  [Bottom] [Side] <Insert type>.

6. Top or Strainer Material:  [Stainless steel] <Insert material>.

7. Top Shape:  [Round] [Square] <Insert shape>.

8. Dimensions of Top or Strainer:  <Insert dimensions and describe body, sump, and grate.>

9. Seepage Flange:  [Not required] [Required].

10. Anchor Flange:  [Not required] [Required].

11. Clamping Device:  [Not required] [Required].

12. Trap-Primer Connection:  [Not required] [Required].

13. Trap Material:  [Cast iron] [Stainless steel] [Not required] <Insert material>.

14. Trap Pattern:  [Deep-seal P-trap] [Standard P-trap] [Not required] <Insert pattern>.

Copy and edit paragraph and subparagraphs below for each type of plastic floor drain required.  If only one type is required, drawing designation may be omitted.

C. Plastic Floor Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. Josam Company; Josam Div.

d. Oatey.

e. Plastic Oddities; a division of Diverse Corporate Technologies.

f. Sioux Chief Manufacturing Company, Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. <Insert manufacturer's name.>

4. Standard:  ASME A112.6.3.

5. Material:  [ABS] [or] [PVC] <Insert material>.

6. Seepage Flange:  [Not required] [Required].

7. Clamping Device:  [Not required] [Required].

8. Outlet:  [Bottom] [Side] <Insert type>.

9. Sediment Bucket:  [Not required] <Insert description>.

10. Top or Strainer Material:  [Bronze] [Plastic] [Stainless steel] <Insert other>.

11. Top of Body and Strainer Finish:  [Nickel bronze] [Polished bronze] [Rough bronze] [Stainless steel] <Insert other>.

12. Top Shape:  [Round] [Square] <Insert shape>.

13. Dimensions of Top or Strainer:  <Insert dimensions and describe body, sump, and grate if required.>

14. Trap Material:  [Cast iron] [Plastic drainage piping] [Not required] <Insert material>.

15. Trap Pattern:  [Standard P-trap] [Not required] <Insert pattern>.

2.4 TRENCH DRAINS

Copy and edit paragraph and subparagraphs below for each type of trench drain required.  If only one type is required, drawing designation may be omitted.

A. Trench Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.6.3 for trench drains.

5. Material:  Ductile or gray iron.

6. Flange:  [Anchor] [Seepage] [Not required].

7. Clamping Device:  [Not required] [Required].

8. Outlet:  [Bottom] [End] [Side] <Insert location>.

9. Grate Material:  [Ductile iron] [Ductile iron or gray iron] [Gray iron] [Stainless steel] <Insert material>.

10. Grate Finish:  [Painted] [Not required] <Insert finish>.

11. Dimensions of Frame and Grate:  <Insert dimensions and describe body, sump, and grate if required.>

12. Top Loading Classification:  [Extra Heavy-Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

13. Trap Material:  [Cast iron] [Stainless steel] [Not required] <Insert material>.

14. Trap Pattern:  [Standard P-trap] [Not required] <Insert pattern>.

2.5 CHANNEL DRAINAGE SYSTEMS

Copy and edit paragraph and subparagraphs below for each type of stainless-steel channel drainage system required.  If only one type is required, drawing designation may be omitted.

A. Stainless-Steel Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for ASME A112.3.1, stainless-steel channel drainage systems.

a. Josam Company; Blucher-Josam Div.

b. <Insert manufacturer's name.>

Manufacturers in list below are for non-ASME A112.3.1, stainless-steel channel drainage systems.

c. MultiDrain Systems.

d. Zurn Plumbing Products Group; Flo-Thru Operation.

e. <Insert manufacturer's name.>

Retain subparagraph and associated subparagraphs below for ASME A112.3.1, stainless-steel channel drainage systems.

4. Type:  Modular system of stainless-steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Standard:  ASME A112.3.1, for trench drains.

b. Channel Sections:  Interlocking-joint, stainless-steel with level invert.

1) Dimensions:  [5.8 inches (147 mm)] [11.7 inches (297mm)] wide.  Include number of units required to form total lengths indicated.

c. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

d. Covers:  Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

e. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

f. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for non-ASME A112.3.1, stainless-steel channel drainage systems.

5. Type:  Modular system of stainless-steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, stainless steel with level invert.

1) Dimensions:  [6 inches (152 mm)] [12 inches (305 mm)] wide.  Include number of units required to form total lengths indicated.

b. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

c. Covers:  Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of polymer-concrete channel drainage system required.  If only one type is required, drawing designation may be omitted.

B. Polymer-Concrete Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists of manufacturers below.

Manufacturers in list below are for narrow, sloped-invert, polymer-concrete channel drainage systems.

a. ABT, Inc.

b. ACO Polymer Products, Inc.

c. Forte Composites, Inc.

d. Josam Company; Mea-Josam Div.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Strongwell Corporation; Lenoir City Division.

g. <Insert manufacturer's name.>

Manufacturers in list below are for narrow, level-invert, polymer-concrete channel drainage systems.

h. ABT, Inc.

i. ACO Polymer Products, Inc.

j. Forte Composites, Inc.

k. Josam Company; Mea-Josam Div.

l. <Insert manufacturer's name.>

Manufacturers in list below are for wide, level-invert, polymer-concrete channel drainage systems.

m. ABT, Inc.

n. ACO Polymer Products, Inc.

o. Josam Company; Mea-Josam Div.

p. Strongwell Corporation; Lenoir City Division.

q. <Insert manufacturer's name.>

4. Type:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

Retain one of three "Channel Sections" subparagraphs and associated subparagraphs below.

Retain subparagraph and associated subparagraphs below for narrow, sloped-invert, polymer-concrete channel drainage systems.

a. Channel Sections:  Narrow, interlocking-joint, sloped-invert, polymer-concrete modular units with end caps.  Include rounded bottom, with built-in invert slope of 0.6 percent and with outlets in number, sizes, and locations indicated.  Include extension sections necessary for required depth.

1) Dimensions:  4-inch (102-mm) inside width.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

b. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

c. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for narrow, level-invert, polymer-concrete channel drainage systems.

f. Channel Sections:  Narrow, interlocking-joint, precast, polymer-concrete modular units with end caps.  Include rounded bottom, with level invert and with NPS 4 (DN 100) outlets in number and locations indicated.

1) Dimensions:  [5-inch (127-mm)] <Insert dimension> inside width and [9-3/4 inches (248 mm)] <Insert dimension> deep.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

g. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

h. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

i. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

j. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for wide, level-invert, polymer-concrete channel drainage systems.

k. Channel Sections:  Wide, interlocking-joint, precast, polymer-concrete modular units with end caps.  Include flat or rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

1) Dimensions:  [8-inch (203-mm)] <Insert dimension> inside width and [13-3/4 inches (350 mm)] <Insert dimension> deep.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

l. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

m. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

n. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

o. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of polymer-concrete sediment interceptor required.  If only one type is required, drawing designation may be omitted.

C. Polymer-Concrete Sediment Interceptor <Insert drawing designation if any>:

1. Description:  [27-inch- (686-mm-)] <Insert dimension> square, precast, polymer-concrete body, with outlets in number and sizes indicated.  Include 24-inch- (610-mm-) square, gray-iron slotted grate.

2. Frame:  [Gray-iron or galvanized steel for grate] [Not required].

Copy and edit paragraph and subparagraphs below for each type of FRP channel drainage system required.  If only one type is required, drawing designation may be omitted.

D. FRP Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ACO Polymer Products, Inc.

b. Aquaduct, Inc.; an ACO Polymer Products, Inc. Company.

c. Josam Company; Mea-Josam Div.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Zurn Plumbing Products Group; Flo-Thru Operation.

f. <Insert manufacturer's name.>

4. Description:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, sloped-invert, FRP modular units, with end caps.  Include flat, rounded, or inclined inside bottom, with outlets in number, sizes, and locations indicated.

1) Dimensions:  [4 inches (102 mm)] [4 or 6 inches (102 or 152 mm)] [6 inches (152 mm)] [6 or 8 inches (152 or 203 mm)] [8 inches (203 mm)] wide.  Include number of units required to form total lengths indicated.

2) Frame:  [Galvanized steel] [Stainless steel] [Manufacturer's standard metal] <Insert material> for grates.

b. Grates:  With slots or perforations and widths and thickness that fit recesses in channel sections.

1) Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

c. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of plastic channel drainage system required.  If only one type is required, drawing designation may be omitted.

E. Plastic Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists of manufacturers below.

Manufacturers in list below are for HDPE or PE channel drainage systems.

a. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

b. Tuf-Tite Corporation.

c. Zurn Plumbing Products Group; Flo-Thru Operation.

d. <Insert manufacturer's name.>

Manufacturers in list below are for PP channel drainage systems.

e. Infinity Plastics, Inc.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. <Insert manufacturer's name.>

Manufacturers in list below are for PVC channel drainage systems.

h. MultiDrain Systems.

i. NDS Inc.

j. <Insert manufacturer's name.>

Manufacturers in list below are for HDPE, PE, PP, or PVC channel drainage systems.

k. Infinity Plastics, Inc.

l. MultiDrain Systems.

m. NDS Inc.

n. Smith, Jay R. Mfg Co.; Division of Smith Industries, Inc.

o. Tuf-Tite Corporation.

p. Zurn Plumbing Products Group; Flo-Thru Operation.

q. <Insert manufacturer's name.>

4. Type:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, [HDPE or PE] [PP] [or] [PVC] modular units,  with end caps.  Include flat, rounded, or inclined bottom, with level invert and with outlets in number, sizes, and locations indicated.

1) Dimensions:  4 inches (102 mm) wide.  Include number of units required to form total lengths indicated.

b. Grates:  With slots or perforations and widths and thickness that fit recesses in channel sections.

1) Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Color:  <Insert color or delete subparagraph.>

c. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

d. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

2.6 AIR-ADMITTANCE VALVES

Copy and edit paragraph and subparagraphs below for each type of fixture air-admittance valve required.  If only one type is required, drawing designation may be omitted.

Valves in paragraph below are available in NPS 1-1/2 and NPS 2 (DN 40 and DN 50).  Valves NPS 1-1/4 to NPS 4 (DN 32 to DN 100) are allowed by ASSE 1051.

A. Fixture Air-Admittance Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Ayrlett, LLC.

b. Durgo, Inc.

c. Oatey.

d. ProSet Systems Inc.

e. RectorSeal.

f. Studor, Inc.

g. <Insert manufacturer's name.>

3. Standard:  ASSE 1051, Type A for single fixture or Type B for branch piping.

4. Housing:  Plastic.

5. Operation:  Mechanical sealing diaphragm.

6. Size:  Same as connected fixture or branch vent piping.

Copy and edit paragraph and subparagraphs below for each type of stack air-admittance valve required.  If only one type is required, drawing designation may be omitted.

Valves in paragraph below are available in NPS 1-1/2, NPS 2, and NPS 3 (DN 40, DN 50, and DN 80).  There are no size limitations in ASSE 1050.

B. Stack Air-Admittance Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Durgo, Inc.

b. Oatey.

c. Studor, Inc.

d. <Insert manufacturer's name.>

3. Standard:  ASSE 1050 for vent stacks.

4. Housing:  Plastic.

5. Operation:  Mechanical sealing diaphragm.

6. Size:  Same as connected stack vent or vent stack.

Copy and edit paragraph and subparagraphs below for each type of wall box required.  If only one type is required, drawing designation may be omitted.

C. Wall Box <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Durgo, Inc.

b. Oatey.

c. RectorSeal.

d. Studor, Inc.

e. <Insert manufacturer's name.>

3. Description:  White plastic housing with white plastic grille, made for recessed installation.  Include bottom pipe connection and space to contain one air-admittance valve.

4. Size:  About 9 inches wide by 8 inches high by 4 inches deep (230 mm wide by 200 mm high by 100 mm deep).

2.7 ROOF FLASHING ASSEMBLIES

Copy and edit first paragraph and subparagraphs below for each type of roof flashing assembly required.  If only one type is required, drawing designation may be omitted.

A. Roof Flashing Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company; Elmdor/Stoneman Div.

b. Thaler Metal Industries Ltd.

c. <Insert manufacturer's name.>

B. Description:  Manufactured assembly made of [4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch- (1.6-mm-)] [6.0-lb/sq. ft. (30-kg/sq. m), 0.0938-inch- (2.4-mm-)] thick, lead flashing collar and skirt extending at least [6 inches (150 mm)] [8 inches (200 mm)] [10 inches (250 mm)] from pipe, with galvanized-steel boot reinforcement and counterflashing fitting.

Retain one or more of three subparagraphs below.  If retaining more than one, indicate location of each on Drawings.

1. Open-Top Vent Cap:  Without cap.

2. Low-Silhouette Vent Cap:  With vandal-proof vent cap.

3. Extended Vent Cap:  With field-installed, vandal-proof vent cap.

2.8 THROUGH-PENETRATION FIRESTOP ASSEMBLIES

Copy and edit paragraph and subparagraphs below for each type of through-penetration firestop assembly required.  If only one type is required, drawing designation may be omitted.

A. Through-Penetration Firestop Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. ProSet Systems Inc.

b. <Insert manufacturer's name.>

3. Standard:  UL 1479 assembly of sleeve and stack fitting with firestopping plug.

4. Size:  Same as connected soil, waste, or vent stack.

5. Sleeve:  Molded PVC plastic, of length to match slab thickness and with integral nailing flange on one end for installation in cast-in-place concrete slabs.

Fitting in subparagraph below is for use with plastic stacks.

6. Stack Fitting:  ASTM A 48/A 48M, gray-iron, hubless-pattern, wye branch with neoprene O-ring at base and gray-iron plug in thermal-release harness.  Include PVC protective cap for plug.

Coating in subparagraph below is for use with corrosion-resistant plastic stacks.

7. Special Coating:  Corrosion resistant on interior of fittings.

2.9 MISCELLANEOUS SANITARY DRAINAGE PIPING SPECIALTIES

Copy and edit paragraph and subparagraphs below for each type of open drain required.  If only one type is required, drawing designation may be omitted.

A. Open Drains <Insert drawing designation if any>:

1. Description:  Shop or field fabricate from ASTM A 74, Service class, hub-and-spigot, cast-iron, soil-pipe fittings.  Include P-trap, hub-and-spigot riser section; and where required, increaser fitting joined with ASTM C 564, rubber gaskets.

2. Size:  Same as connected waste piping[ with increaser fitting of size indicated].

Copy and edit paragraph and subparagraphs below for each type of deep-seal trap required.  If only one type is required, drawing designation may be omitted.

B. Deep-Seal Traps <Insert drawing designation if any>:

1. Description:  Cast-iron or bronze casting, with inlet and outlet matching connected piping and cleanout trap-seal primer valve connection.

2. Size:  Same as connected waste piping.

a. NPS 2 (DN 50):  4-inch- (100-mm-) minimum water seal.

b. NPS 2-1/2 (DN 65) and Larger:  5-inch- (125-mm-) minimum water seal.

Copy and edit paragraph and subparagraphs below for each type of floor-drain, trap-seal primer fitting required.  If only one type is required, drawing designation may be omitted.

C. Floor-Drain, Trap-Seal Primer Fittings <Insert drawing designation if any>:

1. Description:  Cast iron, with threaded inlet and threaded or spigot outlet, and trap-seal primer valve connection.

2. Size:  Same as floor drain outlet with NPS 1/2 (DN 15) side inlet.

Copy and edit paragraph and subparagraphs below for each type of air-gap fitting required.  If only one type is required, drawing designation may be omitted.

D. Air-Gap Fittings <Insert drawing designation if any>:

1. Standard:  ASME A112.1.2, for fitting designed to ensure fixed, positive air gap between installed inlet and outlet piping.

2. Body:  Bronze or cast iron.

3. Inlet:  Opening in top of body.

4. Outlet:  Larger than inlet.

5. Size:  Same as connected waste piping and with inlet large enough for associated indirect waste piping.

Copy and edit paragraph and subparagraphs below for each type of sleeve flashing device required.  If only one type is required, drawing designation may be omitted.

E. Sleeve Flashing Device <Insert drawing designation if any>:

1. Description:  Manufactured, cast-iron fitting, with clamping device, that forms sleeve for pipe floor penetrations of floor membrane.  Include galvanized-steel pipe extension in top of fitting that will extend [1 inch (25 mm)] [2 inches (51 mm)] <Insert dimension> above finished floor and galvanized-steel pipe extension in bottom of fitting that will extend through floor slab.

2. Size:  As required for close fit to riser or stack piping.

Copy and edit paragraph and subparagraphs below for each type of stack flashing fitting required.  If only one type is required, drawing designation may be omitted.

F. Stack Flashing Fittings <Insert drawing designation if any>:

1. Description:  Counterflashing-type, cast-iron fitting, with bottom recess for terminating roof membrane, and with threaded or hub top for extending vent pipe.

2. Size:  Same as connected stack vent or vent stack.

Copy and edit paragraph and subparagraphs below for each type of vent cap required.  If only one type is required, drawing designation may be omitted.

G. Vent Caps <Insert drawing designation if any>:

1. Description:  Cast-iron body with threaded or hub inlet and vandal-proof design.  Include vented hood and setscrews to secure to vent pipe.

2. Size:  Same as connected stack vent or vent stack.

Copy and edit paragraph and subparagraphs below for each type of frost-resistant vent terminal required.  If only one type is required, drawing designation may be omitted.

H. Frost-Resistant Vent Terminals <Insert drawing designation if any>:

1. Description:  Manufactured or shop-fabricated assembly constructed of copper, lead-coated copper, or galvanized steel.

2. Design:  To provide 1-inch (25-mm) enclosed air space between outside of pipe and inside of flashing collar extension, with counterflashing.

Copy and edit paragraph and subparagraphs below for each type of expansion joint required.  If only one type is required, drawing designation may be omitted.

Fittings in paragraph below are designed for use with roof drains but may also be used with conductors and sanitary drainage and vent systems if required.

I. Expansion Joints <Insert drawing designation if any>:

1. Standard:  ASME A112.21.2M.

2. Body:  Cast iron with bronze sleeve, packing, and gland.

3. End Connections:  Matching connected piping.

4. Size:  Same as connected soil, waste, or vent piping.

2.10 FLASHING MATERIALS

Coordinate this Article with Division 7 Sections "Sheet Metal Flashing and Trim" and "Roof Accessories." Delete Article if all required materials are specified in Division 7 Sections.

Coordinate first two paragraphs and associated subparagraphs below with Division 7 Section "Sheet Metal Flashing and Trim" if used on roofs.

A. Lead Sheet:  ASTM B 749, Type L51121, copper bearing, with the following minimum weights and thicknesses, unless otherwise indicated:

1. General Use:  4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch (1.6-mm) thickness.

2. Vent Pipe Flashing:  3.0-lb/sq. ft. (15-kg/sq. m), 0.0469-inch (1.2-mm) thickness.

3. Burning:  6-lb/sq. ft. (30-kg/sq. m), 0.0938-inch (2.4-mm) thickness.

Coordinate first two paragraphs and associated subparagraphs below with Division 7 Section "Sheet Metal Flashing and Trim" if used for drainage receptors.

B. Copper Sheet:  ASTM B 152/B 152M, of the following minimum weights and thicknesses, unless otherwise indicated:

1. General Applications:  12 oz./sq. ft. (3.7 kg/sq. m or 0.41-mm) thickness.

2. Vent Pipe Flashing:  8 oz./sq. ft. (2.5 kg/sq. m or 0.27-mm) thickness.

C. Zinc-Coated Steel Sheet:  ASTM A 653/A 653M, with 0.20 percent copper content and 0.04-inch (1.01-mm) minimum thickness, unless otherwise indicated.  Include G90 (Z275) hot-dip galvanized, mill-phosphatized finish for painting if indicated.

D. Elastic Membrane Sheet:  ASTM D 4068, flexible, chlorinated polyethylene, 40-mil (1.01-mm) minimum thickness.

E. Fasteners:  Metal compatible with material and substrate being fastened.

F. Metal Accessories:  Sheet metal strips, clamps, anchoring devices, and similar accessory units required for installation; matching or compatible with material being installed.

G. Solder:  ASTM B 32, lead-free alloy.

H. Bituminous Coating:  SSPC-Paint 12, solvent-type, bituminous mastic.

2.11 FOG DISPOSAL SYSTEMS

Copy and edit this Article for each type of FOG disposal system required.  If only one type is required, drawing designation may be omitted.

A. FOG Disposal Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

b. <Insert manufacturer's name.>

4. Standard:  IAPMO PS 118, for removing solids from and breaking down and digesting suspended fats, oils, and greases from food[-preparation] [or] [-processing] wastewater.

5. Flow-Control Fitting:  Matching unit size.

6. Strainer Unit:  Stainless-steel housing with aluminum cover and removable-basket-type, stainless-steel, wire-mesh strainer.[ Include pressure plug instead of cover.] [ Include extra basket.] [ Include stainless-steel extension.]

7. Media Chamber:  Stainless-steel housing and aluminum cover, with internal baffles, piping, plastic coalescing surfaces, and clarifier section with test ports.[ Include stainless-steel extension.]

8. Shelf:  Stainless steel, 19.5 inches wide by 13 inches high by 8.75 inches deep (495 mm wide by 330 mm high by 222 mm deep), for metering pump, control devices, and culture bottle.

9. Culture Metering Pump, Timer, Control, and Tubing:  Proprietary.

10. Culture:  Include 1-gal. (3.8-L) bottle, as recommended by unit manufacturer.

11. Strainer and Media-Chamber, Unit Size:  [20 gpm (1.26 L/s)] [35 gpm (2.21 L/s)].

12. Inlet and Outlet:  NPS 2 (DN 50).

Retain two subparagraphs above or first two subparagraphs below.

13. Strainer and Media-Chamber, Unit Size:  [50 gpm (3.15 L/s)] [75 gpm (4.73 L/s)].

14. Inlet and Outlet:  NPS 3 (DN 80).

15. Piping:  Waste and vent piping is specified in Division 15 Section "Sanitary Waste and Vent Piping."

16. Power Requirement:  [120-V ac] <Insert power>.

17. Full-Load Amperes:  <Insert value> A.

18. Minimum Circuit Ampacity:  <Insert value> A.

19. Maximum Overcurrent Protection:  <Insert value> A.

2.12 GREASE INTERCEPTORS

Copy and edit this Article for each type of grease interceptor required.  If only one type is required, drawing designation may be omitted.

A. Grease Interceptors <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for cast-iron or steel grease interceptors.

a. Applied Chemical Technology, Incorporated.

b. Josam Company; Josam Div.

c. MIFAB, Inc.

d. Rockford Sanitary Systems, Inc.

e. Schier Products Company.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. Tyler Pipe; Wade Div.

h. Watts Drainage Products Inc.

i. Zurn Plumbing Products Group; Light Commercial Operation.

j. Zurn Plumbing Products Group; Specification Drainage Operation.

k. <Insert manufacturer's name.>

Manufacturers in list below are for plastic grease interceptors.

l. Ashland Trap Distribution Co.

m. Bio-Microbics, Inc.

n. Canplas LLC.

o. Schier Products Company.

p. Zurn Plumbing Products Group; Light Commercial Operation.

q. <Insert manufacturer's name.>

4. Standard:  ASME A112.14.3[ and PDI-G101], for intercepting and retaining fats, oils, and greases from food[-preparation] [or] [-processing] wastewater.

PDI certification is currently limited to 50-gpm (3.15-L/s) flow rate and 100-lb (45.4-kg) grease retention by PDI-G101.  Larger uncertified units are available.  PDI-G101 is being revised, should be available by end of 2003, and will include capacities to 100 gpm (6.3 L/s).

5. Plumbing and Drainage Institute Seal:  [Not required] [Required].

6. Body Material:  [Cast iron] [Cast iron or steel] [Plastic] <Insert material>.

7. Interior Lining:  [Corrosion-resistant enamel] [Not required] <Insert lining>.

8. Exterior Coating:  [Corrosion-resistant enamel] [Not required] <Insert coating>.

9. Body Dimensions:  <Insert dimensions.>

10. Body Extension:  [Not required] [Required].

Rate in subparagraph below is limited to 100 gpm (6.3 L/s).

11. Flow Rate:  <Insert interceptor design rate.>

Capacity in first subparagraph below is limited to 200 lb (90.7 kg).

12. Grease Retention Capacity:  <Insert capacity.>

13. Inlet and Outlet Size:  <Insert size.>

14. End Connections:  [Flanged] [Hub] [Threaded].

15. Cleanout:  Integral[ or field installed on outlet].

16. Mounting:  [Above floor] [Recessed in acid-resistant, coated steel frame and cradle] [Recessed, flush with floor] <Insert mounting>.

17. Flow-Control Fitting:  [Not required] [Required].

18. Operation:  [Automatic recovery] [Manual cleaning] [Semiautomatic, manual drawoff] <Insert operation>.

2.13 GREASE REMOVAL DEVICES

Copy and edit this Article for each type of grease removal device required.  If only one type is required, drawing designation may be omitted.

A. Grease Removal Devices <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Applied Chemical Technology, Incorporated.

b. G K & L, Inc.

c. International Grease Recovery Device.

d. Josam Company; Blucher-Josam Div.

e. Lowe Engineering; a division of Highland Tank & Manufacturing Co., Inc.

f. Thermaco, Inc.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.14.4[ and with PDI-G101 for flow tests], for automatic intercepting and removal of fats, oils, and greases from food[-preparation] [or] [-processing] <Insert application> wastewater.

PDI certification is currently limited to 50-gpm (3.15-L/s) flow rate and 100-lb (45.4-kg) grease retention by PDI-G101.  Larger uncertified units are available.  PDI-G101 is being revised, should be available by end of 2003, and will include capacities to 100 gpm (6.3 L/s).

5. Body Material:  [Stainless steel] [Steel] <Insert material>.

6. Interior Separation Device:  [Baffles] [Screens] <Insert device>.

7. Heater:  [Not required] [Required].

8. Interior Lining:  [Not required] <Insert description if required>.

9. Exterior Coating:  [Not required] <Insert description if required>.

10. Unit Dimensions:  <Insert dimensions.>

11. Flow Rate:  <Insert recovery unit design rate.>

12. Basket Material:  [Stainless steel] <Insert material>.

13. Inlet and Outlet Size:  <Insert size.>

14. End Connections:  [Flanged] [Hub] [Threaded].

15. Cleanout:  Integral[ or field installed on outlet].

16. Mounting:  [Above floor] <Insert mounting>.

17. Flow-Control Fitting:  [Not required] [Required].

18. Operation:  [Automatic recovery] <Insert operation>.

19. Power Requirement:  [120-V ac] <Insert power>.

20. Full-Load Amperes:  <Insert value> A.

21. Minimum Circuit Ampacity:  <Insert value> A.

22. Maximum Overcurrent Protection:  <Insert value> A.

23. Waste Grease Receptacle:  [Furnished by Owner] <Insert description>.

2.14 OIL INTERCEPTORS

Copy and edit this Article for each type of oil interceptor required.  If only one type is required, drawing designation may be omitted.

A. Oil Interceptors <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for cast-iron or steel oil interceptors.

a. Applied Chemical Technology, Incorporated.

b. Josam Company; Josam Div.

c. MIFAB, Inc.

d. Rockford Sanitary Systems, Inc.

e. Schier Products Company.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. Tyler Pipe; Wade Div.

h. Watts Drainage Products Inc.

i. Zurn Plumbing Products Group; Specification Drainage Operation.

j. <Insert manufacturer's name.>

Manufacturers in list below are for plastic oil interceptors.

k. Ashland Trap Distribution Co.

l. Schier Products Company.

m. Town & Country Plastics, Inc.

n. <Insert manufacturer's name.>

4. Type:  Factory-fabricated interceptor for separating and removing [light oil] <Insert type of oil> from wastewater.

5. Body Material:  [Cast iron or steel] [Plastic] <Insert material>.

6. Interior Lining:  [Corrosion-resistant enamel] [Not required] <Insert lining>.

7. Exterior Coating:  [Corrosion-resistant enamel] [Not required] <Insert coating>.

8. Body Dimensions:  <Insert dimensions.>

9. Flow Rate:  <Insert interceptor design rate.>

10. Inlet and Outlet Size:  <Insert size.>

11. End Connections:  [Flanged] [Hub] [Threaded].

12. Cleanout:  Integral[ or field installed on outlet].

13. Mounting:  [Above floor] [Recessed in acid-resistant, coated steel frame and cradle] [Recessed, flush with floor] <Insert mounting>.

14. Flow-Control Fitting:  [Not required] [Required].

15. Descriptive Type or Function:  <Describe type or function or delete subparagraph.>

16. Oil Storage Tank:  [Coordinate with Division 15 Section "Facility Fuel-Oil Piping."] <Insert tank description.>

2.15 SOLIDS INTERCEPTORS

Copy and edit this Article for each type of solids interceptor required.  If only one type is required, drawing designation may be omitted.

A. Solids Interceptors <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for cast-iron or steel solids interceptors.

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Rockford Sanitary Systems, Inc.

d. Schier Products Company.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Tyler Pipe; Wade Div.

g. Watts Drainage Products Inc.

h. Zurn Plumbing Products Group; Specification Drainage Operation.

i. <Insert manufacturer's name.>

Manufacturers in list below are for plastic solids interceptors.

j. Ashland Trap Distribution Co.

k. Schier Products Company.

l. Town & Country Plastics, Inc.

m. <Insert manufacturer's name.>

4. Type:  Factory-fabricated interceptor made for removing and retaining [lint] [sediment] <Insert solid> from wastewater.

5. Body Material:  [Cast iron or steel] [Stainless steel] [Plastic] <Insert material>.

6. Interior Separation Device:  [Baffles] [Screens] <Insert device>.

7. Interior Lining:  [Corrosion-resistant enamel] [Not required] <Insert lining>.

8. Exterior Coating:  [Corrosion-resistant enamel] [Not required] <Insert coating>.

9. Body Dimensions:  <Insert dimensions.>

10. Flow Rate:  [Not required] <Insert description if required>.

11. Inlet and Outlet Size:  <Insert size.>

12. End Connections:  [Threaded] <Insert connections>.

13. Mounting:  [Above floor] [Inline] <Insert mounting>.

2.16 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Common Motor Requirements for Plumbing Equipment." If different characteristics are required, add paragraphs here to suit Project.

A. General requirements for motors are specified in Division 15 Section "Common Motor Requirements for Plumbing Equipment."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

PART 3 -  EXECUTION

3.1 CONCRETE BASES

Revise this Article to suit equipment to be installed.  Indicate dowel rod quantity, size, and spacing on Drawings.  Retain this Article if products are to be installed on concrete bases.

A. Anchor [FOG disposal systems] [grease interceptors] [grease removal devices] [and] [solids interceptors] to concrete bases.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 19-inch (480-mm) centers around full perimeter of base.

2. For installed equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be imbedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

5. Concrete base construction requirements are specified in Division 15 Section "Common Work Results for Plumbing."

6. Cast-in-place concrete materials and placement requirements are specified in Division 3.

3.2 INSTALLATION

In this Article, retain only those sanitary piping specialties that are specified in Part 2.  Additional instructions may be required for special applications.  Show locations of specialties in plans, details, and schematics on Drawings.

A. Refer to Division 15 Section "Common Work Results for Plumbing" for piping joining materials, joint construction, and basic installation requirements.

B. Install backwater valves in building drain piping.  For interior installation, provide cleanout deck plate flush with floor and centered over backwater valve cover, and of adequate size to remove valve cover for servicing.

C. Install cleanouts in aboveground piping and building drain piping according to the following, unless otherwise indicated:

1. Size same as drainage piping up to NPS 4 (DN 100).  Use NPS 4 (DN 100) for larger drainage piping unless larger cleanout is indicated.

2. Locate at each change in direction of piping greater than 45 degrees.

3. Locate at minimum intervals of 50 feet (15 m) for piping NPS 4 (DN 100) and smaller and 100 feet (30 m) for larger piping.

4. Locate at base of each vertical soil and waste stack.

D. For floor cleanouts for piping below floors, install cleanout deck plates with top flush with finished floor.

E. For cleanouts located in concealed piping, install cleanout wall access covers, of types indicated, with frame and cover flush with finished wall.

F. Install floor drains at low points of surface areas to be drained.  Set grates of drains flush with finished floor, unless otherwise indicated.

Coordinate four subparagraphs and associated subparagraphs below with Drawings.

1. Position floor drains for easy access and maintenance.

2. Set floor drains below elevation of surrounding finished floor to allow floor drainage.  Set with grates depressed according to the following drainage area radii:

a. Radius, 30 Inches (750 mm) or Less:  Equivalent to 1 percent slope, but not less than 1/4-inch (6.35-mm) total depression.

b. Radius, 30 to 60 Inches (750 to 1500 mm):  Equivalent to 1 percent slope.

c. Radius, 60 Inches (1500 mm) or Larger:  Equivalent to 1 percent slope, but not greater than 1-inch (25-mm) total depression.

3. Install floor-drain flashing collar or flange so no leakage occurs between drain and adjoining flooring.  Maintain integrity of waterproof membranes where penetrated.

4. Install individual traps for floor drains connected to sanitary building drain, unless otherwise indicated.

G. Install trench drains at low points of surface areas to be drained.  Set grates of drains flush with finished surface, unless otherwise indicated.

Retain one of first two paragraphs below.

H. Assemble and install ASME A112.3.1, stainless-steel channel drainage systems according to ASME A112.3.1.  Install on support devices so that top will be flush with surface.

I. Assemble non-ASME A112.3.1, stainless-steel channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

J. Assemble FRP channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

K. Assemble plastic channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

Air-admittance valves in first two paragraphs below cannot replace all vent piping.  They should be used only where normal venting is difficult.  If used, they should be indicated on Drawings.

L. Install fixture air-admittance valves on fixture drain piping.

M. Install stack air-admittance valves at top of stack vent and vent stack piping.

N. Install air-admittance-valve wall boxes recessed in wall.

Retain one of first two paragraphs below.

O. Install roof flashing assemblies on sanitary stack vents and vent stacks that extend through roof.

P. Install flashing fittings on sanitary stack vents and vent stacks that extend through roof.

Q. Install through-penetration firestop assemblies in plastic [conductors] [and] [stacks] at floor penetrations.

R. Assemble open drain fittings and install with top of hub [1 inch (25 mm)] [2 inches (51 mm)] <Insert dimension> above floor.

S. Install deep-seal traps on floor drains and other waste outlets, if indicated.

T. Install floor-drain, trap-seal primer fittings on inlet to floor drains that require trap-seal primer connection.

1. Exception:  Fitting may be omitted if trap has trap-seal primer connection.

2. Size:  Same as floor drain inlet.

U. Install air-gap fittings on draining-type backflow preventers and on indirect-waste piping discharge into sanitary drainage system.

V. Install sleeve flashing device with each riser and stack passing through floors with waterproof membrane.

Retain paragraph below to reduce vandalism.

W. Install vent caps on each vent pipe passing through roof.

Retain first paragraph below for freezing climates.  These units may be used to prevent frost closure instead of increasing vent size if permitted by authorities having jurisdiction.

X. Install frost-resistant vent terminals on each vent pipe passing through roof.  Maintain 1-inch (25-mm) clearance between vent pipe and roof substrate.

Y. Install expansion joints on vertical stacks and conductors.  Position expansion joints for easy access and maintenance.

Retain first paragraph below for freezing climates.  These units may be used to prevent frost closure instead of increasing vent size if permitted by authorities having jurisdiction.

Z. Install frost-proof vent caps on each vent pipe passing through roof.  Maintain 1-inch (25-mm) clearance between vent pipe and roof substrate.

AA. Assemble components of FOG disposal systems and install on floor.  Install trap, vent, fresh-air inlet, and flow-control fitting according to authorities having jurisdiction.  Install shelf fastened to reinforcement in wall construction and adjacent to unit, unless otherwise indicated.  Install culture bottle, culture metering pump, timer, and control on shelf.  Install tubing between culture bottle, metering pump, and chamber.

AB. Install grease interceptors, including trapping, venting, and flow-control fitting, according to authorities having jurisdiction and with clear space for servicing.

Retain one or more of first three subparagraphs below.

1. Above-Floor Installation:  Set unit with bottom resting on floor, unless otherwise indicated.

2. Flush with Floor Installation:  Set unit and extension, if required, with cover flush with finished floor.

3. Recessed Floor Installation:  Set unit in receiver housing having bottom or cradle supports, with receiver housing cover flush with finished floor.

4. Install cleanout immediately downstream from interceptors not having integral cleanout on outlet.

AC. Install grease removal devices on floor.  Install trap, vent, and flow-control fitting according to authorities having jurisdiction.  Install control panel adjacent to unit, unless otherwise indicated.

AD. Install oil interceptors, including trapping, venting, and flow-control fitting, according to authorities having jurisdiction and with clear space for servicing.  Coordinate oil-interceptor storage tank and gravity drain with Division 15 Section "Facility Fuel-Oil Piping."

AE. Install solids interceptors with cleanout immediately downstream from interceptors that do not have integral cleanout on outlet.  Install trap on interceptors that do not have integral trap and are connected to sanitary drainage and vent systems.

AF. Install wood-blocking reinforcement for wall-mounting-type specialties.

AG. Install traps on plumbing specialty drain outlets.  Omit traps on indirect wastes unless trap is indicated.

AH. Install escutcheons at wall, floor, and ceiling penetrations in exposed finished locations and within cabinets and millwork.  Use deep-pattern escutcheons if required to conceal protruding pipe fittings.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to equipment to allow service and maintenance.

C. FOG Disposal Systems:  Connect inlet and outlet to unit, connect flow-control fitting and fresh-air inlet piping to unit inlet piping, and connect vent piping between trap and media chamber.  Connect electrical power.

D. Grease Interceptors:  Connect inlet and outlet to unit, and connect flow-control fitting and vent to unit inlet piping.  Install valve on outlet of automatic drawoff-type unit.

E. Grease Removal Devices:  Connect controls, electrical power, factory-furnished accessories, and inlet, outlet, and vent piping to unit.

F. Oil Interceptors:  Connect inlet, outlet, vent, and gravity drawoff piping to unit; flow-control fitting and vent to unit inlet piping; and gravity drawoff and suction piping to oil storage tank.

G. Ground equipment according to Division 16 Section "Grounding and Bonding."

H. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FLASHING INSTALLATION

Coordinate this Article with Division 7 Section "Sheet Metal Flashing and Trim."

A. Fabricate flashing from single piece unless large pans, sumps, or other drainage shapes are required.  Join flashing according to the following if required:

1. Lead Sheets:  Burn joints of lead sheets 6.0-lb/sq. ft. (30-kg/sq. m), 0.0938-inch (2.4-mm) thickness or thicker.  Solder joints of lead sheets 4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch (1.6-mm) thickness or thinner.

2. Copper Sheets:  Solder joints of copper sheets.

B. Install sheet flashing on pipes, sleeves, and specialties passing through or embedded in floors and roofs with waterproof membrane.

1. Pipe Flashing:  Sleeve type, matching pipe size, with minimum length of 10 inches (250 mm), and skirt or flange extending at least 8 inches (200 mm) around pipe.

2. Sleeve Flashing:  Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around sleeve.

3. Embedded Specialty Flashing:  Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around specialty.

C. Set flashing on floors and roofs in solid coating of bituminous cement.

D. Secure flashing into sleeve and specialty clamping ring or device.

Retain one or both paragraphs below.

E. Install flashing for piping passing through roofs with counterflashing or commercially made flashing fittings, according to Division 7 Section "Sheet Metal Flashing and Trim."

F. Extend flashing up vent pipe passing through roofs and turn down into pipe, or secure flashing into cast-iron sleeve having calking recess.

Coordinate paragraph below with Division 7 Section "Sheet Metal Flashing and Trim."

G. Fabricate and install flashing and pans, sumps, and other drainage shapes.

3.5 LABELING AND IDENTIFYING

A. Equipment Nameplates and Signs:  Install engraved plastic-laminate equipment nameplate or sign on or near each of the following:

1. FOG disposal systems.

2. Grease interceptors.

3. Grease removal devices.

4. Oil interceptors.

5. Solids interceptors.

B. Distinguish among multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations, in addition to identifying unit.  Nameplates and signs are specified in Division 15 Section "Identification for Plumbing Piping and Equipment."

3.6 FIELD QUALITY CONTROL

Delete this Article if no FOG disposal systems or grease removal devices.

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled [FOG disposal systems] [and] [grease removal devices] and their installation, including piping and electrical connections, and to assist in testing.

B. Tests and Inspections:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.7 PROTECTION

A. Protect drains during remainder of construction period to avoid clogging with dirt or debris and to prevent damage from traffic or construction work.

B. Place plugs in ends of uncompleted piping at end of each day or when work stops.

3.8 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain [FOG disposal systems] [and] [grease removal devices].  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15155

SANITARY WASTE PIPING SPECIALTIES
15155 - 1

