Copyright 2004 AIA
MASTERSPEC Full Length
06/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15181 - HYDRONIC PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes pipe and fitting materials, joining methods, special-duty valves, and specialties for the following:

Adjust list below to suit Project.

1. Hot-water heating piping.

2. Chilled-water piping.

3. Dual-temperature heating and cooling water piping.

4. Condenser-water piping.

5. Glycol cooling-water piping.

6. Makeup-water piping.

7. Condensate-drain piping.

8. Blowdown-drain piping.

9. Air-vent piping.

10. Safety-valve-inlet and -outlet piping.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Hydronic Pumps" for pumps, motors, and accessories for hydronic piping.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. PTFE:  Polytetrafluoroethylene.

RTRF and RTRP in two paragraphs below are ASTM abbreviations.

B. RTRF:  Reinforced thermosetting resin (fiberglass) fittings.

C. RTRP:  Reinforced thermosetting resin (fiberglass) pipe.

1.4 PERFORMANCE REQUIREMENTS

A. Hydronic piping components and installation shall be capable of withstanding the following minimum working pressure and temperature:

Working pressure is equal to the relief pressure plus the static height of the system and pumping head.  The only working pressure mandated by authorities having jurisdiction is for makeup water.

1. Hot-Water Heating Piping:  <Insert psig (kPa)> at [200 deg F (93 deg C)] <Insert temperature>.

2. Chilled-Water Piping:  <Insert psig (kPa)> at [200 deg F (93 deg C)] <Insert temperature>.

3. Dual-Temperature Heating and Cooling Water Piping:  <Insert psig (kPa)> at [200 deg F (93 deg C)] <Insert temperature>.

4. Condenser-Water Piping:  <Insert psig (kPa)> at [150 deg F (66 deg C)] <Insert temperature>.

5. Glycol Cooling-Water Piping:  <Insert psig (kPa)> at [150 deg F (66 deg C)] <Insert temperature>.

6. Makeup-Water Piping:  [80 psig (552 kPa)] <Insert pressure> at [150 deg F (66 deg C)] <Insert temperature>.

7. Condensate-Drain Piping:  [150 deg F (66 deg C)] <Insert temperature>.

8. Blowdown-Drain Piping:  [200 deg F (93 deg C)] <Insert temperature>.

9. Air-Vent Piping:  [200 deg F (93 deg C)] <Insert temperature>.

10. Safety-Valve-Inlet and -Outlet Piping:  Equal to the pressure of the piping system to which it is attached.

1.5 SUBMITTALS

A. Product Data:  For each type of the following:

1. Plastic pipe and fittings with solvent cement.

2. RTRP and RTRF with adhesive.

3. Pressure-seal fittings.

4. Valves.  Include flow and pressure drop curves based on manufacturer's testing for calibrated-orifice balancing valves and automatic flow-control valves.

5. Air control devices.

6. Chemical treatment.

7. Hydronic specialties.

B. LEED Submittal:

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for solvent cements and adhesive primers.

1. Product Data for Credit EQ 4.1:  For solvent cements and adhesive primers, including printed statement of VOC content.

C. Shop Drawings:  Detail, at [1/4 (1:50)] <Insert scale> scale, the piping layout, fabrication of pipe anchors, hangers, supports for multiple pipes, alignment guides, expansion joints and loops, and attachments of the same to the building structure.  Detail location of anchors, alignment guides, and expansion joints and loops.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For Installer.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For air control devices, hydronic specialties, and special-duty valves to include in emergency, operation, and maintenance manuals.

Delete paragraph below if chemical treatment is specified in Division 15 Section "HVAC Water Treatment."

H. Water Analysis:  Submit a copy of the water analysis to illustrate water quality available at Project site.

1.6 QUALITY ASSURANCE

A. Installer Qualifications:

Retain subparagraph below for pressure-sealed joints in copper or steel piping.

1. Installers of Pressure-Sealed Joints:  Installers shall be certified by the pressure-seal joint manufacturer as having been trained and qualified to join piping with pressure-seal pipe couplings and fittings.

Retain subparagraph below for fiberglass pipe assembly.

2. Fiberglass Pipe and Fitting Installers:  Installers of RTRF and RTRP shall be certified by the manufacturer of pipes and fittings as having been trained and qualified to join fiberglass piping with manufacturer-recommended adhesive.

Retain first two paragraphs and associated subparagraphs below for welded supports or piping.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

B. Steel Support Welding:  Qualify processes and operators according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

C. Welding:  Qualify processes and operators according to ASME Boiler and Pressure Vessel Code:  Section IX.

1. Comply with provisions in ASME B31 Series, "Code for Pressure Piping."

2. Certify that each welder has passed AWS qualification tests for welding processes involved and that certification is current.

D. ASME Compliance:  Comply with ASME B31.9, "Building Services Piping," for materials, products, and installation.  Safety valves and pressure vessels shall bear the appropriate ASME label.  Fabricate and stamp air separators and expansion tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

Delete paragraph below if chemical-treatment systems are specified in Division 15 Section "HVAC Water Treatment."

A. Water-Treatment Chemicals:  Furnish enough chemicals for initial system startup and for preventive maintenance for one year from date of Substantial Completion.

Retain paragraph below if calibrated-orifice, balancing valves are retained in Part 2.

B. Differential Pressure Meter:  For each type of balancing valve and automatic flow control valve, include flowmeter, probes, hoses, flow charts, and carrying case.

PART 2 -  PRODUCTS

First four articles below include examples of materials listed in the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment," Chapter 41, "Pipes, Tubes, and Fittings." See "Writing Guide" Article in the Evaluations.

2.1 COPPER TUBE AND FITTINGS

Type M (C) in paragraph below is not included in Table 5, "Application of Pipe, Fittings, and Valves for Heating and Air Conditioning," in the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment."

A. Drawn-Temper Copper Tubing:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)].

Type K (A) soft temper in paragraph below is applicable for belowground installations.

B. Annealed-Temper Copper Tubing:  ASTM B 88, Type K (ASTM B 88M, Type A).

DWV tubing in first paragraph below is intended for nonpressure applications and is applicable for condensate drains.

C. DWV Copper Tubing:  ASTM B 306, Type DWV.

D. Wrought-Copper Fittings:  ASME B16.22.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Anvil International, Inc.

b. S. P. Fittings; a division of Star Pipe Products.

c. Victaulic Company of America.

d. <Insert manufacturer's name.>

Retain first subparagraph below for grooved-end fittings.

4. Grooved-End Copper Fittings:  ASTM B 75 (ASTM B 75M), copper tube or ASTM B 584, bronze casting.

5. Grooved-End-Tube Couplings:  Rigid pattern, unless otherwise indicated; gasketed fitting.  Ductile-iron housing with keys matching pipe and fitting grooves,[ prelubricated] EPDM gasket rated for minimum 230 deg F (110 deg C) for use with housing, and steel bolts and nuts.

When this Section was updated, the fittings in paragraph below were manufactured by a single manufacturer and were available for pipe sizes NPS 1/2 through NPS 4 (DN 15 through DN 100).

E. Copper or Bronze Pressure-Seal Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Stadler-Viega.

b. <Insert manufacturer's name.>

4. Housing:  Copper.

5. O-Rings and Pipe Stops:  EPDM.

6. Tools:  Manufacturer's special tools.

7. Minimum 200-psig (1379-kPa) working-pressure rating at 250 deg F (121 deg C).

When this Section was updated, the fittings in first paragraph below were manufactured by a single manufacturer and were available for pipe sizes NPS 1/2 through NPS 4 (DN 15 through DN 100).

F. Copper, Mechanically Formed Tee Option:  For forming T-branch on copper water tube.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. T-DRILL Industries Inc.

b. <Insert manufacturer's name.>

G. Wrought-Copper Unions:  ASME B16.22.

2.2 STEEL PIPE AND FITTINGS

A. Steel Pipe:  ASTM A 53/A 53M, black steel with plain ends; type, grade, and wall thickness as indicated in Part 3 "Piping Applications" Article.

B. Cast-Iron Threaded Fittings:  ASME B16.4; Classes 125 and 250 as indicated in Part 3 "Piping Applications" Article.

C. Malleable-Iron Threaded Fittings:  ASME B16.3, Classes 150 and 300 as indicated in Part 3 "Piping Applications" Article.

D. Malleable-Iron Unions:  ASME B16.39; Classes 150, 250, and 300 as indicated in Part 3 "Piping Applications" Article.

Coordinate flange class in first paragraph below with products in other parts of this Section and in related Sections to match face size and bolt patterns.

E. Cast-Iron Pipe Flanges and Flanged Fittings:  ASME B16.1, Classes 25, 125, and 250; raised ground face, and bolt holes spot faced as indicated in Part 3 "Piping Applications" Article.

F. Wrought-Steel Fittings:  ASTM A 234/A 234M, wall thickness to match adjoining pipe.

Flanges and fittings in first paragraph and subparagraphs below are available in several classes, materials, facings, and end connections.

G. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, including bolts, nuts, and gaskets of the following material group, end connections, and facings:

1. Material Group:  1.1.

2. End Connections:  Butt welding.

3. Facings:  Raised face.

H. Grooved Mechanical-Joint Fittings and Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Anvil International, Inc.

b. Central Sprinkler Company; a division of Tyco Fire & Building Products.

c. National Fittings, Inc.

d. S. P. Fittings; a division of Star Pipe Products.

e. Victaulic Company of America.

f. <Insert manufacturer's name.>

Retain first subparagraph below for grooved-end fittings.

4. Joint Fittings:  ASTM A 536, Grade 65-45-12 ductile iron; ASTM A 47/A 47M, Grade 32510 malleable iron; ASTM A 53/A 53M, Type F, E, or S, Grade B fabricated steel; or ASTM A 106, Grade B steel fittings with grooves or shoulders constructed to accept grooved-end couplings; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

5. Couplings:  Ductile- or malleable-iron housing and synthetic rubber gasket of central cavity pressure-responsive design; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

I. Steel Pressure-Seal Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Victaulic Company of America.

b. <Insert manufacturer's name.>

4. Housing:  Steel.

5. O-Rings and Pipe Stop:  EPDM.

6. Tools:  Manufacturer's special tool.

7. Minimum 300-psig (2070-kPa) working-pressure rating at 230 deg F (110 deg C).

Unreinforced, welded, in-branch connections weaken a main pipeline; reinforcement is necessary unless wall thickness of both mains and branches is sufficient to sustain pressure.

J. Steel Pipe Nipples:  ASTM A 733, made of same materials and wall thicknesses as pipe in which they are installed.

2.3 PLASTIC PIPE AND FITTINGS

See the Evaluations for discussion of product characteristics and maximum temperatures.

A. CPVC Plastic Pipe:  ASTM F 441/F 441M, Schedules 40 and 80, plain ends as indicated in Part 3 "Piping Applications" Article.

B. CPVC Plastic Pipe Fittings:  Socket-type pipe fittings, ASTM F 438 for Schedule 40 pipe; ASTM F 439 for Schedule 80 pipe.

C. PVC Plastic Pipe:  ASTM D 1785, Schedules 40 and 80, plain ends as indicated in Part 3 "Piping Applications" Article.

D. PVC Plastic Pipe Fittings:  Socket-type pipe fittings, ASTM D 2466 for Schedule 40 pipe; ASTM D 2467 for Schedule 80 pipe.

2.4 FIBERGLASS PIPE AND FITTINGS

Piping is available with ends for other types of joints.  See the Evaluations for discussion of product characteristics and maximum temperatures and pressures.

A. RTRP:  ASTM D 2996, filament-wound pipe with tapered bell and spigot ends for adhesive joints.

B. RTRF:  Compression or spray-up/contact molded of same material, pressure class, and joining method as pipe.

C. Flanges:  ASTM D 4024.  Full-face gaskets suitable for the service, minimum 1/8-inch (3.2-mm) thick, 60-70 durometer.  ASTM A 307, Grade B, hex head bolts with washers.

2.5 JOINING MATERIALS

A. Pipe-Flange Gasket Materials:  Suitable for chemical and thermal conditions of piping system contents.

1. ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

a. Full-Face Type:  For flat-face, Class 125, cast-iron and cast-bronze flanges.

b. Narrow-Face Type:  For raised-face, Class 250, cast-iron and steel flanges.

B. Flange Bolts and Nuts:  ASME B18.2.1, carbon steel, unless otherwise indicated.

C. Plastic, Pipe-Flange Gasket, Bolts, and Nuts:  Type and material recommended by piping system manufacturer, unless otherwise indicated.

See the Evaluations for discussions of solder and brazing materials described in first two paragraphs below.

D. Solder Filler Metals:  ASTM B 32, lead-free alloys.  Include water-flushable flux according to ASTM B 813.

E. Brazing Filler Metals:  AWS A5.8, BCuP Series, copper-phosphorus alloys for joining copper with copper; or BAg-1, silver alloy for joining copper with bronze or steel.

F. Welding Filler Metals:  Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

G. Solvent Cements for Joining Plastic Piping:

1. CPVC Piping:  ASTM F 493.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. Use CPVC solvent cement that has a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

b. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. PVC Piping:  ASTM D 2564.  Include primer according to ASTM F 656.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

b. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

H. Fiberglass Pipe Adhesive:  As furnished or recommended by pipe manufacturer.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use fiberglass adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

I. Gasket Material:  Thickness, material, and type suitable for fluid to be handled and working temperatures and pressures.

2.6 TRANSITION FITTINGS

A. Plastic-to-Metal Transition Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Charlotte Pipe and Foundry Company.

b. IPEX Inc.

c. KBi.

d. <Insert manufacturer's name.>

3. [CPVC] [PVC] [CPVC and PVC] one-piece fitting with one threaded brass or copper insert and one Schedule 80 solvent-cement-joint end.

B. Plastic-to-Metal Transition Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Charlotte Pipe and Foundry Company.

b. IPEX Inc.

c. KBi.

d. NIBCO INC.

e. <Insert manufacturer's name.>

3. MSS SP-107, [CPVC] [PVC] [CPVC and PVC] union.  Include brass or copper end, Schedule 80 solvent-cement-joint end, rubber gasket, and threaded union.

2.7 DIELECTRIC FITTINGS

A. Description:  Combination fitting of copper-alloy and ferrous materials with threaded, solder-joint, plain, or weld-neck end connections that match piping system materials.

B. Insulating Material:  Suitable for system fluid, pressure, and temperature.

C. Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. Hart Industries International, Inc.

d. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; AquaSpec Commercial Products Division.

f. <Insert manufacturer's name.>

Revise pressure rating and temperature in subparagraph below to suit Project, or add other options for specific applications.

3. Factory-fabricated union assembly, for 250-psig (1725-kPa) minimum working pressure at 180 deg F (82 deg C).

D. Dielectric Flanges:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

d. <Insert manufacturer's name.>

Revise pressure rating in subparagraph below to suit Project, or add other options for specific applications.

3. Factory-fabricated companion-flange assembly, for 150- or 300-psig (1035- or 2070-kPa) minimum working pressure as required to suit system pressures.

E. Dielectric-Flange Kits:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Advance Products & Systems, Inc.

b. Calpico, Inc.

c. Central Plastics Company.

d. Pipeline Seal and Insulator, Inc.

e. <Insert manufacturer's name.>

3. Companion-flange assembly for field assembly.  Include flanges, full-face- or ring-type neoprene or phenolic gasket, phenolic or polyethylene bolt sleeves, phenolic washers, and steel backing washers.

Revise pressure rating in subparagraph below to suit Project, or add other options for specific applications.

4. Separate companion flanges and steel bolts and nuts shall have 150- or 300-psig (1035- or 2070-kPa) minimum working pressure where required to suit system pressures.

F. Dielectric Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Calpico, Inc.

b. Lochinvar Corporation.

c. <Insert manufacturer's name.>

Revise pressure rating and temperature in subparagraph below to suit Project, or add other options for specific applications.

3. Galvanized-steel coupling with inert and noncorrosive thermoplastic lining; threaded ends; and 300-psig (2070-kPa) minimum working pressure at 225 deg F (107 deg C).

G. Dielectric Nipples:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Perfection Corporation; a subsidiary of American Meter Company.

b. Precision Plumbing Products, Inc.

c. Sioux Chief Manufacturing Company, Inc.

d. Victaulic Company of America.

e. <Insert manufacturer's name.>

Revise pressure rating and temperature in subparagraph below to suit Project, or add other options for specific applications.

3. Electroplated steel nipple with inert and noncorrosive, thermoplastic lining; plain, threaded, or grooved ends; and 300-psig (2070-kPa) minimum working pressure at 225 deg F (107 deg C).

2.8 VALVES

A. Gate, Globe, Check, Ball, and Butterfly Valves:  Comply with requirements specified in Division 15 Section "Valves."

B. Automatic Temperature-Control Valves, Actuators, and Sensors:  Comply with requirements specified in Division 15 Section "HVAC Instrumentation and Controls."

MSS SP-122, "Plastic Industrial Ball Valves," is a standard for plastic ball valves.  It is not comprehensive and additional data may be required for certain applications.  In general, end types and pressure and temperature ratings are required.  No applicable standards are available for plastic butterfly or check valves.  CPVC piping in this Section is rated for up to 180 deg F (82 deg C).  Verify that plastic valves are adequate for operating temperature of piping systems.

C. Plastic Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Valve, Inc.

b. Asahi/America.

c. Charlotte Pipe and Foundry Company.

d. Colonial Engineering.

e. George Fischer Inc.

f. Hayward Industrial Products, Inc.

g. IPEX Inc.

h. Jomar International Ltd.

i. KBi.

j. Legend Valve.

k. NIBCO INC.

l. Plast-O-Matic Valves, Inc.

m. SMC The Specialty Mfg. Co.

n. Thermoplastic Valves Inc.

o. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

p. <Insert manufacturer's name.>

4. Body:  One-, two-, or three-piece CPVC or PVC to match piping.

5. Ball:  Full-port CPVC or PVC to match piping.

6. Seats:  PTFE.

7. Seals:  EPDM.

8. End Connections:  Socket, union, or flanged.

9. Handle Style:  Tee shape.

10. CWP Rating:  Equal to piping service.

11. Maximum Operating Temperature:  Equal to piping service.

Not all manufacturers comply with the standard in subparagraph below.

12. Comply with MSS SP-122.

Large plastic butterfly valves may have reduced pressure ratings.

D. Plastic Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Valve, Inc.

b. Asahi/America.

c. Colonial Engineering.

d. George Fischer Inc.

e. Hayward Industrial Products, Inc.

f. IPEX Inc.

g. Legend Valve.

h. NIBCO INC.

i. Plast-O-Matic Valves, Inc.

j. SMC The Specialty Mfg. Co.

k. Thermoplastic Valves Inc.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. <Insert manufacturer's name.>

4. Body:  PVC or CPVC to match piping wafer type for installation between flanges.

5. Disc:  EPDM-coated steel.

6. Seats:  PTFE.

7. Handle Style:  Locking lever.

8. CWP Rating:  Equal to piping service.

9. Maximum Operating Temperature:  Equal to piping service.

E. Plastic Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Valve, Inc.

b. Asahi/America.

c. Colonial Engineering.

d. George Fischer Inc.

e. Hayward Industrial Products, Inc.

f. IPEX Inc.

g. KBi.

h. Legend Valve.

i. NIBCO INC.

j. Plast-O-Matic Valves, Inc.

k. SMC The Specialty Mfg. Co.

l. Thermoplastic Valves Inc.

m. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

n. <Insert manufacturer's name.>

4. Body:  One-, two-, or three-piece PVC or CPVC to match piping.

5. Ends:  Socket or flanged.

6. Seats:  PTFE.

7. Check Style:  Swing or ball type.

8. CWP Rating:  Equal to piping service.

9. Maximum Operating Temperature:  Equal to piping service.

F. Bronze, Calibrated-Orifice, Balancing Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong Pumps, Inc.

b. Bell & Gossett Domestic Pump; a division of ITT Industries.

c. Flow Design Inc.

d. Gerand Engineering Co.

e. Griswold Controls.

f. Taco.

g. <Insert manufacturer's name.>

4. Body:  Bronze, ball or plug type with calibrated orifice or venturi.

5. Ball:  Brass or stainless steel.

6. Plug:  Resin.

7. Seat:  PTFE.

8. End Connections:  Threaded or socket.

9. Pressure Gage Connections:  Integral seals for portable differential pressure meter.

10. Handle Style:  Lever, with memory stop to retain set position.

11. CWP Rating: Minimum 125 psig (860 kPa).

12. Maximum Operating Temperature:  250 deg F (121 deg C).

G. Cast-Iron or Steel, Calibrated-Orifice, Balancing Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong Pumps, Inc.

b. Bell & Gossett Domestic Pump; a division of ITT Industries.

c. Flow Design Inc.

d. Gerand Engineering Co.

e. Griswold Controls.

f. Taco.

g. Tour & Andersson; available through Victaulic Company of America.

h. <Insert manufacturer's name.>

4. Body:  Cast-iron or steel body, ball, plug, or globe pattern with calibrated orifice or venturi.

5. Ball:  Brass or stainless steel.

6. Stem Seals:  EPDM O-rings.

7. Disc:  Glass and carbon-filled PTFE.

8. Seat:  PTFE.

9. End Connections:  Flanged or grooved.

10. Pressure Gage Connections:  Integral seals for portable differential pressure meter.

11. Handle Style:  Lever, with memory stop to retain set position.

12. CWP Rating:  Minimum 125 psig (860 kPa).

13. Maximum Operating Temperature:  250 deg F (121 deg C).

H. Diaphragm-Operated, Pressure-Reducing Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. Bell & Gossett Domestic Pump; a division of ITT Industries.

d. Conbraco Industries, Inc.

e. Spence Engineering Company, Inc.

f. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

g. <Insert manufacturer's name.>

4. Body:  Bronze or brass.

5. Disc:  Glass and carbon-filled PTFE.

6. Seat:  Brass.

7. Stem Seals:  EPDM O-rings.

8. Diaphragm:  EPT.

9. Low inlet-pressure check valve.

10. Inlet Strainer: <Insert materials>, removable without system shutdown.

11. Valve Seat and Stem:  Noncorrosive.

12. Valve Size, Capacity, and Operating Pressure:  Selected to suit system in which installed, with operating pressure and capacity factory set and field adjustable.

I. Diaphragm-Operated Safety Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Amtrol, Inc.

b. Armstrong Pumps, Inc.

c. Bell & Gossett Domestic Pump; a division of ITT Industries.

d. Conbraco Industries, Inc.

e. Spence Engineering Company, Inc.

f. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

g. <Insert manufacturer's name.>

4. Body:  Bronze or brass.

5. Disc:  Glass and carbon-filled PTFE.

6. Seat:  Brass.

7. Stem Seals:  EPDM O-rings.

8. Diaphragm:  EPT.

9. Wetted, Internal Work Parts:  Brass and rubber.

10. Inlet Strainer: <Insert materials>, removable without system shutdown.

11. Valve Seat and Stem:  Noncorrosive.

12. Valve Size, Capacity, and Operating Pressure:  Comply with ASME Boiler and Pressure Vessel Code:  Section IV, and selected to suit system in which installed, with operating pressure and capacity factory set and field adjustable.

J. Automatic Flow-Control Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Flow Design Inc.

b. Griswold Controls.

c. <Insert manufacturer's name.>

4. Body:  Brass or ferrous metal.

5. Piston and Spring Assembly:  [Stainless steel] [Corrosion resistant], tamper proof, self cleaning, and removable.

6. Combination Assemblies:  Include bonze or brass-alloy ball valve.

7. Identification Tag:  Marked with zone identification, valve number, and flow rate.

8. Size:  Same as pipe in which installed.

9. Performance:  Maintain constant flow, plus or minus 5 percent over system pressure fluctuations.

10. Minimum CWP Rating:  [175 psig (1207 kPa)] [300 psig (2070 kPa)].

11. Maximum Operating Temperature:  [200 deg F (93 deg C)] [250 deg F (121 deg C)].

2.9 AIR CONTROL DEVICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Amtrol, Inc.

2. Armstrong Pumps, Inc.

3. Bell & Gossett Domestic Pump; a division of ITT Industries.

4. Taco.

5. <Insert manufacturer's name.>

Air vents aid in system filling.  Air removal after initial startup is accomplished by air separator or boiler dip-tube.

Leakage from automatic air vents may cause damage to ceilings and other finished surfaces.  Manual air vents may be preferred over automatic air vents in finished spaces.

C. Manual Air Vents:

1. Body:  Bronze.

2. Internal Parts:  Nonferrous.

3. Operator:  Screwdriver or thumbscrew.

4. Inlet Connection:  NPS 1/2 (DN 15).

5. Discharge Connection:  NPS 1/8 (DN 6).

6. CWP Rating:  150 psig (1035 kPa).

7. Maximum Operating Temperature:  225 deg F (107 deg C).

D. Automatic Air Vents:

1. Body:  Bronze or cast iron.

2. Internal Parts:  Nonferrous.

3. Operator:  Noncorrosive metal float.

4. Inlet Connection:  NPS 1/2 (DN 15).

5. Discharge Connection:  NPS 1/4 (DN 8).

6. CWP Rating:  150 psig (1035 kPa).

7. Maximum Operating Temperature:  240 deg F (116 deg C).

Retain one of two paragraphs and associated subparagraphs below to suit system capacity and space available.  Bladder- and diaphragm-type tanks can be mounted on floor.

E. Expansion Tanks:

1. Tank:  Welded steel, rated for 125-psig (860-kPa) working pressure and 375 deg F (191 deg C) maximum operating temperature, with taps in bottom of tank for tank fitting and taps in end of tank for gage glass.  Tanks shall be factory tested with taps fabricated and labeled according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

2. Air-Control Tank Fitting:  Cast-iron body, copper-plated tube, brass vent tube plug, and stainless-steel ball check, 100-gal. (379-L) unit only; sized for compression-tank diameter.  Provide tank fittings for 125-psig (860-kPa) working pressure and 250 deg F (121 deg C) maximum operating temperature.

3. Tank Drain Fitting:  Brass body, nonferrous internal parts; 125-psig (860-kPa) working pressure and 240 deg F (116 deg C) maximum operating temperature; constructed to admit air to compression tank, drain water, and close off system.

4. Gage Glass:  Full height with dual manual shutoff valves, [3/4-inch- (20-mm-)] <Insert dimension> diameter gage glass, and slotted-metal glass guard.

F. [Diaphragm] [Bladder]-Type Expansion Tanks:

1. Tank:  Welded steel, rated for 125-psig (860-kPa) working pressure and 375 deg F (191 deg C) maximum operating temperature.  Factory test with taps fabricated and supports installed and labeled according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

2. [Diaphragm] [Bladder]:  Securely sealed into tank to separate air charge from system water to maintain required expansion capacity.

3. Air-Charge Fittings:  Schrader valve, stainless steel with EPDM seats.

Retain one of three paragraphs and associated subparagraphs below to suit system capacity.

G. Tangential-Type Air Separators:

1. Tank:  Welded steel; ASME constructed and labeled for 125-psig (860-kPa) minimum working pressure and 375 deg F (191 deg C) maximum operating temperature.

2. Air Collector Tube:  Perforated stainless steel, constructed to direct released air into expansion tank.

3. Tangential Inlet and Outlet Connections:  Threaded for NPS 2 (DN 50) and smaller; flanged connections for NPS 2-1/2 (DN 65) and larger.

4. Blowdown Connection:  Threaded.

5. Size:  Match system flow capacity.

H. In-Line Air Separators:

1. Tank:  One-piece cast iron with an integral weir constructed to decelerate system flow to maximize air separation.

2. Maximum Working Pressure:  Up to 175 psig (1207 kPa).

3. Maximum Operating Temperature:  Up to 300 deg F (149 deg C).

I. Air Purgers:

1. Body:  Cast iron with internal baffles that slow the water velocity to separate the air from solution and divert it to the vent for quick removal.

2. Maximum Working Pressure:  150 psig (1035 kPa).

3. Maximum Operating Temperature:  250 deg F (121 deg C).

2.10 CHEMICAL TREATMENT

Delete this Article if chemical-treatment systems are specified in Division 15 Section "HVAC Water Treatment."

A. Bypass Chemical Feeder:  Welded steel construction; 125-psig (860-kPa) working pressure; 5-gal. (19-L) capacity; with fill funnel and inlet, outlet, and drain valves.

1. Chemicals:  Specially formulated, based on analysis of makeup water, to prevent accumulation of scale and corrosion in piping and connected equipment.

B. Ethylene and Propylene Glycol:  Industrial grade with corrosion inhibitors and environmental-stabilizer additives for mixing with water in systems indicated to contain antifreeze or glycol solutions.

2.11 HYDRONIC PIPING SPECIALTIES

A. Y-Pattern Strainers:

1. Body:  ASTM A 126, Class B, cast iron with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for NPS 2 (DN 50) and smaller; flanged ends for NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  [40] [60]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating:  125 psig (860 kPa).

B. Basket Strainers:

1. Body:  ASTM A 126, Class B, high-tensile cast iron with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for NPS 2 (DN 50) and smaller; flanged ends for NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  [40] [60]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating:  125 psig (860 kPa).

C. T-Pattern Strainers:

1. Body:  Ductile or malleable iron with removable access coupling and end cap for strainer maintenance.

2. End Connections:  Grooved ends.

3. Strainer Screen:  [40] [60]-mesh startup strainer, and perforated stainless-steel basket with 57 percent free area.

4. CWP Rating:  750 psig (5170 kPa).

Retain first paragraph and subparagraphs below for small pipe sizes.  Allow sufficient length for installation.  Where space is limited and for larger piping applications, consider using flexible joints and spherical connectors.

Combinations of grooved mechanical-joint couplings and short nipples may also be used.  Refer to Victaulic's technical information.

D. Stainless-Steel Bellow, Flexible Connectors:

1. Body:  Stainless-steel bellows with woven, flexible, bronze, wire-reinforcing protective jacket.

2. End Connections:  Threaded or flanged to match equipment connected.

3. Performance:  Capable of 3/4-inch (20-mm) misalignment.

4. CWP Rating:  150 psig (1035 kPa).

5. Maximum Operating Temperature:  250 deg F (121 deg C).

E. Spherical, Rubber, Flexible Connectors:

1. Body:  Fiber-reinforced rubber body.

2. End Connections:  Steel flanges drilled to align with Classes 150 and 300 steel flanges.

3. Performance:  Capable of misalignment.

4. CWP Rating:  150 psig (1035 kPa).

5. Maximum Operating Temperature:  250 deg F (121 deg C).

F. Expansion fittings are specified in Division 15 Section "Pipe Expansion Fittings and Loops."

PART 3 -  EXECUTION

3.1 PIPING APPLICATIONS

Retain at least one pipe material in paragraphs and subparagraphs below for each service required for Project.  Services are specified separately to allow different pipe materials and joining methods for each.  If materials and methods are the same for multiple services, combine the requirements by editing the paragraph titles.  To allow the Contractor to choose among various pipe materials, retain multiple materials for each required service and pipe size.  Pipe materials and joining methods in this Article, in general, are as listed in the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment," Chapter 41, "Pipes, Tubes, and Fittings." The change point for pipe materials and joining methods is specified, in this master, where the pipe size changes from NPS 2 to NPS 2-1/2 (DN 50 to DN 65).  Revise this change point to suit office policy.  See "Writing Guide" Article in the Evaluations.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

A. Hot-water heating piping, aboveground, [NPS 2 (DN 50) and smaller,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] joints.

2. Schedule [40] [30] [20] steel pipe; Class [125, cast-iron] [150, malleable-iron] [250, cast-iron] [300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

3. Schedule 5 steel pipe; steel, pressure-seal couplings and fittings; and pressure-seal joints.

CPVC pipe in subparagraph below has temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

B. Hot-water heating piping, aboveground, [NPS 2-1/2 (DN 65) and larger,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of five subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [30] [20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

3. Schedule [40] [30] [20] steel pipe; grooved, mechanical joint coupling and fittings; and grooved, mechanical joints.

CPVC and RTRP in two subparagraphs below have temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

5. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

C. Hot-water heating piping installed belowground and within slabs shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type K (A), annealed-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.  Use the fewest possible joints.

RTRP in subparagraph below has temperature and pressure limitations.  See Evaluations.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

D. Chilled-water piping, aboveground, [NPS 2 (DN 50) and smaller,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] joints.

2. Schedule [40] [30] [20] steel pipe; Class [125, cast-iron] [150, malleable-iron] [250, cast-iron] [300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

3. Schedule 5 steel pipe; steel, pressure-seal couplings and fittings; and pressure-seal joints.

CPVC pipe in subparagraph below has temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

E. Chilled-water piping, aboveground, [NPS 2-1/2 (DN 65) and larger,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of five subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [30] [20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

3. Schedule [40] [30] [20] steel pipe; grooved, mechanical joint coupling and fittings; and grooved, mechanical joints.

CPVC and RTRP in two subparagraphs below have temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

5. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

F. Chilled-water piping installed belowground and within slabs shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type K (A), annealed-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.  Use the fewest possible joints.

RTRP in subparagraph below has temperature and pressure limitations.  See Evaluations.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

G. Dual-temperature heating and cooling water piping, aboveground, [NPS 2 (DN 50) and smaller,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] joints.

2. Schedule [40] [30] [20] steel pipe; Class [125, cast-iron] [150, malleable-iron] [250, cast-iron] [300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

3. Schedule 5 steel pipe; steel, pressure-seal couplings and fittings; and pressure-seal joints.

CPVC pipe in subparagraph below has temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

H. Dual-temperature heating and cooling water piping, aboveground, [NPS 2-1/2 (DN 65) and larger,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of five subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [30] [20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

3. Schedule [40] [30] [20] steel pipe; grooved, mechanical joint coupling and fittings; and grooved, mechanical joints.

CPVC and RTRP in two subparagraphs below have temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

5. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

I. Dual-temperature heating and cooling water piping installed belowground and within slabs shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type K (A), annealed-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.  Use the fewest possible joints.

RTRP in subparagraph below has temperature and pressure limitations.  See Evaluations.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

J. Condenser-water piping, aboveground, [NPS 2 (DN 50) and smaller,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] joints.

2. Schedule [80] [40] [30] [20] steel pipe; Class [125, cast-iron] [150, malleable-iron] [250, cast-iron] [300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

3. Schedule 5 steel pipe; steel, pressure-seal couplings and fittings; and pressure-seal joints.

CPVC pipe in subparagraph below has temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

K. Condenser-water piping, aboveground, [NPS 2-1/2 (DN 65) and larger,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of five subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [80] [40] [30] [20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

3. Schedule [80] [40] [30] [20] steel pipe; grooved, mechanical joint coupling and fittings; and grooved, mechanical joints.

CPVC and RTRP in two subparagraphs below have temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

5. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

L. Condenser-water piping installed belowground and within slabs shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type K (A), annealed-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.  Use the fewest possible joints.

RTRP in subparagraph below has temperature and pressure limitations.  See Evaluations.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

M. Glycol cooling-water piping, aboveground, [NPS 2 (DN 50) and smaller,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of four subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] joints.

2. Schedule [40] [30] [20] steel pipe; Class [125, cast-iron] [150, malleable-iron] [250, cast-iron] [300, malleable-iron] fittings; cast-iron flanges and flange fittings; and threaded joints.

3. Schedule 5 steel pipe; steel, pressure-seal couplings and fittings; and pressure-seal joints.

CPVC pipe in subparagraph below has temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

Retain "any of" option in paragraph below to allow Contractor to select piping materials from those retained.

N. Glycol cooling-water piping, aboveground, [NPS 2-1/2 (DN 65) and larger,] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of five subparagraphs below.  If more than one type of material and joining method is retained and it is not the intent to give the Contractor the option to select materials, delete the "any of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [30] [20] steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

3. Schedule [40] [30] [20] steel pipe; grooved, mechanical joint coupling and fittings; and grooved, mechanical joints.

CPVC and RTRP in two subparagraphs below have temperature and pressure limitations.  See Evaluations.

4. Schedule [40] [80] CPVC plastic pipe and fittings and solvent-welded joints.

5. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

O. Glycol cooling-water piping installed belowground and within slabs shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type K (A), annealed-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.  Use the fewest possible joints.

RTRP in subparagraph below has temperature and pressure limitations.  See Evaluations.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in first paragraph below to allow Contractor to select piping materials from those retained.

P. Makeup-water piping installed aboveground shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Type [L (B)] [M (C)], drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [80] CPVC plastic pipe and fittings, and solvent-welded joints.

Q. Makeup-Water Piping Installed Belowground and within Slabs:  Type K (A), annealed-temper copper tubing, wrought-copper fittings, and soldered joints.  Use the fewest possible joints.

Retain one of first two paragraphs below.

R. Condensate-Drain Piping:  Type [M (C)] [DWV], drawn-temper copper tubing, wrought-copper fittings, and soldered joints[ or Schedule 40 PVC plastic pipe and fittings and solvent-welded joints].

S. Condensate-Drain Piping:  Schedule 40 PVC plastic pipe and fittings and solvent-welded joints.

T. Blowdown-Drain Piping:  Same materials and joining methods as for piping specified for the service in which blowdown drain is installed.

U. Air-Vent Piping:

1. Inlet:  Same as service where installed with metal-to-plastic transition fittings for plastic piping systems according to the piping manufacturer's written instructions.

2. Outlet:  Type K (A), annealed-temper copper tubing with soldered or flared joints.

V. Safety-Valve-Inlet and -Outlet Piping for Hot-Water Piping:  Same materials and joining methods as for piping specified for the service in which safety valve is installed with metal-to-plastic transition fittings for plastic piping systems according to the piping manufacturer's written instructions.

3.2 VALVE APPLICATIONS

A. Install shutoff-duty valves at each branch connection to supply mains, and at supply connection to each piece of equipment.

B. Install [throttling-duty] [calibrated-orifice, balancing] valves at each branch connection to return main.

C. Install calibrated-orifice, balancing valves in the return pipe of each heating or cooling terminal.

D. Install check valves at each pump discharge and elsewhere as required to control flow direction.

E. Install safety valves at hot-water generators and elsewhere as required by ASME Boiler and Pressure Vessel Code.  Install drip-pan elbow on safety-valve outlet and pipe without valves to the outdoors; and pipe drain to nearest floor drain or as indicated on Drawings.  Comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, for installation requirements.

F. Install pressure-reducing valves at makeup-water connection to regulate system fill pressure.

3.3 PIPING INSTALLATIONS

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicate piping locations and arrangements if such were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.

C. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

D. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

E. Install piping to permit valve servicing.

F. Install piping at indicated slopes.

G. Install piping free of sags and bends.

H. Install fittings for changes in direction and branch connections.

I. Install piping to allow application of insulation.

J. Select system components with pressure rating equal to or greater than system operating pressure.

K. Install groups of pipes parallel to each other, spaced to permit applying insulation and servicing of valves.

L. Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

M. Install piping at a uniform grade of 0.2 percent upward in direction of flow.

N. Reduce pipe sizes using eccentric reducer fitting installed with level side up.

O. Install branch connections to mains using [mechanically formed] tee fittings in main pipe, with the branch connected to the bottom of the main pipe.  For up-feed risers, connect the branch to the top of the main pipe.

P. Install valves according to Division 15 Section "Valves."

Q. Install unions in piping, NPS 2 (DN 50) and smaller, adjacent to valves, at final connections of equipment, and elsewhere as indicated.

R. Install flanges in piping, NPS 2-1/2 (DN 65) and larger, at final connections of equipment and elsewhere as indicated.

S. Install strainers on inlet side of each control valve, pressure-reducing valve, solenoid valve, in-line pump, and elsewhere as indicated.  Install NPS 3/4 (DN 20) nipple and ball valve in blowdown connection of strainers NPS 2 (DN 50) and larger.  Match size of strainer blowoff connection for strainers smaller than NPS 2 (DN 50).

T. Install expansion loops, expansion joints, anchors, and pipe alignment guides as specified in Division 15 Section "Pipe Expansion Fittings and Loops."

U. Identify piping as specified in Division 15 Section "Mechanical Identification."

3.4 HANGERS AND SUPPORTS

Piping support must account for expansion and contraction, vibration, dead load of piping and its contents, and seismic-bracing requirements.

A. Hanger, support, and anchor devices are specified in Division 15 Section "Hangers and Supports." Comply with the following requirements for maximum spacing of supports.

Retain first paragraph below for projects in areas that require seismic restraints.

B. Seismic restraints are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

C. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal piping less than 20 feet (6 m) long.

2. Adjustable roller hangers and spring hangers for individual horizontal piping 20 feet (6 m) or longer.

3. Pipe Roller:  MSS SP-58, Type 44 for multiple horizontal piping 20 feet (6 m) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

5. Provide copper-clad hangers and supports for hangers and supports in direct contact with copper pipe.

6. On plastic pipe, install pads or cushions on bearing surfaces to prevent hanger from scratching pipe.

Verify actual supported loads for hanger sizes and spacing.  Consult structural engineer.  Spacing and sizes are from the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment."

D. Install hangers for steel piping with the following maximum spacing and minimum rod sizes:

1. NPS 3/4 (DN 20):  Maximum span, 7 feet (2.1 m); minimum rod size, 1/4 inch (6.4 mm).

2. NPS 1 (DN 25):  Maximum span, 7 feet (2.1 m); minimum rod size, 1/4 inch (6.4 mm).

3. NPS 1-1/2 (DN 40):  Maximum span, 9 feet (2.7 m); minimum rod size, 3/8 inch (10 mm).

4. NPS 2 (DN 50):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

5. NPS 2-1/2 (DN 65):  Maximum span, 11 feet (3.4 m); minimum rod size, 3/8 inch (10 mm).

6. NPS 3 (DN 80):  Maximum span, 12 feet (3.7 m); minimum rod size, 3/8 inch (10 mm).

7. NPS 4 (DN 100):  Maximum span, 14 feet (4.3 m); minimum rod size, 1/2 inch (13 mm).

8. NPS 6 (DN 150):  Maximum span, 17 feet (5.2 m); minimum rod size, 1/2 inch (13 mm).

9. NPS 8 (DN 200):  Maximum span, 19 feet (5.8 m); minimum rod size, 5/8 inch (16 mm).

10. NPS 10 (DN 250):  Maximum span, 20 feet (6.1 m); minimum rod size, 3/4 inch (19 mm).

11. NPS 12 (DN 300):  Maximum span, 23 feet (7 m); minimum rod size, 7/8 inch (22 mm).

12. NPS 14 (DN 350):  Maximum span, 25 feet (7.6 m); minimum rod size, 1 inch (25 mm).

13. NPS 16 (DN 400):  Maximum span, 27 feet (8.2 m); minimum rod size, 1 inch (25 mm).

14. NPS 18 (DN 450):  Maximum span, 28 feet (8.5 m); minimum rod size, 1-1/4 inches (32 mm).

15. NPS 20 (DN 500):  Maximum span, 30 feet (9.1 m); minimum rod size, 1-1/4 inches (32 mm).

E. Install hangers for drawn-temper copper piping with the following maximum spacing and minimum rod sizes:

1. NPS 3/4 (DN 20):  Maximum span, 5 feet (1.5 m); minimum rod size, 1/4 inch (6.4 mm).

2. NPS 1 (DN 25):  Maximum span, 6 feet (1.8 m); minimum rod size, 1/4 inch (6.4 mm).

3. NPS 1-1/2 (DN 40):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

4. NPS 2 (DN 50):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

5. NPS 2-1/2 (DN 65):  Maximum span, 9 feet (2.7 m); minimum rod size, 3/8 inch (10 mm).

6. NPS 3 (DN 80):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

F. Plastic Piping Hanger Spacing:  Space hangers according to pipe manufacturer's written instructions for service conditions.  Avoid point loading.  Space and install hangers with the fewest practical rigid anchor points.

G. Fiberglass Piping Hanger Spacing:  Space hangers according to pipe manufacturer's written instructions for service conditions.  Avoid point loading.  Space and install hangers with the fewest practical rigid anchor points.

H. Support vertical runs at roof, at each floor, and at 10-foot (3-m) intervals between floors.

3.5 PIPE JOINT CONSTRUCTION

A. Join pipe and fittings according to the following requirements and Division 15 Sections specifying piping systems.

B. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

C. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

D. Soldered Joints:  Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube end.  Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.

E. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8.

F. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

G. Welded Joints:  Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators according to Part 1 "Quality Assurance" Article.

H. Flanged Joints:  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Use suitable lubricants on bolt threads.

I. Plastic Piping Solvent-Cemented Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

1. Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

2. CPVC Piping:  Join according to ASTM D 2846/D 2846M Appendix.

3. PVC Pressure Piping:  Join ASTM D 1785 schedule number, PVC pipe and PVC socket fittings according to ASTM D 2672.  Join other-than-schedule number PVC pipe and socket fittings according to ASTM D 2855.

4. PVC Nonpressure Piping:  Join according to ASTM D 2855.

J. Fiberglass Bonded Joints:  Prepare pipe ends and fittings, apply adhesive, and join according to pipe manufacturer's written instructions.

Retain paragraph below for grooved-end pipe couplings for copper or steel pipe.

K. Grooved Joints:  Assemble joints with coupling and gasket, lubricant, and bolts.  Cut or roll grooves in ends of pipe based on pipe and coupling manufacturer's written instructions for pipe wall thickness.  Use grooved-end fittings and rigid, grooved-end-pipe couplings.

Retain paragraph below for mechanically formed outlets in place of tee fittings in copper pipe.

L. Mechanically Formed, Copper-Tube-Outlet Joints:  Use manufacturer-recommended tool and procedure, and brazed joints.

Retain paragraph below for pressure-sealed joints in copper or steel piping.

M. Pressure-Sealed Joints:  Use manufacturer-recommended tool and procedure.  Leave insertion marks on pipe after assembly.

3.6 HYDRONIC SPECIALTIES INSTALLATION

Retain one of first two paragraphs below.  Leakage from automatic air vents may cause damage to ceilings and other finished surfaces.  Air vents aid in system filling.  Air removal after initial startup is accomplished by air separator or boiler dip-tube.  Manual air vents may be a better solution.

A. Install manual air vents at high points in piping, at heat-transfer coils, and elsewhere as required for system air venting.

B. Install automatic air vents at high points of system piping in mechanical equipment rooms only.  Manual vents at heat-transfer coils and elsewhere as required for air venting.

C. Install piping from boiler air outlet, air separator, or air purger to expansion tank with a 2 percent upward slope toward tank.

Retain one of two paragraphs below according to air separator specified in Part 2.

D. Install in-line air separators in pump suction.  Install drain valve on air separators NPS 2 (DN 50) and larger.

E. Install tangential air separator in pump suction.  Install blowdown piping with gate or full-port ball valve; extend full size to nearest floor drain.

Delete paragraph below if Division 15 Section "HVAC Water Treatment" is used.  Coordinate floor drain location for equipment drain near feeder.

F. Install bypass chemical feeders in each hydronic system where indicated, in upright position with top of funnel not more than 48 inches (1200 mm) above the floor.  Install feeder in minimum NPS 3/4 (DN 20) bypass line, from main with full-size, full-port, ball valve in the main between bypass connections.  Install NPS 3/4 (DN 20) pipe from chemical feeder drain, to nearest equipment drain and include a full-size, full-port, ball valve.

Retain one of two paragraphs and associated subparagraphs below.

G. Install expansion tanks above the air separator.  Install tank fitting in tank bottom and charge tank.  Use manual vent for initial fill to establish proper water level in tank.

1. Install tank fittings that are shipped loose.

2. Support tank from floor or structure above with sufficient strength to carry weight of tank, piping connections, fittings, plus tank full of water.  Do not overload building components and structural members.

H. Install expansion tanks on the floor.  Vent and purge air from hydronic system, and ensure tank is properly charged with air to suit system Project requirements.

3.7 TERMINAL EQUIPMENT CONNECTIONS

A. Sizes for supply and return piping connections shall be the same as or larger than equipment connections.

B. Install control valves in accessible locations close to connected equipment.

C. Install bypass piping with globe valve around control valve.  If parallel control valves are installed, only one bypass is required.

D. Install ports for pressure gages and thermometers at coil inlet and outlet connections according to Division 15 Section "Meters and Gages."

3.8 CHEMICAL TREATMENT

Delete this Article if Division 15 Section "HVAC Water Treatment" is used.

Delete first paragraph and subparagraphs below if water analysis has been or will be conducted by Owner.

A. Perform an analysis of makeup water to determine type and quantities of chemical treatment needed to keep system free of scale, corrosion, and fouling, and to sustain the following water characteristics:

Consult water-treatment specialist and insert, in subparagraphs below, specific values required for Project.

1. pH:  [9.0 to 10.5] <Insert pH>.

2. "P" Alkalinity:  [100 to 500 ppm] <Insert range>.

3. Boron:  [100 to 200 ppm] <Insert range>.

4. Chemical Oxygen Demand:  Maximum [100 ppm] <Insert value>.  Modify this value if closed system contains glycol.

5. Corrosion Inhibitor:

Retain one of first five subparagraphs below.

a. Sodium Nitrate:  [1000 to 1500 ppm] <Insert range>.

b. Molybdate:  [200 to 300 ppm] <Insert range>.

c. Chromate:  [200 to 300 ppm] <Insert range>.

d. Sodium Nitrate Plus Molybdate:  [100 to 200 ppm] <Insert range> each.

e. Chromate Plus Molybdate:  [50 to 100 ppm] <Insert range> each.

6. Soluble Copper:  Maximum [0.20 ppm] <Insert value>.

7. Tolyiriazole Copper and Yellow Metal Corrosion Inhibitor:  Minimum [10 ppm] <Insert value>.

8. Total Suspended Solids:  Maximum [10 ppm] <Insert value>.

9. Ammonia:  Maximum [20 ppm] <Insert value>.

10. Free Caustic Alkalinity:  Maximum [20 ppm] <Insert value>.

11. Microbiological Limits:

a. Total Aerobic Plate Count:  Maximum [1000] <Insert number> organisms/ml.

b. Total Anaerobic Plate Count:  Maximum [100] <Insert number> organisms/ml.

c. Nitrate Reducers:  [100] <Insert number> organisms/ml.

d. Sulfate Reducers:  Maximum [0] <Insert number> organisms/ml.

e. Iron Bacteria:  Maximum [0] <Insert number> organisms/ml.

12. <Insert other requirements if necessary.>

B. Fill system with fresh water and add liquid alkaline compound with emulsifying agents and detergents to remove grease and petroleum products from piping.  Circulate solution for a minimum of 24 hours, drain, clean strainer screens, and refill with fresh water.

C. Add initial chemical treatment and maintain water quality in ranges noted above for the first year of operation.

D. Fill systems indicated to have antifreeze or glycol solutions with the following concentrations:

1. Hot-Water Heating Piping:  Minimum <Insert number> percent [ethylene] [propylene] glycol.

2. Chilled-Water Piping:  Minimum <Insert number> percent [ethylene] [propylene] glycol.

3. Dual-Temperature Heating and Cooling Water Piping:  Minimum <Insert number> percent [ethylene] [propylene] glycol.

4. Glycol Cooling-Water Piping:  Minimum <Insert number> percent [ethylene] [propylene] glycol.

3.9 FIELD QUALITY CONTROL

A. Prepare hydronic piping according to ASME B31.9 and as follows:

1. Leave joints, including welds, uninsulated and exposed for examination during test.

2. Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure.  If temporary restraints are impractical, isolate expansion joints from testing.

3. Flush hydronic piping systems with clean water; then remove and clean or replace strainer screens.

4. Isolate equipment from piping.  If a valve is used to isolate equipment, its closure shall be capable of sealing against test pressure without damage to valve.  Install blinds in flanged joints to isolate equipment.

5. Install safety valve, set at a pressure no more than one-third higher than test pressure, to protect against damage by expanding liquid or other source of overpressure during test.

B. Perform the following tests on hydronic piping:

Procedures in subparagraphs below are paraphrased from ASME B31.9.

1. Use ambient temperature water as a testing medium unless there is risk of damage due to freezing.  Another liquid that is safe for workers and compatible with piping may be used.

2. While filling system, use vents installed at high points of system to release air.  Use drains installed at low points for complete draining of test liquid.

3. Isolate expansion tanks and determine that hydronic system is full of water.

4. Subject piping system to hydrostatic test pressure that is not less than 1.5 times the system's working pressure.  Test pressure shall not exceed maximum pressure for any vessel, pump, valve, or other component in system under test.  Verify that stress due to pressure at bottom of vertical runs does not exceed 90 percent of specified minimum yield strength or 1.7 times "SE" value in Appendix A in ASME B31.9, "Building Services Piping."

5. After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage.  Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.

6. Prepare written report of testing.

C. Perform the following before operating the system:

1. Open manual valves fully.

2. Inspect pumps for proper rotation.

3. Set makeup pressure-reducing valves for required system pressure.

4. Inspect air vents at high points of system and determine if all are installed and operating freely (automatic type), or bleed air completely (manual type).

5. Set temperature controls so all coils are calling for full flow.

6. Inspect and set operating temperatures of hydronic equipment, such as boilers, chillers, cooling towers, to specified values.

7. Verify lubrication of motors and bearings.

END OF SECTION 15181END OF SECTION 15181

HYDRONIC PIPING
15181 - 1

