Copyright 2002 AIA
MASTERSPEC
06/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 15186 - STEAM CONDENSATE PUMPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes [electric-driven] [pressure-powered] steam condensate pumps.

1.3 SUBMITTALS

A. Product Data:  Include certified performance curves and rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.  Indicate pump's operating point on curves.  Include receiver capacity and material.

B. Shop Drawings:  Show pump layout and connections.  Include setting drawings with templates for installing foundation and anchor bolts and other anchorages.

Retain subparagraph below for electric-driven steam condensate pumps.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Operation and Maintenance Data:  For pumps to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain steam condensate pumps through one source from a single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of steam condensate pumps and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. ASME Compliance:  Fabricate and label steam condensate pumps to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Manufacturer's Preparation for Shipping:  Clean flanges and exposed machined metal surfaces and treat with anticorrosion compound after assembly and testing.  Protect flanges, pipe openings, and nozzles with wooden flange covers or with screwed-in plugs.

B. Store steam condensate pumps in dry location.

C. Retain protective covers for flanges and protective coatings during storage.

D. Protect bearings and couplings against damage from sand, grit, and other foreign matter.

E. Comply with pump manufacturer's written rigging instructions.

1.6 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 ELECTRIC-DRIVEN STEAM CONDENSATE PUMPS

A. Description:  Factory-fabricated, packaged, electric-driven pumps; with receiver, pump(s), controls, and accessories suitable for operation with steam condensate.

Retain one or more of five paragraphs and associated subparagraphs below.  Retain first paragraph and associated subparagraphs for small simplex or duplex pumps with 12,000-sq. ft. EDR (845-kW) maximum capacity and up to 20-psig (140-kPa) discharge pressure.

B. Configuration:  [Simplex] [Duplex] floor-mounting pump with receiver and float switch(es); rated to pump 200 deg F (93 deg C) steam condensate.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

b. Aurora Pump; Division of Pentair Pump Group.

c. Domestic Pump; Div. of ITT Industries.

d. MEPCO (Marshall Engineered Products Co.).

e. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

f. Pentair Pump Group.

g. Roth Pump Company.

h. Skidmore Div.; Vent-Rite Valve Corp.

i. Spence Engineering Company, Inc.; Division of Circor International, Inc.

j. Spirax Sarco, Inc.

k. Sterling, Inc.

l. <Insert manufacturer's name.>

2. Receiver:  Floor-mounting, [close-grained cast iron] [welded steel] [close-grained cast iron or welded steel]; with externally adjustable float switch(es), and flange(s) for pump mounting.

3. Pump(s):  Centrifugal, close coupled, vertical design, permanently aligned, and bronze fitted; with replaceable bronze case ring and mechanical seal; mounted on receiver flange.

4. Factory Wiring:  Between pump(s) and float switch(es), for single external electrical connection.  Fused control power transformer if voltage exceeds 230 V.

Retain subparagraph below for duplex units.

5. [Electrical] [Mechanical] pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate if the normal start level for a single pump is exceeded.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

6. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

4) Speed:  <Insert rpm.>

5) Motor Horsepower:  <Insert value.>

c. Receiver:

1) Capacity:  <Insert gal. (L).>

2) Inlet Size:  <Insert NPS (DN).>

3) Height to Inlet:  <Insert inches (mm).>

d. Electrical Characteristics:

Power supply to this pump includes controls.

1) Volts:  [120] [230] [240] <Insert value>.

2) Phase:  Single.

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

Retain paragraph and subparagraphs below for small, duplex, turbine pumps with 12,000-sq. ft. EDR (845-kW) maximum capacity and up to 20-psig (140-kPa) discharge pressure.

C. Configuration:  Duplex floor-mounting pump with receiver and float switches; rated to pump 210 deg F (99 deg C) steam condensate.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

b. Aurora Pump; Division of Pentair Pump Group.

c. Domestic Pump; Div. of ITT Industries.

d. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

e. Roth Pump Company.

f. Skidmore Div.; Vent-Rite Valve Corp.

g. Spence Engineering Company, Inc.; Division of Circor International, Inc.

h. Spirax Sarco, Inc.

i. Sterling, Inc.

j. <Insert manufacturer's name.>

Stainless-steel and plastic receivers are available from some manufacturers.

2. Receiver:  Floor-mounting, [close-grained cast iron] [welded steel] [close-grained cast iron or welded steel] <Insert material>; with externally adjustable float switches and flanges for pump mounting.

3. Pumps:  Regenerative turbine, close coupled, permanently aligned, and bronze fitted; with mechanical seals and an independent pump control circuit for each pump; mounted on base or receiver flange; rated to operate with a minimum of 2 feet (6 kPa) of NPSH.

4. Factory Wiring:  Between pumps and float switches, for single external electrical connection.  Fused control power transformer if voltage exceeds 230 V.

5. [Electrical] [Mechanical] pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate if the normal start level for a single pump is exceeded.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

6. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

4) Speed:  <Insert rpm.>

5) Motor Horsepower:  <Insert value.>

c. Receiver:

1) Capacity:  <Insert gal. (L).>

2) Inlet Size:  <Insert NPS (DN).>

3) Height to Inlet:  <Insert inches (mm).>

d. Electrical Characteristics:

Power supply to this pump includes controls.

1) Volts:  [120] [230] [240] <Insert value>.

2) Phase:  Single.

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

Retain paragraph and subparagraphs below for large, duplex, receiver-mounted pumps with approximately 150,000-sq. ft. EDR (10 545-kW) maximum capacity and up to 75-psig (520-kPa) discharge pressure.

D. Configuration:  Duplex floor-mounting pumps with receiver and float switches; rated to pump minimum [200 deg F (93 deg C)] [210 deg F (99 deg C)] steam condensate.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

b. Aurora Pump; Division of Pentair Pump Group.

c. Domestic Pump; Div. of ITT Industries.

d. MEPCO (Marshall Engineered Products Co.).

e. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

f. Pentair Pump Group.

g. Roth Pump Company.

h. Skidmore Div.; Vent-Rite Valve Corp.

i. Spence Engineering Company, Inc.; Division of Circor International, Inc.

j. Spirax Sarco, Inc.

k. Sterling, Inc.

l. <Insert manufacturer's name.>

2. Receiver:  Floor-mounting, [close-grained cast iron] [welded steel] [close-grained cast iron or welded steel]; externally adjustable float switches; with water-level gage, steam condensate thermometer, discharge-pressure gage for each pump, bronze gate valves between receiver and pumps, flanges for pump mounting, and lifting eyebolts.

3. Inlet Strainer:  Cast iron with self-cleaning bronze screen, dirt pocket, and cleanout plug on receiver inlet.

Retain option in first subparagraph below if requiring 210 deg F (99 deg C) rating.

4. Pumps:  Centrifugal, close coupled, vertical design, permanently aligned, and bronze fitted; with replaceable bronze case rings, stainless-steel shafts, and mechanical seals; mounted on receiver flanges[; rated to operate with a minimum of 2 feet (6 kPa) of NPSH].

5. Control Panel:  NEMA 250, Type [1] [2] [12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump; factory wired for single external electrical connection; and with the following components within cabinet:

a. Motor controller for each pump.

b. Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

c. Manual lead-lag control to override electrical pump alternator to manually select the lead pump.

d. Momentary contact "TEST" push button on cover for each pump.

e. Numbered terminal strip.

f. Disconnect switch.

Retain subparagraph below for pumps with more than 230 V or if otherwise required.

g. Fused transformer for control circuit.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

6. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

4) Speed:  <Insert rpm.>

5) Motor Horsepower:  <Insert value.>

c. Receiver:

1) Capacity:  <Insert gal. (L).>

2) Inlet Size:  <Insert NPS (DN).>

3) Height to Inlet:  <Insert inches (mm).>

d. Electrical Characteristics:

1) Volts:  [120] [208] [230] [240] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

Retain paragraph and subparagraphs below for large duplex pumps with elevated receiver and with approximately 150,000-sq. ft. EDR (10 545-kW) maximum capacity and up to 75-psig (520-kPa) discharge pressure.

E. Configuration:  Duplex floor-mounting pump with elevated receiver, float switches, and connecting piping; rated to pump 212 deg F (100 deg C) steam condensate.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

b. Aurora Pump; Division of Pentair Pump Group.

c. Domestic Pump; Div. of ITT Industries.

d. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

e. Roth Pump Company.

f. Skidmore Div.; Vent-Rite Valve Corp.

g. Spence Engineering Company, Inc.; Division of Circor International, Inc.

h. Spirax Sarco, Inc.

i. <Insert manufacturer's name.>

2. Receiver:  [Close-grained cast iron] [Welded steel] [Close-grained cast iron or welded steel], mounted on fabricated-steel supports; externally adjustable float switches; with water-level gage, steam condensate thermometer, pump discharge pressure gages, bronze isolation valves between receiver and pumps, and lifting eyebolts.

3. Inlet Strainer:  Cast iron with self-cleaning bronze screen, dirt pocket, and cleanout plug on receiver inlet.

4. Pumps:  Centrifugal, close coupled, permanently aligned, and bronze fitted; with replaceable bronze case rings, stainless-steel shafts, and mechanical seals; mounted on base below receiver; rated to operate with a minimum of 2 feet (6 kPa) of NPSH.

Revise or delete first three subparagraphs below to suit Project.

5. Pipe:  ASTM A 53/A 53M, Type S, Grade B or ASTM A 106; Schedule 80; seamless steel.

6. Fittings NPS 2 (DN 50) and Smaller:  ASME B16.1, Class 125 cast iron, threaded.

7. Fittings NPS 2-1/2 (DN 65) and Larger:  ASTM A 234/A 234M, steel, for welded connections.

8. Control Panel:  NEMA 250, Type [1] [2] [12] <Insert type> enclosure with hinged door and grounding lug; mounted on pump; factory wired for single external electrical connection; and with the following components within cabinet:

a. Motor controller for each pump.

b. Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

c. Manual lead-lag control to override electrical alternator to manually select the lead pump.

d. Momentary contact "TEST" push button on cover for each pump.

e. Numbered terminal strip.

f. Disconnect switch.

Retain subparagraph below for pumps with more than 230 V or if otherwise required.

g. Fused transformer for control circuit.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

9. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

4) Speed:  <Insert rpm.>

5) Motor Horsepower:  <Insert value.>

c. Receiver:

1) Capacity:  <Insert gal. (L).>

2) Inlet Size:  <Insert NPS (DN).>

3) Height to Inlet:  <Insert inches (mm).>

d. Electrical Characteristics:

1) Volts:  [120] [208] [230] [240] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

Retain paragraph and subparagraphs below for underground duplex pumps.  Coordinate basin dimensions, inlet size, and location on Drawings.

F. Configuration:  Underground duplex pump with basin and float switches; rated to pump 200 deg F (93 deg C) steam condensate.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company; Div. of Hannmann Machinery Systems, Inc.

b. Aurora Pump; Division of Pentair Pump Group.

c. Domestic Pump; Div. of ITT Industries.

d. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

e. Roth Pump Company.

f. Skidmore Div.; Vent-Rite Valve Corp.

g. Spence Engineering Company, Inc.; Division of Circor International, Inc.

h. Spirax Sarco, Inc.

i. <Insert manufacturer's name.>

2. Basin:  Cast iron, with hub-type inlets.

3. Basin Cover:  Cast iron or steel with gasketed openings for access, pumps, pump shafts, control rods, discharge piping, and vent connections.

Retain flange below where required to anchor basin to concrete slab if there is a ground-water problem.

a. Anchor Flange:  Cast iron, attached to basin, in location and of size required to anchor basin to concrete slab.

4. Pumps:  Wet-pit mounted, vertical, flexible coupled, and suspended.

a. Casing:  Cast iron with open inlet.

b. Shaft and Bearings:  Stainless-steel shaft with oil-lubricated, bronze, intermediate sleeve bearings; 48-inch (1200-mm) maximum intervals where basin depth is more than 48 inches (1200 mm); and grease-lubricated, ball-type, thrust bearings.

c. Shaft Couplings:  Flexible, capable of absorbing vibration.

d. Seals:  Mechanical; with carbon rotating ring, bearing on a ceramic seat held by a stainless-steel spring, and enclosed by a flexible bellows and gasket.

e. Motors:  Vertically mounted on cast-iron pedestal.

f. Pump Discharge Piping:  Manufacturer's standard steel or bronze pipe, unless otherwise indicated.

5. Control Panel:  NEMA 250, Type [1] [2] [12] <Insert type> enclosure with hinged door and grounding lug; mounted on pump; factory wired for single external electrical connection; and with the following components within cabinet:

a. Motor controller for each pump.

b. Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

c. Manual lead-lag control to override electrical alternator to manually select the lead pump.

d. Momentary contact "TEST" push button on cover for each pump.

e. Numbered terminal strip.

f. Disconnect switch.

Retain subparagraph below for pumps with more than 230 V or if otherwise required.

g. Fused transformer for control circuit.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

6. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

4) Speed:  <Insert rpm.>

5) Motor Horsepower:  <Insert value.>

c. Underground Basin:

1) Diameter:  <Insert inches (mm).>

2) Depth:  <Insert inches (mm).>

3) Inlet Size:  <Insert NPS (DN).>

4) Bottom to Centerline of Inlet:  <Insert inches (mm).>

d. Electrical Characteristics:

1) Volts:  [120] [208] [230] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

2.3 PRESSURE-POWERED STEAM CONDENSATE PUMPS

Steam, compressed air, or other operating medium under pressure is required for these pumps.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Armstrong Fluid Handling; Div. of Armstrong International, Inc.

2. MEPCO (Marshall Engineered Products Co.).

3. Nicholson Steam Trap; a division of Spence Engineering Company, Inc.

4. Spence Engineering Company, Inc.; Division of Circor International, Inc.

5. Spirax Sarco, Inc.

6. <Insert manufacturer's name.>

B. Description:  Factory-fabricated, pressure-powered pumps with mechanical controls, valves, piping connections, and accessories suitable for pumping steam condensate using [steam] [compressed air].

C. Configuration:  [Simplex] [Duplex] pump with float-operated valve control.

1. Pump Body:  [Cast iron] [Welded steel].

2. Piping Connections:  Threaded; for steam condensate, operating medium, vent, and indicated accessories.

3. Level Gage:  Glass site gage with shutoff cocks.

4. Valves:  Manufacturer's standard check valves on inlet and outlet.

5. Internal Parts:  Stainless-steel float, springs, and actuating mechanism.

6. Valve Seals:  Replaceable from exterior.

Retain subparagraph below for pumps with receiver.  Choose material or allow option for either material.

7. Receiver:  [Cast iron] [Welded steel] [Cast iron or welded steel], factory mounted on steel supports; with water-level site glass and threaded piping connections.

Retain two subparagraphs below for duplex pumps or for simplex pumps with receiver.

8. Pipe:  ASTM A 53/A 53M, Type S, Grade B or ASTM A 106; Schedule 80; seamless steel.

9. Fittings:  ASME B16.1, Class 125 cast iron, threaded.

If Project has more than one pump, delete subparagraph and associated subparagraphs below and schedule pumps on Drawings.

10. Capacities and Characteristics:

a. Unit Capacity with Single Pump Operation:  <Insert sq. ft. EDR (kW).>

b. Capacity, Each Pump:

1) Flow:  <Insert gpm (L/s).>

2) Discharge Head:  <Insert psig (kPa).>

3) Discharge Size:  <Insert NPS (DN).>

c. Operating Steam Pressure:  <Insert psig (kPa).>

d. Steam Consumption Rate:  <Insert lb/1000 lb (kg/1000 kg)> of steam condensate.

Retain last two subparagraphs above for steam-powered pumps or first two subparagraphs below for compressed-air-powered pumps.

e. Operating Compressed-Air Pressure:  <Insert psig (kPa).>

f. Compressed-Air Consumption Rate:  <Insert cu. ft./1000 lb (L/1000 kg)> of steam condensate.

g. Receiver:

1) Capacity:  <Insert gal (L).>

2) Inlet Size:  <Insert NPS (DN).>

3) Height to Inlet:  <Insert inches (mm).>

2.4 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors."  If different characteristics are required, add paragraphs below to suit Project.

A. Comply with requirements in Division 15 Section "Motors."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation tolerances and other conditions affecting performance of work.

B. Examine rough installation of steam condensate piping.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Delete first paragraph below for pressure-powered steam condensate pumps.

A. Install pumps according to HI 1.1-1.5, "Centrifugal Pumps for Nomenclature, Definitions, Application and Operation."

B. Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

C. Support pumps and piping separately so piping is not supported by pumps.

D. Install pumps on concrete bases.  Anchor pumps to bases using inserts or anchor bolts.

E. Install thermometers and pressure gages.

3.3 CONNECTIONS

Coordinate piping installation and specialty arrangement requirements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

Retain three paragraphs below for pressure-powered pump systems.

C. Install steam supply for pressure-powered pumps as required by Division 15 Section "Steam and Condensate Piping."

D. Install compressed-air supply for pressure-powered pumps as required by Division 15 Section "General-Service Compressed-Air Piping."

E. Install gate and check valves on inlet and outlet of pressure-powered pumps.

Retain first paragraph below for electric-driven pump systems.

F. Install check valve, gate valve, and globe valve at pump discharge connections for each electric-driven pump.

G. Pipe drain to nearest floor drain for overflow and drain piping connections.

H. Install full-size vent piping to outdoors, terminating in 180-degree elbow at point above highest steam system connection or as indicated.

I. Ground equipment according to Division 16 Section "Grounding and Bonding."

J. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 STARTUP SERVICE

A. Verify that steam condensate pumps are installed and connected according to the Contract Documents.

B. Complete installation and startup checks according to manufacturer's written instructions.

C. Clean strainers.

D. Set steam condensate pump controls.

E. Set pump controls for automatic start, stop, and alarm operation.

F. Perform the following preventive maintenance operations and checks before starting:

1. Set float switches to operate at proper levels.

2. Set throttling valves on pump discharge for specified flow.

3. Check motors for proper rotation.

4. Test pump controls and demonstrate compliance with requirements.

5. Replace damaged or malfunctioning pump controls and equipment.

6. Verify that pump controls are correct for required application.

G. Start steam condensate pumps according to manufacturer's written startup instructions.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain steam condensate pumps.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15186

STEAM CONDENSATE PUMPS
15186 - 13

