Copyright 2005 AIA
MASTERSPEC
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15251 - GENERAL-SERVICE PACKAGED AIR COMPRESSORS AND RECEIVERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Lubricated, reciprocating air compressors.

2. Oil-free, reciprocating air compressors.

3. Oilless, reciprocating air compressors.

4. Oil-free, rotary-screw air compressors.

5. Oil-flooded, rotary-screw air compressors.

6. Oil-free, rotary, sliding-vane air compressors.

7. Oil-sealed, rotary, sliding-vane air compressors.

8. Inlet-air filters.

9. Air-cooled, compressed-air aftercoolers.

10. Water-cooled, compressed-air aftercoolers.

11. Refrigerant compressed-air dryers.

12. Desiccant compressed-air dryers.

13. Computer interface cabinet.

1.3 DEFINITIONS

Retain definitions remaining after this Section has been edited.

A. Actual Air:  Air delivered from air compressors.  Flow rate is delivered compressed air measured in acfm (actual L/s).

B. Low Voltage:  As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

C. Standard Air:  Free air at 68 deg F (20 deg C) and 1 atmosphere (29.92 in. Hg) before compression or expansion and measured in scfm (standard L/s).

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design compressed-air equipment mounting, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain paragraph below with "Delegated-Design Submittal" Paragraph in "Submittals" Article if Project requires seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

B. Seismic Performance:  Compressed-air equipment shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First paragraph below is defined in Division 1 Section "Submittal Procedures" as an "Action Submittal."

A. Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

1. Wiring Diagrams:  For power, signal, and control wiring.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Delegated-Design Submittal:  For compressed-air equipment mounting indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of supports.

2. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Sections specifying vibration isolation devices, supports, and seismic controls.  See SEI/ASCE 7 for certification requirements for equipment and components.

C. Seismic Qualification Certificates:  For compressed-air equipment, accessories, and components, from manufacturers.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Operation and Maintenance Data:  For compressed-air equipment to include in emergency, operation, and maintenance manuals.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. ASME Compliance:  Fabricate and label receivers to comply with ASME Boiler and Pressure Vessel Code.

1.7 PROJECT CONDITIONS

Retain this article if interruption of existing compressed-air service is required.

A. Interruption of Existing Compressed-Air Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of compressed-air service.

2. Do not proceed with interruption of compressed-air service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.8 COORDINATION

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

1.9 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Air-Compressor, Inlet-Air-Filter Elements:  Equal to <Insert number> percent of amount installed, but no fewer than <Insert number> units.

2. Belts:  [One] [Two] <Insert number> for each belt-driven compressor.

PART 2 -  PRODUCTS

2.1 GENERAL REQUIREMENTS FOR PACKAGED AIR COMPRESSORS AND RECEIVERS

A. General Description:  Factory-assembled, -wired, -piped, and -tested; electric-motor-driven; air-cooled; continuous-duty air compressors and receivers that deliver air of quality equal to intake air.

B. Control Panels:  Automatic control station with load control and protection functions.  Comply with NEMA ICS 2 and UL 508.

1. Enclosure:  NEMA ICS 6, Type 12 control panel unless otherwise indicated.

2. Motor Controllers:  Full-voltage, combination magnetic type with undervoltage release feature and motor-circuit-protector-type disconnecting means and short-circuit protective device.

3. Control Voltage:  120-V ac or less, using integral control power transformer.

4. Motor Overload Protection:  Overload relay in each phase.

5. Starting Devices:  Hand-off-automatic selector switch in cover of control panel, plus pilot device for automatic control.

Retain first subparagraph below if Project has duplex and multiplex air compressors.

6. Automatic control switches to [alternate lead-lag compressors for duplex] [sequence lead-lag compressors for multiplex] air compressors.

7. Instrumentation:  Include discharge-air pressure gage, air-filter maintenance indicator, hour meter, compressor discharge-air and coolant temperature gages, and control transformer.

8. Alarm Signal Device:  For connection to alarm system to indicate when backup air compressor is operating.

C. Receivers:  Steel tank constructed according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

1. Pressure Rating:  At least as high as highest discharge pressure of connected compressors, and bearing appropriate code symbols.

2. Interior Finish:  Corrosion-resistant coating.

3. Accessories:  Include safety valve, pressure gage, drain, and pressure-reducing valve.

Retain paragraph below for projects in seismic areas.

D. Mounting Frame:  Fabricate mounting and attachment to pressure vessel with reinforcement strong enough to resist packaged equipment movement during a seismic event when base is anchored to building structure.

2.2 LUBRICATED, RECIPROCATING AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.

1. Atlas Copco.

2. CompAir, Ltd.

3. Curtis-Toledo.

4. Gardner Denver, Inc.

5. General Air Products, Inc.

6. Ingersoll-Rand; Air Solutions Group.

7. Kaeser Compressors, Inc.

8. Powerex, Inc.

9. Quincy Compressor; an EnPro Industries company.

10. Saylor-Beall Manufacturing Company.

11. <Insert manufacturer's name>.

C. Compressor(s):  Lubricated, reciprocating-piston type with lubricated compression chamber and crankcase.

1. Submerged gear-type oil pump.

2. Oil filter.

3. Combined high discharge-air temperature and low lubrication-oil pressure switch.

4. Belt guard totally enclosing pulleys and belts.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] [Three] <Insert number>; [single] [single or two] [two] stage.

a. Intercooler between stages of two-stage units.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [100 psig (690 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Mounting:  [Freestanding] [Tank mounted].

8. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

9. Unit Electrical Characteristics:

a. Volts:  [120] [208] [240] <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

10. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

2.3 OIL-FREE, RECIPROCATING AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.

1. Gast Manufacturing Inc.

2. Ingersoll-Rand; Air Solutions Group.

3. Quincy Compressor; an EnPro Industries company.

4. <Insert manufacturer's name>.

C. Compressor(s):  Oil-free, reciprocating-piston type with nonlubricated compression chamber, lubricated crankcase, and of construction that prohibits oil from entering compression chamber.

1. Submerged gear-type oil pump.

2. Oil filter.

3. Combined high discharge-air temperature and low lubrication-oil pressure switch.

4. Belt guard totally enclosing pulleys and belts.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] [Three] <Insert number>; single stage.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [100 psig (690 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Mounting:  [Freestanding] [Tank mounted].

8. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

9. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

10. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

2.4 OILLESS, RECIPROCATING AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.

1. Curtis-Toledo.

2. Gast Manufacturing Inc.

3. General Air Products, Inc.

4. Ingersoll-Rand; Air Solutions Group.

5. JUN-AIR USA, Inc.

6. Kaeser Compressors, Inc.

7. Powerex, Inc.

8. Quincy Compressor; an EnPro Industries company.

9. Rietschle Thomas Sheboygan, Inc.

10. Squire-Cogswell/Aeros Instruments, Inc.

11. <Insert manufacturer's name>.

C. Compressor(s):  Oilless (nonlubricated), reciprocating-piston type, with sealed oil-free bearings, that will deliver air of quality equal to intake air.

1. High discharge-air temperature switch.

2. Belt guard totally enclosing pulleys and belts.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] [Three] <Insert number>; [single] [single or two] [two] stage.

a. Intercooler between stages of two-stage units.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [100 psig (690 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Mounting:  [Freestanding] [Tank mounted].

8. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

9. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

10. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

2.5 OIL-FREE, ROTARY-SCREW AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.

1. Atlas Copco.

2. CompAir, Ltd.

3. Gardner Denver, Inc.

4. Ingersoll-Rand; Air Solutions Group.

5. <Insert manufacturer's name>.

C. Compressor(s):  Oil-free, rotary-screw type with nonlubricated helical screws and lubricated gear box, and of construction that prohibits oil from entering compression chamber.

1. Coupling:  Nonlubricated, flexible type.

2. Cooling/Lubrication System:  Unit-mounted, air-cooled exchanger package prepiped to unit; with air pressure circulation system with coolant stop valve, full-flow coolant filter, and thermal bypass valve.

3. Air Filter:  Dry type, with maintenance indicator and cleanable replaceable filter element.

4. Air/Coolant Receiver and Separation System:  150-psig- (1035-kPa-) rated steel tank with ASME safety valve, coolant-level gage, multistage air-coolant separator element, minimum pressure valve, blowdown valve, discharge check valve, coolant stop valve, full-flow coolant filter, and thermal bypass valve.

5. Capacity Control:  Capacity modulation between zero and 100 percent air delivery, with operating pressures between 50 and 100 psig (345 and 690 kPa).  Include necessary control to hold constant pressure.  When air demand is zero, unload compressor by using pressure switch and blowdown valve.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] <Insert number>; single stage.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [100 psig (690 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

8. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

9. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

10. Enclosure:  Steel with sound-attenuating material lining.

2.6 OIL-FLOODED, ROTARY-SCREW AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.

1. Atlas Copco.

2. CompAir, Ltd.

3. Gardner Denver, Inc.

4. Ingersoll-Rand; Air Solutions Group.

5. Kaeser Compressors, Inc.

6. Quincy Compressor; an EnPro Industries company.

7. Sullair Corporation.

8. <Insert manufacturer's name>.

C. Compressor(s):  Oil-flooded, rotary-screw type with lubricated helical screws and lubricated gear box.

1. Coupling:  Nonlubricated, flexible type.

2. Cooling/Lubrication System:  Unit-mounted, air-cooled exchanger package prepiped to unit; with air pressure circulation system with coolant stop valve, full-flow coolant filter, and thermal bypass valve.

3. Air Filter:  Dry type, with maintenance indicator and cleanable replaceable filter element.

4. Air/Coolant Receiver and Separation System:  150-psig- (1035-kPa-) rated steel tank with ASME safety valve, coolant-level gage, multistage air-coolant separator element, minimum pressure valve, blowdown valve, discharge check valve, coolant stop valve, full-flow coolant filter, and thermal bypass valve.

5. Capacity Control:  Capacity modulation between zero and 100 percent air delivery, with operating pressures between 50 and 100 psig (345 and 690 kPa).  Include necessary control to hold constant pressure.  When air demand is zero, unload compressor by using pressure switch and blowdown valve.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] <Insert number>; [single] [single or two] [two] stage.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [100 psig (690 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] [200 psig (1380 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

8. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

9. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] [250 psig (1725 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

10. Enclosure:  Steel with sound-attenuating material lining.

2.7 OIL-FREE, ROTARY, SLIDING-VANE AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.  Manufacturers in first two subparagraphs below make low-capacity air compressors that deliver air at maximum of 20 to 25 psig (138 to 173 kPa).

1. Becker Pumps Corp.

2. Gast Manufacturing Inc.

3. <Insert manufacturer's name>.

C. Compressor(s):  Oil-free, nonpulsating, rotary, sliding-vane type with nonlubricated sliding vanes.

1. Cleanable inlet screens.

2. Outlet silencers on discharge connections.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] <Insert number>; single stage.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [15 psig (103 kPa)] [20 psig (138 kPa)] [25 psig (173 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Mounting:  [Freestanding] [Tank mounted].

8. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

9. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

10. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

2.8 OIL-SEALED, ROTARY, SLIDING-VANE AIR COMPRESSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Verify that products of listed manufacturers can produce volume of air at pressure required.  Manufacturers in first two subparagraphs below make low-capacity air compressors that deliver air at maximum of 25 to 30 psig (173 to 207 kPa).

1. Becker Pumps Corp.

2. Davey Compressor Company.

3. Gast Manufacturing Inc.

4. <Insert manufacturer's name>.

Manufacturer in first subparagraph below makes high-capacity air compressors that deliver air at pressures up to 150 psig (1035 kPa).

5. CompAir, Ltd.

6. <Insert manufacturer's name>.

C. Compressor(s):  Nonpulsating, rotary, sliding-vane type with oil-sealed sliding vanes.

1. Cleanable inlet screens.

2. Outlet silencers and oil-mist separators on discharge connections.

If Project has more than one type or configuration of compressor, delete paragraph below and schedule compressors on Drawings.

D. Capacities and Characteristics:

1. Air Compressor(s):  [One] [Two] <Insert number>; single stage.

Retain one or both of first two subparagraphs below.

2. Standard-Air Capacity of Each Air Compressor:  <Insert scfm (standard L/s)> free air.

3. Actual-Air Capacity of Each Air Compressor:  <Insert acfm (actual L/s)> delivered.

4. Discharge-Air Pressure:  [20 psig (138 kPa)] [25 psig (173 kPa)] [30 psig (207 kPa)] [100 psig (690 kPa)] [125 psig (860 kPa)] <Insert value>.

5. Intake-Air Temperature:  <Insert deg F (deg C)>.

6. Discharge-Air Temperature:  <Insert deg F (deg C)>.

7. Mounting:  [Freestanding] [Tank mounted].

8. Motor (Each Air Compressor):

a. Horsepower:  <Insert value>.

b. Speed:  [1750] [3400] <Insert speed> rpm.

9. Unit Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

10. Receiver:  ASME construction steel tank.

a. Arrangement:  [Horizontal] [Vertical].

b. Capacity:  <Insert gal. (L)>.

c. Interior Finish:  [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating> coating.

d. Pressure Rating:  [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> minimum.

e. Pressure Regulator Setting:  <Insert psig (kPa)>.

f. Pressure Relief Valve Setting:  <Insert psig (kPa)>.

g. Drain:  [Automatic] [Manual] valve.

2.9 INLET-AIR FILTERS

Retain one of two paragraphs in this article.

A. Description:  Combination inlet-air filter-silencer, suitable for remote installation, for each air compressor.

Revise first subparagraph below if filter is in-line type and installed in an interior space.  Install gooseneck with screen on exterior air inlet.

1. Construction:  Weatherproof housing for replaceable, dry-type filter element, with silencer tubes or other method of sound reduction.

2. Capacity:  Match capacity of air compressor, with filter having collection efficiency of 99 percent retention of particles larger than 10 micrometers.

B. Description:  Combination inlet-air filter-silencer, suitable for remote installation, for multiple air compressors.

Revise first subparagraph below if filter is in-line type and installed in an interior space.  Install gooseneck with screen on exterior air inlet.

1. Construction:  Weatherproof housing for replaceable, dry-type filter element, with silencer tubes or other method of sound reduction.

2. Capacity:  Match total capacity of connected air compressors, with filter having collection efficiency of 99 percent retention of particles larger than 10 micrometers.

2.10 AIR-COOLED, COMPRESSED-AIR AFTERCOOLERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Air/Tak, Inc.

2. Arrow Pneumatics, Inc.

3. Curtis-Toledo.

4. Gardner Denver, Inc.

5. Hankison International.

6. Ingersoll-Rand; Air Solutions Group.

7. Pneumatech Inc.

8. Saylor-Beall Manufacturing Company.

9. Van Air Systems, Inc.

10. Zeks Compressed Air Solutions.

11. <Insert manufacturer's name>.

C. Description:  Electric-motor-driven, fan-operation, finned-tube unit; rated at [250 psig (1725 kPa)] <Insert pressure> and leak tested at 350-psig (2415-kPa) minimum air pressure; in capacities indicated.  Size units to cool compressed air in compressor-rated capacities to [10 deg F (6 deg C)] <Insert temperature> above summertime maximum ambient temperature.  Include moisture separator and automatic drain.

If Project has more than one type or configuration of aftercooler, delete paragraph below and schedule aftercoolers on Drawings.

D. Capacities and Characteristics:

1. Standard-Air Capacity of Each Aftercooler:  <Insert scfm (standard L/s)> free air.

2. Pressure:  <Insert psig (kPa)>.

3. Entering, Compressed-Air Temperature:  <Insert deg F (deg C)>.

4. Leaving, Compressed-Air Temperature:  <Insert deg F (deg C)>.

5. Ambient-Air Temperature:  <Insert deg F (deg C)>.

6. Maximum Compressed-Air-Pressure Drop:  <Insert psig (kPa)>.

7. Motor Horsepower:  <Insert value>.

8. Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.11 WATER-COOLED, COMPRESSED-AIR AFTERCOOLERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Air/Tak, Inc.

2. Arrow Pneumatics, Inc.

3. Curtis-Toledo.

4. Gardner Denver, Inc.

5. Hankison International.

6. Ingersoll-Rand; Air Solutions Group.

7. Pneumatech Inc.

8. Saylor-Beall Manufacturing Company.

9. Van Air Systems, Inc.

10. Zeks Compressed Air Solutions.

11. <Insert manufacturer's name>.

C. Description:  Shell and tube unit, rated at [250 psig (1725 kPa)] <Insert pressure> and leak tested at 350-psig (2415-kPa) minimum air pressure, in capacities indicated.  Include moisture separator and automatic drain.

If Project has more than one type or configuration of aftercooler, delete paragraph below and schedule aftercoolers on Drawings.

D. Capacities and Characteristics:

1. Standard-Air Capacity of Each Aftercooler:  <Insert scfm (standard L/s)> free air.

2. Pressure:  <Insert psig (kPa)>.

3. Entering-Water Temperature:  <Insert deg F (deg C)>.

4. Water Flow:  <Insert gpm (L/s)>.

5. Entering, Compressed-Air Temperature:  <Insert deg F (deg C)>.

6. Leaving, Compressed-Air Temperature:  <Insert deg F (deg C)>.

2.12 REFRIGERANT COMPRESSED-AIR DRYERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Air/Tak, Inc.

2. Arrow Pneumatics, Inc.

3. Atlas Copco.

4. Curtis-Toledo.

5. Domnick Hunter Limited; ZANDER, Inc.

6. Donaldson Company, Inc.; Donaldson Ultrafilter Co.

7. Hankison International.

8. Ingersoll-Rand; Air Solutions Group.

9. Kaeser Compressors, Inc.

10. Numatics, Incorporated.

11. Pioneer Air Systems, Inc.

12. Pneumatech Inc.

13. SPX Air Treatment.

14. Van Air Systems, Inc.

15. Wilkerson Operations; Pneumatic Division.

16. Zeks Compressed Air Solutions.

17. <Insert manufacturer's name>.

C. Description:  Noncycling, air-cooled, electric-motor-driven unit with steel enclosure and capability to deliver 35 deg F (2 deg C), 100-psig (690-kPa) air at dew point.  Include automatic ejection of condensate from airstream, step-down transformers, disconnect switches, inlet and outlet pressure gages, thermometers, automatic controls, and filters.

If Project has more than one type or configuration of compressed-air dryer, delete paragraph below and schedule dryers on Drawings.

D. Capacities and Characteristics:

1. Standard-Air Capacity of Each Compressed-Air Dryer:  <Insert scfm (standard L/s)> free air.

2. Pressure:  <Insert psig (kPa)>.

3. Entering-Air Temperature:  <Insert deg F (deg C)>.

4. Leaving-Air Temperature:  <Insert deg F (deg C)>.

5. Leaving-Air Dew Point Temperature:  <Insert deg F (deg C)>.

6. Ambient-Air Temperature:  <Insert deg F (deg C)>.

7. Maximum Air-Pressure Drop:  <Insert psig (kPa)>.

8. Inlet Filter:  [5] <Insert number> micrometers.

9. Outlet Filter:  [1] <Insert number> micrometer(s).

10. Motor Horsepower:  <Insert value>.

11. Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.13 DESICCANT COMPRESSED-AIR DRYERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Air/Tak, Inc.

2. Domnick Hunter Limited; ZANDER, Inc.

3. Donaldson Company, Inc.; Donaldson Ultrafilter Co.

4. Hankison International.

5. Ingersoll-Rand; Air Solutions Group.

6. Kaeser Compressors, Inc.

7. Numatics, Incorporated.

8. Pioneer Air Systems, Inc.

9. Pneumatech Inc.

10. SPX Air Treatment.

11. Van Air Systems, Inc.

12. Wilkerson Operations; Pneumatic Division.

13. Zeks Compressed Air Solutions.

14. <Insert manufacturer's name>.

C. Description:  Twin-tower unit with purge system, mufflers, and capability to deliver [plus 10 deg F (minus 12 deg C), 100-psig (690-kPa)] <Insert values> air at dew point.  Include dew point controlled purge, step-down transformers, disconnect switches, inlet and outlet pressure gages, thermometers, automatic controls, and filters.

If Project has more than one type or configuration of compressed-air dryer, delete paragraph below and schedule dryers on Drawings.

D. Capacities and Characteristics:

1. Standard-Air Capacity of Each Compressed-Air Dryer:  <Insert scfm (standard L/s)> free air.

2. Pressure:  <Insert psig (kPa)>.

3. Entering-Air Temperature:  <Insert deg F (deg C)>.

4. Leaving-Air Temperature:  <Insert deg F (deg C)>.

5. Leaving-Air Dew Point Temperature:  <Insert deg F (deg C)>.

6. Ambient-Air Temperature:  <Insert deg F (deg C)>.

7. Maximum Air-Pressure Drop:  <Insert psig (kPa)>.

8. Inlet Filter:  [5] <Insert number> micrometers.

9. Outlet Filter:  [1] <Insert number> micrometer(s).

10. Electrical Characteristics:

a. Volts:  <Insert value>.

b. Phase(s):  [Single] [Three].

c. Hertz:  [60] <Insert value> Hz.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.14 COMPUTER INTERFACE CABINET

Cabinet in this article is for connection to facility computer.

A. Description:

1. Wall mounting.

2. Welded steel with white enamel finish.

3. Gasketed door.

4. Grounding device.

5. Factory-installed, signal circuit boards.

6. Power transformer.

7. Circuit breaker.

8. Wiring terminal board.

9. Internal wiring capable of interfacing [20] <Insert number> alarm signals.

2.15 MOTORS

Default motor characteristics are specified in Division 15 Section "Motors."

A. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Motors."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

If unique characteristics are required for motors in this Section, retain paragraph below.

B. <Insert unique motor characteristics>.

PART 3 -  EXECUTION

3.1 EQUIPMENT INSTALLATION

Retain one of first four paragraphs below for air compressors and indicated accessories.  If more than one "Equipment Mounting" Paragraph is required, show mounting type on Drawings.  Coordinate with Drawings and with Sections specifying vibration and seismic controls.  Retain or insert amount of required deflection.

Retain first paragraph for equipment supported on concrete base and vibration isolation devices.

A. Equipment Mounting:  Install air compressors[ and aftercoolers] [ and air dryers] [, aftercoolers, and air dryers] on concrete bases using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."  Comply with requirements for vibration isolation devices specified in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

2. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

3. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

4. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for equipment supported on vibration isolation devices without a concrete base.

B. Equipment Mounting:  Install air compressors[ and aftercoolers] [ and air dryers] [, aftercoolers, and air dryers] using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements for vibration isolation devices specified in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

Retain first paragraph below for equipment supported on a vibration isolation inertia base.

C. Equipment Mounting:  Install air compressors[ and aftercoolers] [ and air dryers] [, aftercoolers, and air dryers] on vibration isolation inertia bases.  Comply with requirements specified in Division 15 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Retain first paragraph below for equipment installed on concrete bases without vibration isolation devices.  This may be appropriate for rotary compressors on structural slabs-on-grade.

D. Equipment Mounting:  Install air compressors[ and aftercoolers] [ and air dryers] [, aftercoolers, and air dryers] on concrete bases.  Comply with requirements in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for mounting aftercoolers and dryers on concrete bases without vibration isolation devices separate from compressors.

E. Equipment Mounting:  Install [water-cooled, compressed-air aftercoolers] [and] [desiccant compressed-air dryers] on concrete bases.  Comply with requirements in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

F. Install compressed-air equipment anchored to substrate.

G. Arrange equipment so controls and devices are accessible for servicing.

H. Maintain manufacturer's recommended clearances for service and maintenance.

I. Install the following devices on compressed-air equipment:

1. Thermometer, Pressure Gage, and Safety Valve:  Install on each compressed-air receiver.

2. Pressure Regulators:  Install downstream from air compressors[ and dryers].

3. Automatic Drain Valves:  Install on aftercoolers, receivers, and dryers.  Discharge condensate over nearest floor drain.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for piping specified in Division 15 Section "General-Service Compressed-Air Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

3.3 IDENTIFICATION

A. Identify general-service air compressors and components.  Comply with requirements for identification specified in Division 15 Section "Mechanical Identification."

3.4 STARTUP SERVICE

Retain this article if a factory-authorized service representative is required.

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Check for lubricating oil in lubricated-type equipment.

3. Check belt drives for proper tension.

4. Verify that air-compressor inlet filters and piping are clear.

5. Check for equipment vibration-control supports and flexible pipe connectors and verify that equipment is properly attached to substrate.

6. Check safety valves for correct settings.  Ensure that settings are higher than air-compressor discharge pressure but not higher than rating of system components.

Retain first subparagraph below if seismic restraints are required.

7. Check for proper seismic restraints.

8. Drain receiver tanks.

9. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

10. Test and adjust controls and safeties.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air compressors[ and aftercoolers] [ and air dryers] [, aftercoolers, and air dryers].

END OF SECTION 15251

GENERAL-SERVICE PACKAGED AIR COMPRESSORS AND RECEIVERS
15251 - 1

