Copyright 2003 AIA
MASTERSPEC Full Length
09/03 (R 06/06)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15410 - PLUMBING FIXTURES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following conventional plumbing fixtures and related components:

Adjust list below to suit Project.

1. Faucets for [lavatories] [bathtubs] [bathtub/showers] [showers] [and] [sinks].

2. Laminar-flow faucet-spout outlets.

3. Flushometers.

4. Toilet seats.

5. Protective shielding guards.

6. Fixture supports.

7. Interceptors.

8. Shower receptors.

9. Dishwasher air-gap fittings.

10. Disposers.

11. Hot-water dispensers.

12. Water closets.

13. Urinals.

14. Bidets.

15. Lavatories.

16. Commercial sinks.

17. Shampoo bowls.

18. Wash fountains.

19. Bathtubs.

20. Individual showers.

21. Group showers.

22. Whirlpool bathtubs.

23. Kitchen sinks.

24. Service sinks.

25. Service basins.

26. Laundry trays.

27. Sacristy sinks.

28. Owner-furnished fixtures.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Water Distribution" for exterior plumbing fixtures and hydrants.

2. Division 10 Section "Toilet and Bath Accessories."

3. Division 15 Section "Medical Plumbing Fixtures."

4. Division 15 Section "Emergency Plumbing Fixtures."

5. Division 15 Section "Security Plumbing Fixtures."

6. Division 15 Section "Drinking Fountains and Water Coolers."

7. Division 15 Section "Plumbing Specialties" for backflow preventers, floor drains, and specialty fixtures not included in this Section.

8. Division 15 Section "Water Filtration Equipment" for water filters.

1.3 DEFINITIONS

Retain abbreviations and terms that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. Accessible Fixture:  Plumbing fixture that can be approached, entered, and used by people with disabilities.

C. Cast Polymer:  Cast-filled-polymer-plastic material.  This material includes cultured-marble and solid-surface materials.

D. Cultured Marble:  Cast-filled-polymer-plastic material with surface coating.

E. Fitting:  Device that controls the flow of water into or out of the plumbing fixture.  Fittings specified in this Section include supplies and stops, faucets and spouts, shower heads and tub spouts, drains and tailpieces, and traps and waste pipes.  Piping and general-duty valves are included where indicated.

F. FRP:  Fiberglass-reinforced plastic.

G. PMMA:  Polymethyl methacrylate (acrylic) plastic.

H. PVC:  Polyvinyl chloride plastic.

I. Solid Surface:  Nonporous, homogeneous, cast-polymer-plastic material with heat-, impact-, scratch-, and stain-resistance qualities.

1.4 SUBMITTALS

A. Product Data:  For each type of plumbing fixture indicated.  Include selected fixture and trim, fittings, accessories, appliances, appurtenances, equipment, and supports.  Indicate materials and finishes, dimensions, construction details, and flow-control rates.

B. LEED Submittal:

1. Product Data for Credit WE [2] [3.1] [3.2] [2 and 3.1] [2, 3.1, and 3.2]:  Documentation indicating flow and water consumption requirements.

Retain first paragraph below if fixtures include electrical components and wiring.

C. Shop Drawings:  Diagram power, signal, and control wiring.

D. Operation and Maintenance Data:  For plumbing fixtures to include in emergency, operation, and maintenance manuals.

E. Warranty:  Special warranty specified in this Section.

1.5 QUALITY ASSURANCE

Revise first paragraph and subparagraph below to suit manufacturers and types of fixtures specified.  No manufacturer makes all types of fixtures, faucets, etc.

A. Source Limitations:  Obtain plumbing fixtures, faucets, and other components of each category through one source from a single manufacturer.

1. Exception:  If fixtures, faucets, or other components are not available from a single manufacturer, obtain similar products from other manufacturers specified for that category.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Retain option in first paragraph below if required by authorities having jurisdiction.

C. Regulatory Requirements:  Comply with requirements in ICC A117.1, "Accessible and Usable Buildings and Facilities"[; Public Law 90-480, "Architectural Barriers Act"; and Public Law 101-336, "Americans with Disabilities Act";] for plumbing fixtures for people with disabilities.

D. Regulatory Requirements:  Comply with requirements in Public Law 102-486, "Energy Policy Act," about water flow and consumption rates for plumbing fixtures.

E. NSF Standard:  Comply with NSF 61, "Drinking Water System Components--Health Effects," for fixture materials that will be in contact with potable water.

F. Select combinations of fixtures and trim, faucets, fittings, and other components that are compatible.

G. Comply with the following applicable standards and other requirements specified for plumbing fixtures:

Retain only subparagraphs below that match fixtures, components, and features specified.

1. Enameled, Cast-Iron Fixtures:  ASME A112.19.1M.

2. Plastic Bathtubs:  ANSI Z124.1.

3. Plastic Lavatories:  ANSI Z124.3.

4. Plastic Laundry Trays:  ANSI Z124.6.

5. Plastic Mop-Service Basins:  ANSI Z124.6.

6. Plastic Shower Enclosures:  ANSI Z124.2.

7. Plastic Sinks:  ANSI Z124.6.

8. Plastic Urinal Fixtures:  ANSI Z124.9.

9. Plastic Whirlpool Bathtubs:  ANSI Z124.1 and ASME A112.19.7M.

10. Porcelain-Enameled, Formed-Steel Fixtures:  ASME A112.19.4M.

11. Slip-Resistant Bathing Surfaces:  ASTM F 462.

12. Solid-Surface-Material Lavatories and Sinks:  ANSI/ICPA SS-1.

13. Stainless-Steel Commercial, Handwash Sinks:  NSF 2 construction.

14. Stainless-Steel Residential Sinks:  ASME A112.19.3.

15. Vitreous-China Fixtures:  ASME A112.19.2M.

16. Water-Closet, Flush Valve, Tank Trim:  ASME A112.19.5.

17. Water-Closet, Flushometer Tank Trim:  ASSE 1037.

18. Whirlpool Bathtub Fittings:  ASME A112.19.8M.

H. Comply with the following applicable standards and other requirements specified for [lavatory] [and] [sink] faucets:

Retain only subparagraphs below that match faucets, components, and features specified.

1. Backflow Protection Devices for Faucets with Side Spray:  ASME A112.18.3M.

2. Backflow Protection Devices for Faucets with Hose-Thread Outlet:  ASME A112.18.3M.

3. Diverter Valves for Faucets with Hose Spray:  ASSE 1025.

4. Faucets:  ASME A112.18.1.

5. Hose-Connection Vacuum Breakers:  ASSE 1011.

6. Hose-Coupling Threads:  ASME B1.20.7.

7. Integral, Atmospheric Vacuum Breakers:  ASSE 1001.

8. NSF Potable-Water Materials:  NSF 61.

9. Pipe Threads:  ASME B1.20.1.

10. Sensor-Actuated Faucets and Electrical Devices:  UL 1951.

11. Supply Fittings:  ASME A112.18.1.

12. Brass Waste Fittings:  ASME A112.18.2.

I. Comply with the following applicable standards and other requirements specified for [bathtub] [bathtub/shower] [and] [shower] faucets:

Retain only subparagraphs below that match faucets, components, and features specified.

1. Backflow Protection Devices for Hand-Held Showers:  ASME A112.18.3M.

2. Combination, Pressure-Equalizing and Thermostatic-Control Antiscald Faucets:  ASSE 1016.

3. Deck-Mounted Bath/Shower Transfer Valves:  ASME 18.7.

4. Faucets:  ASME A112.18.1.

5. Hand-Held Showers:  ASSE 1014.

6. High-Temperature-Limit Controls for Thermal-Shock-Preventing Devices:  ASTM F 445.

7. Hose-Coupling Threads:  ASME B1.20.7.

8. Manual-Control Antiscald Faucets:  ASTM F 444.

9. Pipe Threads:  ASME B1.20.1.

10. Pressure-Equalizing-Control Antiscald Faucets:  ASTM F 444 and ASSE 1016.

11. Sensor-Actuated Faucets and Electrical Devices:  UL 1951.

12. Thermostatic-Control Antiscald Faucets:  ASTM F 444 and ASSE 1016.

J. Comply with the following applicable standards and other requirements specified for miscellaneous fittings:

Retain only subparagraphs below that match fittings and features specified.

1. Atmospheric Vacuum Breakers:  ASSE 1001.

2. Brass and Copper Supplies:  ASME A112.18.1.

3. Dishwasher Air-Gap Fittings:  ASSE 1021.

4. Manual-Operation Flushometers:  ASSE 1037.

5. Plastic Tubular Fittings:  ASTM F 409.

6. Brass Waste Fittings:  ASME A112.18.2.

7. Sensor-Operation Flushometers:  ASSE 1037 and UL 1951.

K. Comply with the following applicable standards and other requirements specified for miscellaneous components:

Retain only subparagraphs below that match components and features specified.

1. Disposers:  ASSE 1008 and UL 430.

2. Dishwasher Air-Gap Fittings:  ASSE 1021.

3. Flexible Water Connectors:  ASME A112.18.6.

4. Floor Drains:  ASME A112.6.3.

5. Grab Bars:  ASTM F 446.

6. Hose-Coupling Threads:  ASME B1.20.7.

7. Hot-Water Dispensers:  ASSE 1023 and UL 499.

8. Off-Floor Fixture Supports:  ASME A112.6.1M.

9. Pipe Threads:  ASME B1.20.1.

10. Plastic Shower Receptors:  ANSI Z124.2.

11. Plastic Toilet Seats:  ANSI Z124.5.

12. Supply and Drain Protective Shielding Guards:  ICC A117.1.

13. Whirlpool Bathtub Equipment:  UL 1795.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranties:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of whirlpools that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures of unit shell.

b. Faulty operation of controls, blowers, pumps, heaters, and timers.

c. Deterioration of metals, metal finishes, and other materials beyond normal use.

Verify available warranties for units and components and insert numbers below.

2. Warranty Period for Commercial Applications:  [One] [Three] <Insert number> year(s) from date of Substantial Completion.

3. Warranty Period for Residential Applications of Shells:  [Five] [20] [30] <Insert number> years from date of Substantial Completion.

4. Warranty Period for Residential Applications of Pumps and Blowers:  [Five] [20] <Insert number> years from date of Substantial Completion.

5. Warranty Period for Residential Applications of Electronic Controls:  [Five] <Insert number> years from date of Substantial Completion.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Faucet Washers and O-Rings:  Equal to [10] <Insert number> percent of amount of each type and size installed.

2. Faucet Cartridges and O-Rings:  Equal to [5] <Insert number> percent of amount of each type and size installed.

3. Flushometer Valve, Repair Kits:  Equal to [10] <Insert number> percent of amount of each type installed, but no fewer than [12] <Insert number> of each type.

4. Provide hinged-top wood or metal box, or individual metal boxes, with separate compartments for each type and size of extra materials listed above.

5. Flushometer Tank, Repair Kits:  Equal to [5] <Insert number> percent of amount of each type installed, but no fewer than [2] <Insert number> of each type.

6. Water-Closet Tank, Repair Kits:  Equal to [5] <Insert number> percent of amount of each type installed.

7. Toilet Seats:  Equal to [5] <Insert number> percent of amount of each type installed.

8. Dry Urinal Trap-Seal Cartridges:  Equal to [200] <Insert number> percent of amount of each type installed, but no fewer than [12] <Insert number> of each type.

9. Dry Urinal Trap-Seal Liquid:  Equal to [1 gal (3.8 L)] <Insert volume> for each urinal installed.

PART 2 -  PRODUCTS

Part 2 articles specify typical plumbing fixtures and components.  Retain and edit only those articles applicable to Project.

If applying for LEED certification, retain options in articles below that limit flow rates and usage to those used in the calculation to show water use savings.

2.1 LAVATORY FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type lavatory faucet required.

A. Lavatory Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of five lists below.

Select from list below for commercial, solid-brass faucets.

a. American Standard Companies, Inc.

b. Bradley Corporation.

c. Chicago Faucets.

d. Delta Faucet Company.

e. Eljer.

f. Elkay Manufacturing Co.

g. Fisher Manufacturing Co.

h. Grohe America, Inc.

i. Just Manufacturing Company.

j. Kohler Co.

k. Moen, Inc.

l. Royal Brass Mfg. Co.

m. Sayco; a Briggs Plumbing Products, Inc. Company.

n. Speakman Company.

o. T & S Brass and Bronze Works, Inc.

p. Zurn Plumbing Products Group; Commercial Brass Operation.

q. <Insert manufacturer's name.>

Select from list below for general-duty, solid-brass faucets.

r. American Standard Companies, Inc.

s. Bradley Corporation.

t. Brasstech Inc.; Newport Brass Div.

u. Broadway Collection.

v. Central Brass Manufacturing Company.

w. Chicago Faucets.

x. Delta Faucet Company.

y. Eljer.

z. Elkay Manufacturing Co.

aa. Fisher Manufacturing Co.

ab. Franke Consumer Products, Inc.; Kitchen Systems Div.

ac. Gerber Plumbing Fixtures LLC.

ad. Geberit Manufacturing, Inc.

ae. Grohe America, Inc.

af. Hansgrohe Inc.

ag. Hydrotek International, Inc.

ah. Intersan Manufacturing Company.

ai. Just Manufacturing Company.

aj. Kohler Co.

ak. Moen, Inc.

al. Pegler, Ltd.

am. Price Pfister, Inc.

an. Rohl LLC.

ao. Royal Brass Mfg. Co.

ap. Sayco; a Briggs Plumbing Products, Inc. Company.

aq. Speakman Company.

ar. T & S Brass and Bronze Works, Inc.

as. Water Management, Inc.

at. Wolverine Brass, Inc.

au. Zurn Plumbing Products Group; Commercial Brass Operation.

av. <Insert manufacturer's name.>

Select from list below for general-duty, solid-brass faucets or copper- or brass-underbody faucets.

aw. American Standard Companies, Inc.

ax. Bradley Corporation.

ay. Brasstech Inc.; Newport Brass Div.

az. Broadway Collection.

ba. Central Brass Manufacturing Company.

bb. Chicago Faucets.

bc. Delta Faucet Company.

bd. Eljer.

be. Elkay Manufacturing Co.

bf. Fisher Manufacturing Co.

bg. Franke Consumer Products, Inc.; Kitchen Systems Div.

bh. Gerber Plumbing Fixtures LLC.

bi. Geberit Manufacturing, Inc.

bj. Grohe America, Inc.

bk. Hansgrohe Inc.

bl. Hydrotek International, Inc.

bm. Intersan Manufacturing Company.

bn. Just Manufacturing Company.

bo. Kohler Co.

bp. Moen, Inc.

bq. Paul Decorative Products.

br. Pegler, Ltd.

bs. Phoenix Products, Inc.

bt. Price Pfister, Inc.

bu. Rohl LLC.

bv. Royal Brass Mfg. Co.

bw. Sayco; a Briggs Plumbing Products, Inc. Company.

bx. Sterling Plumbing Group, Inc.

by. St. Thomas Creations.

bz. Speakman Company.

ca. Symmons Industries, Inc.

cb. T & S Brass and Bronze Works, Inc.

cc. Water Management, Inc.

cd. WhiteRock Corp.

ce. Wolverine Brass, Inc.

cf. Zurn Plumbing Products Group; Commercial Brass Operation.

cg. <Insert manufacturer's name.>

Select from list below for general-duty, copper- or brass-underbody faucets.

ch. American Standard Companies, Inc.

ci. Delta Faucet Company.

cj. Eljer.

ck. Gerber Plumbing Fixtures LLC.

cl. Moen, Inc.

cm. Phoenix Products, Inc.

cn. Sayco; a Briggs Plumbing Products, Inc. Company.

co. Sterling Plumbing Group, Inc.

cp. WhiteRock Corp.

cq. Wolverine Brass, Inc.

cr. <Insert manufacturer's name.>

Select from list below for residential, nonmetallic-underbody faucets.

cs. Gerber Plumbing Fixtures LLC.

ct. Phoenix Products, Inc.

cu. Sterling Plumbing Group, Inc.

cv. Zurn Plumbing Products Group; Wilkins Operation.

cw. <Insert manufacturer's name.>

4. Description:  [Single-control mixing] [Single-control nonmixing] [Two-handle mixing] <Insert type> valve.  Include hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture holes; coordinate outlet with spout and fixture receptor.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 13 subparagraphs below may be reduced or omitted.

a. Body Material:  [Commercial, solid brass] [General-duty, solid brass] [General-duty, solid brass or copper or brass underbody with brass cover plate] [General-duty, copper or brass underbody with brass cover plate] [Residential, nonmetallic underbody with brass cover plate] [Residential, nonmetallic underbody with nonmetallic cover plate].

b. Finish:  [Polished chrome plate] [Polished brass] [Nonmetallic].

c. Maximum Flow Rate:  [0.5 gpm (1.5 L/min.)] [2.2 gpm (8.3 L/min.)] [2.5 gpm (9.5 L/min.)] <Insert value>.

Retain subparagraph above or first subparagraph below.

d. Maximum Flow:  [0.25 gal. (0.95 L)] <Insert amount>.

e. Centers:  [3-3/8 inches (86 mm)] [4 inches (102 mm)] [6 inches (152 mm)] [8 inches (203 mm)] [Single hole] [Adjustable].

f. Mounting:  [Deck, exposed] [Deck, concealed] [Back/wall, exposed] [Back/wall, concealed].

g. Valve Handle(s):  [Lever] [Knob] [Knob, nonmetallic] [Cross, four arm] [Wrist blade, 4 inches (102 mm)] [Elbow, 6 inches (152 mm)] [Push button] [Not applicable].

h. Inlet(s):  [NPS 3/8 (DN 10) tubing, plain end] [NPS 3/8 (DN 10) tubing, with NPS 1/2 (DN 15) male adaptor] [NPS 1/2 (DN 15) male shank] [NPS 1/2 (DN 15) female shank].

i. Spout:  [Rigid] [Swing] [Rigid, gooseneck] [Swivel, gooseneck] type.

j. Spout Outlet:  [Aerator] [Spray] [Laminar flow] [Plain end] [Spray, 0.5 gpm (1.5 L/min.)].

k. Operation:  [Compression, manual] [Noncompression, manual] [Sensor] [Self-closing, metering].

l. Drain:  [Not required] [Pop up] [Stopper with chain] [Grid] [Lift and turn].

m. Tempering Device:  [Mechanical] [Thermostatic] [Pressure balance] [Not required].

2.2 BATHTUB FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type bathtub faucet required.

A. Bathtub Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Brasstech Inc.; Newport Brass Div.

c. Broadway Collection.

d. Central Brass Manufacturing Company.

e. Delta Faucet Company.

f. Eljer.

g. Gerber Plumbing Fixtures LLC.

h. Grohe America, Inc.

i. Hansgrohe Inc.

j. Kohler Co.

k. Moen, Inc.

l. Paul Decorative Products.

m. Pegler, Ltd.

n. Powers; a Watts Industries Co.

o. Royal Brass Mfg. Co.

p. Sayco; a Briggs Plumbing Products, Inc. Company.

q. Speakman Company.

r. Sterling Plumbing Group, Inc.

s. St. Thomas Creations.

t. Symmons Industries, Inc.

u. T & S Brass and Bronze Works, Inc.

v. Wolverine Brass, Inc.

w. <Insert manufacturer's name.>

4. Description:  [Single-control mixing] [Two-handle mixing] [Three-handle mixing] [Push-button, metering, nonmixing] <Insert type> valve.  Include hot- and cold-water indicators and tub spout.  Coordinate faucet inlets with supplies.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Body Material:  [Solid brass] <Insert material>.

b. Finish:  [Polished chrome plate] [Polished brass] <Insert finish>.

c. Mounting:  [Deck] [Exposed, over rim] [Wall] <Insert mounting>.

d. Valve Handle(s):  [Lever] [Knob] [Knob, nonmetallic] [Cross, four arm] [Not applicable] <Insert handle(s)>.

e. Bathtub Spout:  [Chrome-plated brass] <Insert material>[ with diverter].

f. Operation:  [Compression, manual] [Noncompression, manual] [Sensor] <Insert operation>.

g. Supply Connections:  [NPS 1/2 (DN 15)] [NPS 1/2 (DN 15), union] [Sweat].

2.3 BATHTUB/SHOWER FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type bathtub/shower faucet required.

A. Bathtub/Shower Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Select from list below for pressure-balance faucets.

a. American Standard Companies, Inc.

b. Brasstech Inc.; Newport Brass Div.

c. Broadway Collection.

d. Central Brass Manufacturing Company.

e. Chicago Faucets.

f. Delta Faucet Company.

g. Eljer.

h. Gerber Plumbing Fixtures LLC.

i. Hansgrohe Inc.

j. Kohler Co.

k. Leonard Valve Company.

l. Moen, Inc.

m. Paul Decorative Products.

n. Pegler, Ltd.

o. Powers; a Watts Industries Co.

p. Price Pfister, Inc.

q. Rohl LLC.

r. Royal Brass Mfg. Co.

s. Sayco; a Briggs Plumbing Products, Inc. Company.

t. Speakman Company.

u. Sterling Plumbing Group, Inc.

v. St. Thomas Creations.

w. Symmons Industries, Inc.

x. T & S Brass and Bronze Works, Inc.

y. Wolverine Brass, Inc.

z. Zurn Plumbing Products Group; AquaSpec Commercial Faucet Operation.

aa. Zurn Plumbing Products Group; Wilkins Operation.

ab. <Insert manufacturer's name.>

Select from list below for thermostatic faucets.

ac. Broadway Collection.

ad. Hansgrohe Inc.

ae. Leonard Valve Company.

af. Powers; a Watts Industries Co.

ag. T & S Brass and Bronze Works, Inc.

ah. <Insert manufacturer's name.>

Select from list below for thermostatic/pressure-balance faucets.

ai. Chicago Faucets.

aj. Grohe America, Inc.

ak. Lawler Manufacturing Co., Inc.

al. T & S Brass and Bronze Works, Inc.

am. <Insert manufacturer's name.>

4. Description:  Single-handle [pressure-balance] [thermostatic] [thermostatic/pressure-balance] <Insert type> valve for bathtub and for shower.  Include hot- and cold-water indicators; check stops; tub spout; and shower head, arm, and flange.  Coordinate faucet inlets with supplies; coordinate outlet with diverter valve.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Body Material:  [Solid brass] <Insert material>[ with nonmetallic trim].

b. Finish:  [Polished chrome plate] [Polished brass] <Insert finish>.

c. Maximum Flow Rate:  [2.5 gpm (9.5 L/min.)] <Insert value>, unless otherwise indicated.

d. Diverter Valve:  [Integral] [Not integral] with mixing valve.

e. Mounting:  [Wall] <Insert mounting>.

f. Bathtub Spout:  [Chrome-plated brass] <Insert material>[ with diverter].

g. Operation:  [Compression, manual] [Noncompression, manual] [Sensor] <Insert operation>.

h. Antiscald Device:  [Integral with mixing valve] [Separate unit].

i. Check Stops:  Check-valve type, integral with or attached to body; on hot- and cold-water supply connections.

j. Supply Connections:  [NPS 1/2 (DN 15)] [NPS 1/2 (DN 15), union] [Sweat].

k. Backflow Protection Device for Hand-Held Shower:  [Required] [Not required].

l. Shower Head Type:  [Ball joint] [Without ball joint] [Ball joint and head integral with mounting flange] [Integral with mounting flange] [Hand held, slide-bar mounted] [Hand held, hook mounted].

m. Shower Head Material:  [Metallic] [Nonmetallic] [Combined, metallic and nonmetallic] with chrome-plated finish.

n. Spray Pattern:  [Fixed] [Adjustable].

o. Integral Volume Control:  [Required] [Not required].

p. Shower-Arm Flow-Control Fitting:  [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

2.4 SHOWER FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type shower faucet required.

A. Shower Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Select from list below for pressure-balance faucets.

a. American Standard Companies, Inc.

b. Brasstech Inc.; Newport Brass Div.

c. Broadway Collection.

d. Central Brass Manufacturing Company.

e. Chicago Faucets.

f. Delta Faucet Company.

g. Eljer.

h. Gerber Plumbing Fixtures LLC.

i. Hansgrohe Inc.

j. Kohler Co.

k. Leonard Valve Company.

l. Moen, Inc.

m. Paul Decorative Products.

n. Pegler, Ltd.

o. Powers; a Watts Industries Co.

p. Price Pfister, Inc.

q. Rohl LLC.

r. Royal Brass Mfg. Co.

s. Sayco; a Briggs Plumbing Products, Inc. Company.

t. Speakman Company.

u. Sterling Plumbing Group, Inc.

v. St. Thomas Creations.

w. Symmons Industries, Inc.

x. T & S Brass and Bronze Works, Inc.

y. Wolverine Brass, Inc.

z. Zurn Plumbing Products Group; AquaSpec Commercial Faucet Operation.

aa. Zurn Plumbing Products Group; Wilkins Operation.

ab. <Insert manufacturer's name.>

Select from list below for thermostatic faucets.

ac. Broadway Collection.

ad. Hansgrohe Inc.

ae. Leonard Valve Company.

af. Powers; a Watts Industries Co.

ag. T & S Brass and Bronze Works, Inc.

ah. <Insert manufacturer's name.>

Select from list below for thermostatic and pressure-balance faucets.

ai. Chicago Faucets.

aj. Grohe America, Inc.

ak. Lawler Manufacturing Co., Inc.

al. T & S Brass and Bronze Works, Inc.

am. <Insert manufacturer's name.>

4. Description:  Single-handle [pressure-balance] [thermostatic] [thermostatic and pressure-balance] valve.  Include hot- and cold-water indicators; check stops; and shower head, arm, and flange.  Coordinate faucet inlets with supplies and outlet with diverter valve.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 16 subparagraphs below may be reduced or omitted.

a. Body Material:  [Solid brass] <Insert material>[ with nonmetallic trim].

b. Finish:  [Polished chrome plate] [Polished brass] <Insert finish>.

c. Maximum Flow Rate:  [2.5 gpm (9.5 L/min.)] <Insert value>, unless otherwise indicated.

d. Diverter Valve:  [Not required] [Integral with mixing valve] [Not integral with mixing valve].

e. Mounting:  [Exposed] [Concealed].

f. Backflow Protection Device for Hand-Held Shower:  [Required] [Not required].

g. Operation:  [Compression, manual] [Noncompression, manual] [Sensor].

h. Antiscald Device:  [Integral with mixing valve] [Separate unit] [Not required].

i. Check Stops:  Check-valve type, integral with or attached to body; on hot- and cold-water supply connections.

j. Supply Connections:  [NPS 1/2 (DN 15)] [NPS 1/2 (DN 15), union] [Sweat].

k. Shower Head Type:  [Ball joint] [Without ball joint] [Ball joint and head integral with mounting flange] [Integral with mounting flange] [Hand held, slide-bar mounted] [Hand held, hook mounted].

l. Shower Head Material:  [Metallic] [Nonmetallic] [Combined, metallic and nonmetallic] with chrome-plated finish.

m. Spray Pattern:  [Fixed] [Adjustable].

n. Integral Volume Control:  [Required] [Not required].

o. Shower-Arm Flow-Control Fitting:  [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

Verify availability of feature in subparagraph below if required.

p. Temperature Indicator:  [Not required] [Integral with faucet].

2.5 SINK FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type sink faucet required.

A. Sink Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of five lists below.

Select from list below for commercial, solid-brass faucets.

a. American Standard Companies, Inc.

b. Bradley Corporation.

c. Broadway Collection.

d. Chicago Faucets.

e. Delta Faucet Company.

f. Dormont Manufacturing Company.

g. Eljer.

h. Elkay Manufacturing Co.

i. Fisher Manufacturing Co.

j. Grohe America, Inc.

k. Just Manufacturing Company.

l. Kohler Co.

m. Moen, Inc.

n. Royal Brass Mfg. Co.

o. Sayco; a Briggs Plumbing Products, Inc. Company.

p. Speakman Company.

q. T & S Brass and Bronze Works, Inc.

r. Zurn Plumbing Products Group; Commercial Brass Operation.

s. <Insert manufacturer's name.>

Select from list below for general-duty, solid-brass faucets.

t. American Standard Companies, Inc.

u. Bradley Corporation.

v. Brasstech Inc.; Newport Brass Div.

w. Broadway Collection.

x. Central Brass Manufacturing Company.

y. Chicago Faucets.

z. Delta Faucet Company.

aa. Eljer.

ab. Elkay Manufacturing Co.

ac. Fisher Manufacturing Co.

ad. Franke Consumer Products, Inc.; Kitchen Systems Div.

ae. Gerber Plumbing Fixtures LLC.

af. Grohe America, Inc.

ag. Hansgrohe Inc.

ah. Hydrotek International, Inc.

ai. Intersan Manufacturing Company.

aj. Just Manufacturing Company.

ak. Kohler Co.

al. Moen, Inc.

am. Pegler, Ltd.

an. Price Pfister, Inc.

ao. Rohl LLC.

ap. Royal Brass Mfg. Co.

aq. Sayco; a Briggs Plumbing Products, Inc. Company.

ar. Speakman Company.

as. T & S Brass and Bronze Works, Inc.

at. Water Management, Inc.

au. Wolverine Brass, Inc.

av. Zurn Plumbing Products Group; Commercial Brass Operation.

aw. <Insert manufacturer's name.>

Select from list below for general-duty, solid-brass or copper-underbody faucets.

ax. American Standard Companies, Inc.

ay. Bradley Corporation.

az. Brasstech Inc.; Newport Brass Div.

ba. Central Brass Manufacturing Company.

bb. Chicago Faucets.

bc. Delta Faucet Company.

bd. Eljer.

be. Elkay Manufacturing Co.

bf. Fisher Manufacturing Co.

bg. Franke Consumer Products, Inc.; Kitchen Systems Div.

bh. Gerber Plumbing Fixtures LLC.

bi. Grohe America, Inc.

bj. Hansgrohe Inc.

bk. Hydrotek International, Inc.

bl. Intersan Manufacturing Company.

bm. Just Manufacturing Company.

bn. Kohler Co.

bo. Moen, Inc.

bp. Paul Decorative Products.

bq. Pegler, Ltd.

br. Phoenix Products, Inc.

bs. Price Pfister, Inc.

bt. Rohl LLC.

bu. Royal Brass Mfg. Co.

bv. Sayco; a Briggs Plumbing Products, Inc. Company.

bw. Sterling Plumbing Group, Inc.

bx. St. Thomas Creations.

by. Speakman Company.

bz. Symmons Industries, Inc.

ca. T & S Brass and Bronze Works, Inc.

cb. Water Management, Inc.

cc. WhiteRock Corp.

cd. Wolverine Brass, Inc.

ce. Zurn Plumbing Products Group; Commercial Brass Operation.

cf. <Insert manufacturer's name.>

Select from list below for general-duty, copper-underbody faucets.

cg. American Standard Companies, Inc.

ch. Delta Faucet Company.

ci. Eljer.

cj. Moen, Inc.

ck. Phoenix Products, Inc.

cl. Sayco; a Briggs Plumbing Products, Inc. Company.

cm. Sterling Plumbing Group, Inc.

cn. WhiteRock Corp.

co. Wolverine Brass, Inc.

cp. <Insert manufacturer's name.>

Select from list below for residential, nonmetallic-underbody faucets.

cq. Gerber Plumbing Fixtures LLC.

cr. Sterling Plumbing Group, Inc.

cs. Zurn Plumbing Products Group; Wilkins Operation.

ct. <Insert manufacturer's name.>

4. Description:  [Kitchen faucet with spray, three-hole fixture] [Kitchen faucet with spray, four-hole fixture] [Kitchen faucet without spray] [Laundry tray faucet] [Service sink faucet with stops in shanks, vacuum breaker, hose-thread outlet, and pail hook] [Bar sink faucet] <Insert type>.  Include hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture holes; coordinate outlet with spout and fixture receptor.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Body Material:  [Commercial, solid brass] [General-duty, solid brass] [General-duty, solid brass or copper or brass underbody with brass cover plate] [General-duty, copper or brass underbody with brass cover plate] [Residential, nonmetallic underbody with brass cover plate] [Residential, nonmetallic underbody with nonmetallic cover plate] <Insert material>.

b. Finish:  [Polished chrome plate] [Polished brass] [Nonmetallic] [Polished or rough brass] [Rough brass] <Insert finish>.

c. Maximum Flow Rate:  [2.5 gpm (9.5 L/min.)] <Insert value>, unless otherwise indicated.

d. Mixing Valve:  [Single control] [Two-lever handle].

e. Backflow Protection Device for Hose Outlet:  [Required] [Not required].

f. Backflow Protection Device for Side Spray:  [Required] [Not required].

g. Centers:  [3-3/8 inches (86 mm)] [4 inches (102 mm)] [6 inches (152 mm)] [8 inches (203 mm)] [Single hole] [Adjustable].

h. Mounting:  [Deck] [Back/wall], [exposed] [concealed].

i. Handle(s):  [Lever] [Knob] [Knob, nonmetallic] [Cross, four arm] [Wrist blade, 4 inches (102 mm)] [Elbow, 6 inches (152 mm)] [Not applicable].

j. Inlet(s):  [NPS 3/8 (DN 10) plain-end tubing] [NPS 3/8 (DN 10) tubing with NPS 1/2 (DN 15) male adapter] [NPS 1/2 (DN 15) male shank] [NPS 1/2 (DN 15) female shank].

k. Spout Type:  [Rigid, solid brass] [Rigid, solid brass with wall brace] [Swing, round tubular] [Swing, shaped tube] [Swing, solid brass] [Rigid gooseneck] [Swivel gooseneck].

l. Spout Outlet:  [Aerator] [Swivel aerator/spray] [Spray] [Laminar flow] [Hose thread] [Plain end].

m. Vacuum Breaker:  [Required] [Not required].

n. Operation:  [Compression, manual] [Noncompression, manual] [Sensor].

o. Drain:  [Not required] [Pop up] [Stopper with chain] [Grid] [Lift and turn].

2.6 LAMINAR-FLOW FAUCET-SPOUT OUTLETS

Spout outlets in this Article are non-aerating, produce less splashing than conventional faucet spouts, and help reduce bacteria growth.  They may be used on bathtub-filler, lavatory, shower, and sink spouts.

Copy and edit paragraph and subparagraphs in this Article for each type faucet-spout outlet required.

A. Laminar-Flow Faucet-Spout Outlets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Chronomite Laboratories, Inc.

b. NEOPERL, Inc.

c. <Insert manufacturer's name.>

4. Description:  Chrome-plated-brass faucet-spout outlet that produces non-aerating, laminar stream.  Include male or female thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes flow of faucet.

2.7 FLUSHOMETERS

Copy and edit paragraph and subparagraphs in this Article for each type flushometer required.

A. Flushometers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Select from list below for diaphragm flushometers.

a. Coyne & Delany Co.

b. Delta Faucet Company.

c. Sloan Valve Company.

d. Zurn Plumbing Products Group; Commercial Brass Operation.

e. <Insert manufacturer's name.>

Select from list below for piston flushometers.

f. Hydrotek International, Inc.

g. Sloan Valve Company.

h. TOTO USA, Inc.

i. <Insert manufacturer's name.>

Select from list below for diaphragm or piston flushometers.

j. Coyne & Delany Co.

k. Delta Faucet Company.

l. Hydrotek International, Inc.

m. Sloan Valve Company.

n. TOTO USA, Inc.

o. Zurn Plumbing Products Group; Commercial Brass Operation.

p. <Insert manufacturer's name.>

4. Description:  Flushometer for [urinal] [water-closet]-type fixture.  Include brass body with corrosion-resistant internal components,[ non-hold-open feature,] control stop with check valve, vacuum breaker, copper or brass tubing, and polished chrome-plated finish on exposed parts.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Internal Design:  [Diaphragm] [or] [piston] operation.

b. Style:  [Exposed] [Concealed].

c. Inlet Size:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

d. Trip Mechanism:  [Oscillating, lever-handle actuator] [Mechanical, push-button actuator with stainless-steel access plate] [Hydraulic, push-button actuator] [Foot-pedal actuator] [Hard-wired, electric-sensor actuator] [Battery-operated sensor actuator] <Insert type>.

e. Consumption:  [0.5 gal./flush (1.9 L/flush)] [1.0 gal./flush (3.8 L/flush)] [1.5 gal./flush (5.7 L/flush)] [1.6 gal./flush (6.0 L/flush)] [3.5 gal./flush (13.3 L/flush)] <Insert rate>.

f. Tailpiece Size:  [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] <Insert size> and [standard] <Insert dimension> length to top of bowl.

2.8 TOILET SEATS

Copy and edit paragraph and subparagraphs in this Article for each type toilet seat required.

A. Toilet Seats, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for residential and light-commercial toilet seats.

a. American Standard Companies, Inc.

b. Bemis Manufacturing Company.

c. Centoco Manufacturing Corp.

d. Church Seats.

e. Eljer.

f. Kohler Co.

g. Olsonite Corp.

h. Sanderson Plumbing Products, Inc.; Beneke Div.

i. Sperzel.

j. <Insert manufacturer's name.>

Select from list below for standard and heavy-duty, commercial toilet seats.

k. Bemis Manufacturing Company.

l. Centoco Manufacturing Corp.

m. Church Seats.

n. Kohler Co.

o. Olsonite Corp.

p. Pressalit A/S.

q. Sanderson Plumbing Products, Inc.; Beneke Div.

r. Sperzel.

s. <Insert manufacturer's name.>

4. Description:  Toilet seat for water-closet-type fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Material:  Molded, solid plastic[ with antimicrobial agent].

b. Configuration:  [Closed] [Open] front [with] [without] cover.

c. Size:  [Elongated] [Regular].

d. Hinge Type:  [CK, check] [SS, self-sustaining] [SC, self-sustaining, check] [SR, self-raising] <Insert type>.

e. Class:  [Residential] [Standard commercial] [Heavy-duty commercial].

f. Color:  [White] [Black] <Insert color>.

2.9 PROTECTIVE SHIELDING GUARDS

A. Protective Shielding Pipe Covers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Engineered Brass Co.

b. Insul-Tect Products Co.; a Subsidiary of MVG Molded Products.

c. McGuire Manufacturing Co., Inc.

d. Plumberex Specialty Products Inc.

e. TCI Products.

f. TRUEBRO, Inc.

g. Zurn Plumbing Products Group; Tubular Brass Plumbing Products Operation.

h. <Insert manufacturer's name.>

3. Description:  Manufactured plastic wraps for covering plumbing fixture [hot-water supply] [hot- and cold-water supplies] and trap and drain piping.  Comply with Americans with Disabilities Act (ADA) requirements.

B. Protective Shielding Piping Enclosures, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. TRUEBRO, Inc.

b. <Insert manufacturer's name.>

3. Description:  Manufactured plastic enclosure for covering plumbing fixture hot- and cold-water supplies and trap and drain piping.  Comply with ADA requirements.

2.10 FIXTURE SUPPORTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Josam Company.

2. MIFAB Manufacturing Inc.

3. Smith, Jay R. Mfg. Co.

4. Tyler Pipe; Wade Div.

5. Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

6. Zurn Plumbing Products Group; Specification Drainage Operation.

7. <Insert manufacturer's name.>

Copy and edit paragraph and subparagraph below for each type water-closet support required.

C. Water-Closet Supports, <Insert drawing designation>:

1. Description:  Combination carrier designed for [accessible] [standard] mounting height of wall-mounting, water-closet-type fixture.  Include single or double, vertical or horizontal, hub-and-spigot or hubless waste fitting as required for piping arrangement; faceplates; couplings with gaskets; feet; and fixture bolts and hardware matching fixture.  Include additional extension coupling, faceplate, and feet for installation in wide pipe space.

Copy and edit paragraph and subparagraphs below for each type urinal support required.

D. Urinal Supports, <Insert drawing designation>:

1. Description:  Type [I, urinal carrier with fixture support plates and coupling with seal and fixture bolts and hardware matching fixture] [II, urinal carrier with hanger and bearing plates] for wall-mounting, urinal-type fixture.  Include steel uprights with feet.

2. Accessible-Fixture Support:  Include rectangular steel uprights.

Copy and edit paragraph and subparagraphs below for each type lavatory support required.

E. Lavatory Supports, <Insert drawing designation>:

1. Description:  Type [I, lavatory carrier with exposed arms and tie rods] [II, lavatory carrier with concealed arms and tie rod] [III, lavatory carrier with hanger plate and tie rod] for wall-mounting, lavatory-type fixture.  Include steel uprights with feet.

2. Accessible-Fixture Support:  Include rectangular steel uprights.

Copy and edit paragraph and subparagraph below for each type sink support required.

F. Sink Supports, <Insert drawing designation>:

1. Description:  Type [I, sink carrier with exposed arms and tie rods] [II, sink carrier with hanger plate, bearing studs, and tie rod] [III, sink carrier with hanger plate and exposed arms] for sink-type fixture.  Include steel uprights with feet.

2.11 INTERCEPTORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Josam Company.

2. MIFAB Manufacturing Inc.

3. Smith, Jay R. Mfg. Co.

4. Tyler Pipe; Wade Div.

5. Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

6. Zurn Plumbing Products Group; Specification Drainage Operation.

7. <Insert manufacturer's name.>

C. Hair Interceptors, <Insert drawing designation>:

1. Description:  Manufactured unit with removable screen or strainer and removable cover; designed to trap and retain hair.

a. Material:  [Brass] [or] [stainless-steel] body.

b. Pipe Connections:  [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)].

D. Sediment Interceptors, <Insert drawing designation>:

1. Description:  Manufactured unit with removable screens or strainer and removable cover; designed to trap and retain waste material.

a. Material:  [Cast-iron or steel body with acid-resistant lining and coating] [or] [carbon-steel body with acid-resistant lining and coating] [stainless-steel].

b. Pipe Connections:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].

2.12 SHOWER RECEPTORS

Copy and edit paragraph and subparagraphs in this Article for each type shower receptor required.

A. Shower Receptors, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of five lists below.

Select from list below for cast-polymer shower receptors.

a. Crane Plumbing, L.L.C./Fiat Products.

b. Florestone Products Co., Inc.

c. <Insert manufacturer's name.>

Select from list below for FRP shower receptors.

d. Aker Plastics Co., Inc.

e. Crane Plumbing, L.L.C./Fiat Products.

f. Florestone Products Co., Inc.

g. LASCO Bathware.

h. Mustee, E. L. & Sons, Inc.

i. Sterling Plumbing Group, Inc.

j. Swan Corporation (The).

k. <Insert manufacturer's name.>

Select from list below for PMMA shower receptors.

l. Acryline USA, Inc.

m. American Standard Companies, Inc.

n. Florestone Products Co., Inc.

o. Jacuzzi, Inc.

p. Jason International, Inc.

q. Kohler Co.

r. LASCO Bathware.

s. Praxis Industries, Inc.; Aquarius Products.

t. Royal Baths Manufacturing Co.

u. <Insert manufacturer's name.>

Select from list below for precast-terrazzo shower receptors.

v. Acorn Engineering Company.

w. Crane Plumbing, L.L.C./Fiat Products.

x. Florestone Products Co., Inc.

y. Precast Terrazzo Enterprises, Inc.

z. Stern-Williams Co., Inc.

aa. <Insert manufacturer's name.>

Select from list below for solid-surface shower receptors.

ab. Bradley Corporation.

ac. Formica Corporation.

ad. Jacuzzi, Inc.

ae. Lippert Corporation.

af. Swan Corporation (The).

ag. <Insert manufacturer's name.>

4. Description:  [Cast-polymer] [FRP] [PMMA] [Precast-terrazzo] [Solid-surface] base for built-up-type shower fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  [Standard, residential] [Handicapped/wheelchair].

b. Size:  [32 by 32 inches (813 by 813 mm)] [36 by 36 inches (914 by 914 mm)] [32 by 42 inches (813 by 1067 mm)] [48 by 60 inches (1219 by 1524 mm)] <Insert dimensions>.

c. Color:  [White] <Insert color>.

d. Outlet:  [Cast-in-floor drain] [Drain] with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] [NPS 3 (DN 80)] outlet.

2.13 DISHWASHER AIR-GAP FITTINGS

A. Dishwasher Air-Gap Fittings, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. B & K Industries, Inc.

b. Brass Craft Mfg. Co.; a Subsidiary of Masco Corporation.

c. Brasstech Inc.; Newport Brass Div.

d. Dearborn Brass; a div. of Moen, Inc.

e. Geberit Manufacturing, Inc.

f. JB Products; a Federal Process Corporation Company.

g. Sioux Chief Manufacturing Company, Inc.

h. Watts Brass & Tubular; a division of Watts Regulator Co.

i. <Insert manufacturer's name.>

3. Description:  Fitting suitable for use with domestic dishwashers and for deck mounting; with plastic body[, chrome-plated brass cover]; and capacity of at least 5 gpm (0.32 L/s); and inlet pressure of at least 5 psig (35 kPa) at a temperature of at least 140 deg F (60 deg C).  Include 5/8-inch- (16-mm-) ID inlet and 7/8-inch- (22-mm-) ID outlet hose connections.

Delete subparagraph and associated subparagraphs below if hoses are not required.

4. Hoses:  Rubber and suitable for temperature of at least 140 deg F (60 deg C).

a. Inlet Hose:  5/8-inch (16-mm) ID and [48 inches (1219 mm)] <Insert length> long.

b. Outlet Hose:  7/8-inch (22-mm) ID and [48 inches (1219 mm)] <Insert length> long.

2.14 DISPOSERS

Copy and edit paragraph and subparagraphs in this Article for each type disposer required.

A. Disposers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for batch-feed disposers.

a. American Standard Companies, Inc.

b. Franke Consumer Products, Inc.; Kitchen Systems Div.

c. In-Sink-Erator; a div. of Emerson Electric Co.

d. KitchenAid.

e. Maytag Co.

f. <Insert manufacturer's name.>

Select from list below for continuous-feed disposers.

g. American Standard Companies, Inc.

h. Anaheim Manufacturing, Inc.; a Subsidiary of Western Industries, Inc.

i. Franke Consumer Products, Inc.; Kitchen Systems Div.

j. In-Sink-Erator; a div. of Emerson Electric Co.

k. KitchenAid.

l. Maytag Co.

m. WhiteRock Corp.

n. <Insert manufacturer's name.>

4. Description:  [Batch] [Continuous]-feed household, food-waste disposer.  Include reset button; wall switch; corrosion-resistant chamber with jam-resistant, cutlery- or stainless-steel grinder or shredder; NPS 1-1/2 (DN 40) outlet; quick-mounting, stainless-steel sink flange; antisplash guard; and combination cover/stopper.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  [Batch] [Continuous]-feed household.

b. Model:  [Not applicable] [Sound-insulated chamber] [Sound-insulated chamber and stainless-steel outer shell].

c. Motor:  115-V ac, 1725 rpm, [1/3] [1/2] [3/4] [1] hp with overload protection.

2.15 HOT-WATER DISPENSERS

Copy and edit paragraph and subparagraphs in this Article for each type hot-water dispenser required.

A. Hot-Water Dispensers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for gooseneck spout with lever-handle, flow-control hot-water dispensers.

a. Anaheim Manufacturing, Inc.; a Subsidiary of Western Industries, Inc.

b. Franke Consumer Products, Inc.; Kitchen Systems Div.

c. In-Sink-Erator; a div. of Emerson Electric Co.

d. Just Manufacturing Company.

e. <Insert manufacturer's name.>

Select from list below for spout with twist-knob or push-button, flow-control hot-water dispensers.

f. Anaheim Manufacturing, Inc.; a Subsidiary of Western Industries, Inc.

g. Elkay Manufacturing Co.

h. In-Sink-Erator; a div. of Emerson Electric Co.

i. Just Manufacturing Company.

j. KitchenAid.

k. <Insert manufacturer's name.>

4. Description:  [Gooseneck spout with lever-handle] [Spout with twist-knob or push-button], flow control, household-type dispenser with instant on-off control; insulated, corrosion-resistant-metal storage tank that is open to atmosphere; electric heating element; chrome-plated faucet or spout; removable strainer; thermostat control for water temperature up to 190 deg F (88 deg C); and thermal-overload protection.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Storage Tank Capacity:  0.5 gal. (1.5 L).

b. Heating Element:  750 W minimum, 115-V ac.

2.16 WATER CLOSETS

Copy and edit paragraph and subparagraphs below for each type wall-mounting, back-outlet water closet required.

A. Water Closets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists below.

Select from list below for gravity-tank-type, 1.6-gal./flush (6-L/flush) water closets.

a. Crane Plumbing, L.L.C./Fiat Products.

b. <Insert manufacturer's name.>

Select from list below for Sloan's "Flushmate" flushometer-tank-type, 1.6-gal./flush (6-L/flush) water closets.

c. American Standard Companies, Inc.

d. <Insert manufacturer's name.>

Select from list below for flushometer-valve-type, 1.6-gal./flush (6-L/flush) water closets.

e. American Standard Companies, Inc.

f. Briggs Plumbing Products, Inc.

g. Capizzi.

h. Crane Plumbing, L.L.C./Fiat Products.

i. Eljer.

j. Kohler Co.

k. St. Thomas Creations.

l. TOTO USA, Inc.

m. <Insert manufacturer's name.>

Select from list below for flushometer-valve-type, 3.5-gal./flush (13.3-L/flush) water closets.

n. American Standard Companies, Inc.

o. Crane Plumbing, L.L.C./Fiat Products.

p. Eljer.

q. Kohler Co.

r. <Insert manufacturer's name.>

4. Description [Accessible, wall] [Wall]-mounting, back-outlet, vitreous-china fixture designed for [flushometer-tank] [gravity-type tank] [flushometer valve] operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Style:  [Close coupled] [One piece].

1) Bowl Type:  [Elongated] [Round front] with siphon-jet design.

2) Design Consumption:  [1.6 gal./flush (6 L/flush)] [3.5 gal./flush (13.3 L/flush)].

3) Tank:  [Gravity type with trim] [Flushometer-tank type with trim and pressurized tank].  Include cover.

4) Trip Mechanism:  [Lever-handle] [Push-button] <Insert type> actuator.

5) Color:  [White] <Insert color>.

b. Supply:  [NPS 1/2 (DN 15)] <Insert size> chrome-plated brass or copper with [wheel-handle] [screwdriver] [loose-key] <Insert type> stop.

Retain "Style" and "Supply" subparagraphs and associated subparagraphs above or "Style" and "Flushometer" subparagraphs and associated subparagraphs below.

c. Style:  Flushometer valve.

1) Bowl Type:  [Elongated] [Round front] with [siphon-jet] [blowout] design.

2) Design Consumption:  [1.6 gal./flush (6 L/flush)] [3.5 gal./flush (13.3 L/flush)] <Insert rate>.

3) Color:  [White] <Insert color>.

d. Flushometer:  <Insert designation.>

e. Toilet Seat:  <Insert designation.>

f. Fixture Support:  Water-closet support <Insert designation> combination carrier.

Copy and edit paragraph and subparagraphs below for each type floor-mounting, floor-outlet water closet required.

B. Water Closets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of six lists below.

Select from list below for gravity-tank-type, 1.6-gal./flush (6-L/flush) water closets.

a. American Standard Companies, Inc.

b. Barclay Products, Ltd.

c. Briggs Plumbing Products, Inc.

d. Crane Plumbing, L.L.C./Fiat Products.

e. Duravit USA, Inc.

f. Eljer.

g. Gerber Plumbing Fixtures LLC.

h. Kohler Co.

i. Mansfield Plumbing Products, Inc.

j. Peerless Pottery, Inc.

k. Sanitarios Azteca, S.A. de C.V.

l. Sterling Plumbing Group, Inc.

m. St. Thomas Creations.

n. TOTO USA, Inc.

o. Water Management, Inc.

p. <Insert manufacturer's name.>

Select from list below for Sloan's "Flushmate" flushometer-tank-type, 1.0-gal./flush (3.8-L/flush) water closets.

q. Capizzi.

r. St. Thomas Creations.

s. <Insert manufacturer's name.>

Select from list below for Sloan's "Flushmate" flushometer-tank-type, 1.6-gal./flush (6-L/flush) water closets.

t. American Standard Companies, Inc.

u. Gerber Plumbing Fixtures LLC.

v. Kohler Co.

w. Mansfield Plumbing Products, Inc.

x. St. Thomas Creations.

y. <Insert manufacturer's name.>

Select from list below for Geberit's "PF/2 Energizer" flushometer-tank-type, 1.6-gal./flush (6-L/flush) water closets.

z. Crane Plumbing, L.L.C./Fiat Products.

aa. Eljer.

ab. Peerless Pottery, Inc.

ac. Water Management, Inc.

ad. <Insert manufacturer's name.>

Select from list below for Briggs's vacuum-assist flushometer-tank-type, 1.6-gal./flush (6-L/flush) water closets.

ae. Briggs Plumbing Products, Inc.

af. <Insert manufacturer's name.>

Select from list below for flushometer-valve-type, 1.6-gal./flush (6-L/flush) water closets.

ag. American Standard Companies, Inc.

ah. Briggs Plumbing Products, Inc.

ai. Capizzi.

aj. Crane Plumbing, L.L.C./Fiat Products.

ak. Eljer.

al. Kohler Co.

am. Mansfield Plumbing Products, Inc.

an. Peerless Pottery, Inc.

ao. Sanitarios Azteca, S.A. de C.V.

ap. St. Thomas Creations.

aq. TOTO USA, Inc.

ar. <Insert manufacturer's name.>

4. Description:  [Accessible, floor] [Floor]-mounting, floor-outlet, vitreous-china fixture designed for [gravity-type tank] [flushometer tank] [flushometer valve] operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in five subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Style:  [Close coupled] [One piece].

Bowls in first subparagraph below could include reverse-trap, siphon-vortex, siphon-wash, and washdown types, but this type fixture is usually siphon-jet.  Verify manufacturer and availability if another type is required.

1) Bowl Type:  [Elongated] [Round front] with [siphon-jet] <Insert type> design.  Include bolt caps matching fixture.

2) Height:  [Standard] [Accessible] [Juvenile] [Child].

3) Design Consumption:  [1 gal./flush (3.8 L/flush)] [1.6 gal./flush (6 L/flush)] [3.5 gal./flush (13.3 L/flush)] <Insert rate>.

4) Tank:  [Gravity type with trim] [Flushometer-tank type with trim and pressurized tank].  Include cover.

5) Trip Mechanism:  [Lever-handle] [Push-button] <Insert type> actuator.

6) Color:  [White] <Insert color>.

b. Supply:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] chrome-plated brass or copper with [wheel-handle] [screwdriver] [loose-key] <Insert type> stop.

Retain "Style" and "Supply" subparagraphs and associated subparagraphs above or "Style" and "Flushometer" subparagraphs and associated subparagraphs below.

c. Style:  Flushometer valve.

1) Bowl Type:  [Elongated] [Round front] with [siphon-jet] [reverse-trap] [blowout] [siphon-vortex] [siphon-wash] [washdown] design.  Include bolt caps matching fixture.

2) Height:  [Standard] [Accessible] [Juvenile] [Child].

3) Design Consumption:  [1.6 gal./flush (6 L/flush)] [3.5 gal./flush (13.3 L/flush)] <Insert rate>.

4) Color:  [White] <Insert color>.

d. Flushometer:  <Insert designation.>

e. Toilet Seat:  <Insert designation.>

Copy and edit paragraph and subparagraphs below for each type floor-mounting, back-outlet water closet required.

C. Water Closets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Select from list below for gravity-tank-type water closets.

a. Crane Plumbing, L.L.C./Fiat Products.

b. Eljer.

c. Kohler Co.

d. <Insert manufacturer's name.>

Select from list below for flushometer-tank-type water closets.

e. American Standard Companies, Inc.

f. Briggs Plumbing Products, Inc.

g. Eljer.

h. Water Management, Inc.

i. <Insert manufacturer's name.>

Select from list below for flushometer-valve-type, 1.6-gal./flush (6-L/flush) water closets.

j. American Standard Companies, Inc.

k. Crane Plumbing, L.L.C./Fiat Products.

l. Eljer.

m. Kohler Co.

n. <Insert manufacturer's name.>

4. Description [Accessible, floor] [Floor]-mounting, back-outlet, vitreous-china fixture designed for [gravity-tank] [flushometer-tank] [flushometer-valve] operation.

a. Style:  Close coupled.

1) Bowl Type:  Elongated with siphon-jet design.  Include bolt caps matching fixture.

2) Height:  [Standard] [Accessible].

3) Design Consumption:  [1.6 gal./flush (6 L/flush)] <Insert rate>.

4) Tank:  Gravity type with trim.  Include cover.

5) Trip Mechanism:  [Lever-handle] <Insert type> actuator.

6) Color:  [White] <Insert color>.

b. Supply:  [NPS 1/2 (DN 15)] <Insert size> chrome-plated brass or copper with [wheel-handle] [screwdriver] [loose-key] <Insert type> stop.

Retain "Style" and "Supply" subparagraphs and associated subparagraphs above or "Style" and "Flushometer" subparagraphs and associated subparagraphs below.

c. Style:  Flushometer valve.

1) Bowl Type:  Elongated with siphon-jet design.  Include bolt caps matching fixture.

2) Height:  [Standard] [Accessible].

3) Design Consumption:  [1.6 gal./flush (6 L/flush)] [3.5 gal./flush (13.3 L/flush)].

4) Color:  [White] <Insert color>.

d. Flushometer:  <Insert designation.>

e. Toilet Seat:  <Insert designation.>

f. Wall Support:  Manufactured waste fitting with seal and fixture bolts.

2.17 URINALS

Copy and edit paragraph and subparagraphs below for each type wall-mounting, back-outlet urinal required.

A. Urinals, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Capizzi.

d. Crane Plumbing, L.L.C./Fiat Products.

e. Duravit USA, Inc.

f. Eljer.

g. Kohler Co.

h. Mansfield Plumbing Products, Inc.

i. Peerless Pottery, Inc.

j. Sanitarios Azteca, S.A. de C.V.

k. St. Thomas Creations.

l. TOTO USA, Inc.

m. <Insert manufacturer's name.>

4. Description:  [Accessible, wall] [Wall]-mounting, back-outlet, vitreous-china fixture designed for flushometer valve operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  [Blowout] [Siphon jet] [Blowout with extended shields] [Siphon jet with extended shields] [Washout with extended shields].

b. Strainer or Trapway:  [Integral cast strainer] [Separate removable strainer] [Open trapway] with integral trap.

c. Design Consumption:  [0.5 gal./flush (1.9 L/flush)] [1 gal./flush (3.8 L/flush)] [1.5 gal./flush (5.7 L/flush)] <Insert rate>.

d. Color:  [White] <Insert color>.

e. Supply Spud Size:  [NPS 3/4 (DN 20)] [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)].

f. Outlet Size:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] [NPS 3 (DN 80)].

g. Flushometer:  <Insert designation.>

h. Fixture Support:  Urinal <Insert designation> chair carrier.

Copy and edit paragraph and subparagraphs below for each type wall-mounting, bottom-outlet urinal required.

B. Urinals, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Crane Plumbing, L.L.C./Fiat Products.

d. Eljer.

e. Kohler Co.

f. Mansfield Plumbing Products, Inc.

g. Peerless Pottery, Inc.

h. St. Thomas Creations.

i. TOTO USA, Inc.

j. <Insert manufacturer's name.>

4. Description [Accessible, wall] [Wall]-mounting, bottom-outlet, vitreous-china fixture designed for flushometer valve operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 10 subparagraphs below may be reduced or omitted.

a. Type:  [Washout] [Washdown].

b. Strainer or Trapway:  [Integral cast strainer] [Separate removable strainer] [Open trapway].

c. Design Consumption:  [0.5 gal./flush (1.9 L/flush)] [1 gal./flush (3.8 L/flush)] <Insert rate>.

d. Color:  [White] <Insert color>.

e. Supply Spud Size:  NPS 3/4 (DN 20).

f. Outlet Size:  NPS 1-1/2 (DN 40).

g. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

h. Flushing Device:  Fixture manufacturer's standard matching fixture.

Retain subparagraph above or first subparagraph below.

i. Flushometer:  <Insert designation.>

j. Fixture Support:  Urinal <Insert designation> chair carrier.

Copy and edit paragraph and subparagraphs below for each stall-type, bottom-outlet urinal required.

C. Urinals, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

4. Description Stall-type, bottom-outlet, vitreous-china fixture designed for flushometer valve operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

Caution:  This type of urinal requires a drainage piping trap under the fixture.  This trap is not part of fixture fittings.

a. Type:  [Straight front] [Sloped front], with seam cover for [21-inch (535-mm)] [24-inch (610-mm)] centers.

b. Strainer or Trapway:  Separate removable strainer.

c. Design Consumption:  1 gal./flush (3.8 L/flush).

d. Color:  [White] <Insert color>.

e. Supply Spud Size:  NPS 3/4 (DN 20).

f. Outlet Size:  NPS 2 (DN 50).

g. Flushometer:  <Insert designation.>

Copy and edit paragraph and subparagraphs below for each type wall-mounting, bottom-outlet, trough-type urinal required.

D. Urinals, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Commercial Enameling Company.

b. Eljer.

c. Kohler Co.

d. <Insert manufacturer's name.>

4. Description:  Wall-mounting, bottom-outlet, trough-type, enameled, cast-iron fixture modified for flushometer valve operation.

a. Style:  Similar to wash sink with back and without pedestal.

b. Size:  [36 inches (915 mm)] [48 inches (1219 mm)] [60 inches (1525 mm)] [72 inches (1830 mm)].

c. Color:  [White] <Insert color>.

d. Drain:  Separate removable dome strainer.

e. Design Consumption:  [Not applicable] <Insert rate>.

f. Supply:  NPS 1/2 (DN 15).

g. Outlet Size:  NPS 1-1/2 (DN 40).

h. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

i. Flushing Device:  Fixture manufacturer's standard, with washdown pipe, matching fixture.

j. Fixture Support:  Sink <Insert designation> chair carrier.

Copy and edit paragraph and subparagraphs below for each type wall-mounting, back-outlet dry urinal required.

E. Urinals, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for plastic (FRP or PMMA) dry urinals.

a. Falcon Waterfree Technologies.

b. Waterless Co.

c. <Insert manufacturer's name.>

Select from list below for vitreous-china dry urinals.

d. Duravit USA, Inc.

e. Falcon Waterfree Technologies.

f. <Insert manufacturer's name.>

4. Description [Accessible, wall] [Wall]-mounting, back-outlet dry, [plastic] [vitreous-china] fixture designed for liquid-trap-seal operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  Without water supply.

b. Trap-Seal Method:  Proprietary cartridge or trap system.

c. Color:  [White] <Insert color>.

d. Outlet Size:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].  Include transition coupling, if required.

e. Trap-Sealing Liquid:  Proprietary.

f. Fixture Support:  Urinal <Insert designation> chair carrier.

2.18 BIDETS

Copy and edit first paragraph and subparagraphs below for each type bidet required.

A. Bidets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Crane Plumbing, L.L.C./Fiat Products.

d. Duravit USA, Inc.

e. Eljer.

f. Gerber Plumbing Fixtures LLC.

g. Kohler Co.

h. Mansfield Plumbing Products, Inc.

i. St. Thomas Creations.

j. <Insert manufacturer's name.>

4. Description:  Floor-mounting, vitreous-china fixture with fittings.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  With [spray] [flushing rim] [spray and flushing rim] and overflow.  Include bolt caps matching fixture.

b. Faucet Hole Punching:  [One] [Two] [Three] [Four] [No] hole(s).

c. Color:  [White] <Insert color>.

d. Faucet:  Fixture manufacturer's standard, or two-valve supply, provided by fixture supplier, with [vacuum breaker, diverter, submerged spray,] [over-rim filling,] pop-up waste, and chrome-plated finish.

e. Supplies:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] chrome-plated copper with stops.

f. Drain Piping:  NPS 1-1/4 (DN 32) chrome-plated, cast-brass P-trap; [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

2.19 LAVATORIES

Copy and edit paragraph and subparagraphs below for each type wall-mounting lavatory required.

A. Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for enameled, cast-iron lavatories.

a. American Standard Companies, Inc.

b. Commercial Enameling Company.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

Select from list below for vitreous-china lavatories.

f. American Standard Companies, Inc.

g. Barclay Products, Ltd.

h. Briggs Plumbing Products, Inc.

i. Crane Plumbing, L.L.C./Fiat Products.

j. Eljer.

k. Gerber Plumbing Fixtures LLC.

l. Kohler Co.

m. Mansfield Plumbing Products, Inc.

n. Peerless Pottery, Inc.

o. Sterling Plumbing Group, Inc.

p. St. Thomas Creations.

q. TOTO USA, Inc.

r. <Insert manufacturer's name.>

4. Description:  [Accessible, wall] [Wall] [Wall-and-pedestal]-mounting, [enameled, cast-iron] [vitreous-china] fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 14 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Type:  [With back] [Ledge back] [Shelf back] [Slab] [Pedestal].

b. Size:  [18 by 15 inches (457 by 381 mm)] [19 by 16 inches (483 by 406 mm)] [20 by 18 inches (508 by 457 mm)] [24 by 20 inches (610 by 508 mm)] <Insert dimensions> rectangular.

c. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers].

d. Faucet Hole Location:  [Top] [Front wall] [Inclined panel].

e. Pedestal:  [Not required] [Required].

f. Color:  [White] <Insert color>.

g. Faucet:  Lavatory <Insert designation> [with pop-up waste] [for separate drain].

h. Supplies:  NPS 3/8 (DN 10) chrome-plated copper with stops.

i. Drain:  [See faucet] [Grid] [Grid with offset waste] <Insert drain>.

1) Location:  [Not applicable] [Near back of bowl] <Insert location>.

j. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or below.

k. Drain Piping:  Schedule 40 [ABS] [or] [PVC], [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], tubular waste to wall; and wall escutcheon.

Retain first subparagraph below with either of last two subparagraphs above.

1) Exception:  Omit P-trap if hair interceptor is required.

l. Hair Interceptor:  [Not required] <Insert designation.>

m. Protective Shielding Guard(s):  <Insert designation.>

n. Fixture Support:  Lavatory <Insert designation>.

Copy and edit paragraph and subparagraphs below for each type counter-mounting lavatory required.

B. Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of seven lists below.

Select from list below for enameled, cast-iron lavatories.

a. Commercial Enameling Company.

b. Eljer.

c. Kohler Co.

d. <Insert manufacturer's name.>

Select from list below for FRP lavatories.

e. Sterling Plumbing Group, Inc.

f. <Insert manufacturer's name.>

Select from list below for PMMA lavatories.

g. Benjamin Manufacturing Co., Inc.

h. Royal Baths Manufacturing Co.

i. <Insert manufacturer's name.>

Select from list below for porcelain-enameled, formed-steel lavatories.

j. American Standard Companies, Inc.

k. Bootz Plumbingware Co.

l. Briggs Plumbing Products, Inc.

m. Crane Plumbing, L.L.C./Fiat Products.

n. Eljer.

o. Mansfield Plumbing Products, Inc.

p. <Insert manufacturer's name.>

Select from list below for solid-surface lavatories.

q. American Standard Companies, Inc.

r. Avonite, Inc.

s. Bradley Corporation.

t. DuPont, Corian Products.

u. Formica Corporation.

v. Franke Consumer Products, Inc., Kitchen Systems Div.

w. Lippert Corporation.

x. Rynone Manufacturing Corp.

y. Swan Corporation (The).

z. <Insert manufacturer's name.>

Select from list below for stainless-steel lavatories.

aa. Acorn Engineering Company.

ab. Elkay Manufacturing Co.

ac. Intersan Manufacturing Company.

ad. Just Manufacturing Company.

ae. <Insert manufacturer's name.>

Select from list below for vitreous-china lavatories.

af. American Standard Companies, Inc.

ag. Barclay Products, Ltd.

ah. Briggs Plumbing Products, Inc.

ai. Crane Plumbing, L.L.C./Fiat Products.

aj. Eljer.

ak. Gerber Plumbing Fixtures LLC.

al. Kohler Co.

am. Mansfield Plumbing Products, Inc.

an. Peerless Pottery, Inc.

ao. Sterling Plumbing Group, Inc.

ap. St. Thomas Creations.

aq. TOTO USA, Inc.

ar. <Insert manufacturer's name.>

4. Description:  [Accessible] [Counter-mounting] [Undercounter-mounting], [enameled, cast-iron] [FRP] [PMMA] [porcelain-enameled, formed-steel] [solid-surface] [stainless-steel] [vitreous-china] fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 14 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Type:  [Flat rim with ledge] [Self-rimming].

Retain one of first three subparagraphs below.

b. Rectangular Lavatory Size:  [18 by 15 inches (457 by 381 mm)] [19 by 16 inches (483 by 406 mm)] [20 by 18 inches (508 by 457 mm)] [24 by 20 inches (610 by 508 mm)] <Insert dimensions>.

c. Oval Lavatory Size:  [19 by 16 inches (483 by 406 mm)] [20 by 17 inches (508 by 432 mm)] <Insert dimensions>.

d. Round Lavatory Size:  [18 inches (457 mm)] [19 inches (483 mm)] <Insert dimensions> in diameter.

e. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers].

f. Faucet Hole Location:  [Top] [Front wall] [Inclined panel].

g. Color:  [White] <Insert color>.

h. Faucet:  Lavatory <Insert designation> [with pop-up waste] [for separate drain].

i. Supplies:  NPS 3/8 (DN 10) chrome-plated copper with stops.

j. Drain:  [See faucet] [Grid] [Grid with offset waste] <Insert drain>.

1) Location:  [Not applicable] [Near back of bowl] <Insert location>.

k. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or below.

l. Drain Piping:  Schedule 40 [ABS] [or] [PVC], [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], tubular waste to wall; and wall escutcheon.

Retain first subparagraph below with either of last two subparagraphs above.

1) Exception:  Omit P-trap if hair interceptor is required.

m. Hair Interceptor:  [Not required] <Insert designation>.

n. Protective Shielding Guard(s):  <Insert designation.>

Copy and edit paragraph and subparagraphs below for each type countertop with integral bowl lavatory required.

C. Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for cultured-marble countertop lavatories.  Usually manufacturers of cultured-marble products only sell locally.  See the International Cast Polymer Alliance's Web site at www.icpa-hq.com for a list of manufacturers near Project site.

a. Crane Plumbing, L.L.C./Fiat Products.

b. RSI Home Products.

c. Rynone Manufacturing Corp.

d. <Insert manufacturer's name.>

Select from list below for solid-surface countertop lavatories.

e. Avonite, Inc.

f. DuPont, Corian Products.

g. Formica Corporation.

h. Lippert Corporation.

i. Swan Corporation (The).

j. Wilsonart International.

k. <Insert manufacturer's name.>

4. Description:  [Accessible ]countertop with integral bowl fixtures for mounting on base unit.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, the requirements in 12 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Backsplash:  [Integral with countertop] [Separate, same material as countertop] [Not required].

b. Overall Rectangular Top Size:  [25 by 17 inches (635 by 432 mm)] [31 by 19 inches (787 by 483 mm)] [49 by 22 inches (1245 by 559 mm)] [73 by 22 inches (1854 by 559 mm)] <Insert dimensions> with [1] [2] [3] [4] bowl(s).

1) Bowl Size:  Oval [19 by 16 inches (483 by 406 mm)] [20 by 17 inches (508 by 432 mm)] <Insert dimensions>.

c. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers].

d. Faucet Hole Location:  [Countertop] <Insert location>.

e. Color:  [White] <Insert color>.

f. Faucet(s):  Lavatory <Insert designation> [with pop-up waste] [with separate drain] for each bowl.

g. Supplies:  NPS 3/8 (DN 10) chrome-plated copper with stops.

h. Drain(s):  [See faucets] [Grid] [Grid with offset waste] <Insert drain>.

1) Location:  [Not applicable] [Near back of bowl] <Insert location>.

i. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or first subparagraph below.

j. Drain Piping:  Schedule 40 [ABS] [or] [PVC], [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], tubular waste to wall; and wall escutcheon.

k. Hair Interceptor(s):  <Insert designation> for bowls as indicated.

l. Protective Shielding Guard(s):  <Insert designation> for bowls as indicated.

Copy and edit paragraph and subparagraphs below for each type lavatory required for wheelchair-bound persons.

D. Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Crane Plumbing, L.L.C./Fiat Products.

d. Eljer.

e. Kohler Co.

f. Mansfield Plumbing Products, Inc.

g. Peerless Pottery, Inc.

h. St. Thomas Creations.

i. <Insert manufacturer's name.>

4. Description:  Accessible, wall-mounting, vitreous-china fixture designed for people in wheelchairs.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 10 subparagraphs below may be reduced or omitted.

a. Type:  [Ledge back] [Shelf back] [Slab] <Insert type>.

b. Size:  [20 by 26 inches (508 by 660 mm)] <Insert dimensions> minimum; rectangular.

c. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers] [Three holes, 8-inch (203-mm) centers] [Three holes, 12-inch (305-mm) centers].

d. Color:  [White] <Insert color>.

Insert polished, chrome-plated, solid-brass faucet type in first subparagraph below.

e. Faucet:  Lavatory <Insert designation> for separate drain.

f. Supplies:  NPS 3/8 (DN 10) chrome-plated copper with stops.

g. Drain:  [Grid] [Grid with offset waste].

h. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or first subparagraph below.

i. Drain Piping:  Schedule 40 [ABS] [or] [PVC], [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], tubular waste to wall; and wall escutcheon.

j. Fixture Support:  Lavatory <Insert designation>.

2.20 COMMERCIAL SINKS

Caution:  Sinks in this Article are not suitable for food preparation or for use as scullery sinks.

Copy and edit paragraph and subparagraphs below for each type counter-mounting commercial sink required.

A. Commercial Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Advance Tabco.

b. Elkay Manufacturing Co.

c. Just Manufacturing Company.

d. Metal Masters Foodservice Equipment Co., Inc.

e. <Insert manufacturer's name.>

4. Description:  [One] [Two] [Three]-compartment, counter-mounting, stainless-steel commercial sink with backsplash.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

Caution:  Verify that selected sink compartments and drains are compatible.

a. Overall Dimensions:  <Insert dimensions.>

b. Metal Thickness:  [0.050 inch (1.3 mm)] <Insert dimension>.

c. Compartment:

1) Dimensions:  <Insert dimensions.>

2) Drain:  [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] [NPS 1-1/2 (DN 40) tailpiece with pop-up waste] <Insert drain>.

a) Location:  [Centered in compartment] [Near back of compartment] [Near left side of compartment] [Near right side of compartment] <Insert location>.

Retain "Compartment" Subparagraph and associated subparagraphs above for single-compartment sink or first subparagraph and associated subparagraphs below for multiple-compartment sink.

d. Each Compartment:

1) Dimensions:  <Insert dimensions.>

2) Drains: [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] [NPS 1-1/2 (DN 40) tailpiece with pop-up waste] <Insert drain>.

a) Location:  [Centered in compartment] [Near back of compartment] <Insert location>.

e. Faucet(s):  Sink <Insert designation>.

1) Number Required:  [One] [Two].

2) Mounting:  Deck.

f. Supplies:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] chrome-plated copper with stops or shutoff valves.

g. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] chrome-plated, cast-brass P-trap; [0.045-inch- (1.1-mm-) thick tubular brass] [copper pipe] waste to wall; [continuous waste; ]and wall escutcheon(s).

Copy and edit paragraph and subparagraphs below for each type freestanding, commercial sink required.

B. Commercial Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Advance Tabco.

b. AERO Manufacturing, Inc.

c. Amtekco Industries, Inc.

d. Elkay Manufacturing Co.

e. Just Manufacturing Company.

f. Marlo Manufacturing.

g. Metal Masters Foodservice Equipment Co., Inc.

h. <Insert manufacturer's name.>

4. Description:  [One] [Two] [Three]-compartment, freestanding, stainless-steel commercial sink with backsplash.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in nine subparagraphs and associated subparagraphs below may be reduced or omitted.

Caution:  Verify that selected sink compartments and drains are compatible.

a. Overall Dimensions:  <Insert dimensions.>

b. Metal Thickness:  [0.050 inch (1.3 mm)] [0.063 inch (1.6 mm)] <Insert dimension>.

c. Compartment:

1) Dimensions:  <Insert dimensions.>

2) Drain: [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] [NPS 1-1/2 (DN 40) tailpiece with pop-up waste] <Insert drain>.

a) Location:  [Centered in compartment] [Near back of compartment] [Near left side of compartment] [Near right side of compartment] <Insert location>.

Retain "Compartment" Subparagraph and associated subparagraphs above for single-compartment sink or first subparagraph and associated subparagraphs below for multiple-compartment sink.

d. Each Compartment:

1) Dimensions:  <Insert dimensions.>

2) Drains: [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] [NPS 1-1/2 (DN 40) tailpiece with pop-up waste] <Insert drain>.

a) Location:  [Centered in compartment] [Near back of compartment] <Insert location>.

e. Drainboard(s):  [Not required] [Both] [Left] [Right] side(s).

1) Dimensions Each:  [Not applicable] <Insert dimensions>.

f. Supports:  Adjustable-length, steel legs.

g. Faucet(s):  Sink <Insert designation>.

1) Number Required:  [One] [Two].

2) Mounting:  In backsplash.

h. Supplies:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] chrome-plated copper with stops or shutoff valves.

i. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] chrome-plated, cast-brass P-trap; [0.045-inch- (1.1-mm-) thick tubular brass] [copper pipe] waste to wall; [continuous waste; ]and wall escutcheon(s).

Copy and edit paragraph and subparagraphs below for each type handwash sink required.  Delete if handwash sinks are specified in Division 11 Section "Foodservice Equipment."

C. Commercial Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Advance Tabco.

b. AERO Manufacturing, Inc.

c. Amtekco Industries, Inc.

d. Elkay Manufacturing Co.

e. Just Manufacturing Company.

f. Marlo Manufacturing.

g. Metal Masters Foodservice Equipment Co., Inc.

h. <Insert manufacturer's name.>

4. Description:  Wall-mounting, stainless-steel, commercial, handwash-sink fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  Basin with radius corners, back for faucet, and support brackets.

b. Size; Approximately 17 by 16 by 5 inches (432 by 406 by 127 mm).

c. Faucet:  Back-mounting, chrome-plated, solid-brass, gooseneck type with individual valves.

d. Supplies:  NPS 1/2 (DN 15) chrome-plated copper with stops.

e. Drain:  Grid.

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

g. Fixture Support:  Sink <Insert designation> for wall-mounting installation.

2.21 SHAMPOO BOWLS

Copy and edit paragraph and subparagraphs in this Article for each type shampoo bowl required.

A. Shampoo Bowls, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for enameled, cast-iron shampoo bowls.

a. Belvedere USA Corporation; a Subsidiary of the Wella Corporation, North America.

b. <Insert manufacturer's name.>

Select from list below for PMMA shampoo bowls.

c. Belvedere USA Corporation; a Subsidiary of the Wella Corporation, North America.

d. Marble Products USA; a division of Takara Belmont.

e. <Insert manufacturer's name.>

4. Description [Enameled, cast-iron] [PMMA] fixture shaped for head rest.  Include vacuum breaker, faucet, hose and spray, drain, and mounting brackets.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs below may be reduced or omitted.

a. Color:  [White] <Insert color>.

b. Supplies:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] chrome-plated copper with stops.

c. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or first subparagraph below.

d. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap; tubular waste to wall; and wall escutcheon.

e. Hair Interceptor:  <Insert designation.>

f. Fixture Support for Counter Mounting:  Brackets or forms.

Retain subparagraph above or below.

g. Fixture Support for Wall Mounting:  Sink <Insert designation>.

2.22 WASH FOUNTAINS

Copy and edit paragraph and subparagraphs below for each type freestanding wash fountain required.

A. Wash Fountains, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. <Insert manufacturer's name.>

4. Description:  [Accessible,] [Circular,] freestanding-design, wash-up fixture.

Caution:  These fixtures require a trap with waste and vent connections for installation in the base and must have vertical vent piping through top of unit, or they may be installed with trap and vent under the floor below the fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Arrangement:  Wash-up stations facing central spray head.

b. Receptor Material:  [Precast terrazzo] [Stainless steel] [Solid surface] on base.

c. Receptor Color or Finish:  [Not applicable] <Insert if required>.

d. Size:  [36- to 39-inch (914- to 990-mm)] [54-inch (1370-mm)] diameter.

e. Number of Stations:  [Two] [Three] [Four] [Five] [Six] [Eight].

f. Control:  [Collective] [Individual], [push-button] [foot-pedal] [sensor] actuation with thermostatic valve and check stops or field-installed check valves.

g. Liquid Soap Dispensers:  [Manual] [Sensor], for each station.

h. Mounting:  Floor.

i. Supplies:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing with ball, gate, or globe valves from [bottom] [top].

j. Shroud:  [Not required] [Stainless steel of size to cover supplies and vent piping].

k. Drain:  Grid with NPS 2 (DN 50) tailpiece.

l. Trap Fitting:  [Not required] [NPS 2 (DN 50) trap with waste and vent connections].

m. Drain Piping:  [NPS 1-1/2 (DN 40),] [NPS 2 (DN 50),] waste to floor.

n. Vent Piping:  [Not required] [NPS 1-1/2 (DN 40) to ceiling].

Copy and edit paragraph and subparagraphs below for each type semicircular or corner wash fountain required.

B. Wash Fountains, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. <Insert manufacturer's name.>

4. Description:  [Accessible] [Semicircular] [Corner] design, wash-up fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Arrangement:  Wash-up stations facing central spray head.

b. Receptor Material:  [Precast terrazzo] [Stainless steel] [Solid surface] on base.

c. Receptor Color or Finish:  [Not applicable] <Insert if required>.

d. Size:  [36- to 39-inch (914- to 990-mm)] [54-inch (1370-mm)] diameter.

e. Number of Stations:  [Two] [Three] [Four].

f. Control:  [Collective] [Individual], [push-button] [foot-pedal] [sensor] actuation with thermostatic valve and check stops or field-installed check valves.

g. Liquid Soap Dispensers:  [Manual] [Sensor], for each station.

h. Mounting:  Floor and flush-to-wall with wall bracket.

i. Supplies:  [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper tubing with ball, gate, or globe valves.

j. Drain:  Grid with [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] tailpiece.

k. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] P-trap, waste to wall, and wall flange.

Copy and edit paragraph and subparagraphs below for each type wall-mounting wash fountain required.

C. Wash Fountains, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Intersan Manufacturing Company.

d. <Insert manufacturer's name.>

4. Description:  [Accessible,] [Flush-to-wall,] linear design, wash-up fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Arrangement:  Wash-up stations facing spray heads.

b. Receptor Material:  [Precast terrazzo] [Stainless steel] [Solid surface] on base.

c. Receptor Color or Finish:  [Not applicable] <Insert if required>.

d. Number of Stations:  [One] [Two] [Three] [Four].

e. Control:  [Collective] [Individual], [push-button] [sensor] actuation with thermostatic valve and check stops or field-installed check valves.

f. Liquid Soap Dispensers:  [Manual] [Sensor], for each station.

g. Mounting:  Floor mounting with bracket for attaching to wall.

h. Faucet(s):  [Push-button] [Sensor-actuated] mixing valve with check stops.

i. Supplies:  NPS 1/2 (DN 15) copper tubing with ball, gate, or globe valves.

j. Drain:  Grid with NPS 1-1/2 (DN 40) tailpiece.

k. Drain Piping:  NPS 1-1/2 (DN 40) P-trap, waste to wall, and wall flange.

2.23 BATHTUBS

Copy and edit paragraph and subparagraphs in this Article for each type bathtub required.

A. Bathtubs, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists below.

Select from list below for enameled, cast-iron bathtubs.

a. Eljer.

b. Jacuzzi, Inc.

c. Kohler Co.

d. <Insert manufacturer's name.>

Select from list below for porcelain-enameled, formed-steel bathtubs.

e. American Standard Companies, Inc.

f. Bootz Plumbingware Co.

g. Briggs Plumbing Products, Inc.

h. Crane Plumbing, L.L.C./Fiat Products.

i. Mansfield Plumbing Products, Inc.

j. <Insert manufacturer's name.>

Select from list below for FRP bathtubs.

k. Aker Plastics Co., Inc.

l. Best Bath Systems; a div. of Fiberglass Systems, Inc.

m. Clarion Bathware.

n. Florestone Products Co., Inc.

o. Praxis Industries, Inc.; Aquarius Products.

p. Sterling Plumbing Group, Inc.

q. Swan Corporation (The).

r. <Insert manufacturer's name.>

Select from list below for PMMA bathtubs.

s. Acryline USA, Inc.

t. American Standard Companies, Inc.

u. Aqua Bath Company, Inc.

v. Aqua Glass Corporation.

w. Aquatic Industries, Inc.

x. Best Bath Systems; a div. of Fiberglass Systems, Inc.

y. Clarion Bathware.

z. Crane Plumbing, L.L.C./Fiat Products.

aa. Florestone Products Co., Inc.

ab. Kohler Co.

ac. Lyons Industries, Inc.

ad. Mansfield Plumbing Products, Inc.; Acrylic Operations.

ae. Praxis Industries, Inc.; Aquarius Products.

af. St. Thomas Creations.

ag. Swan Corporation (The).

ah. <Insert manufacturer's name.>

4. Description:  [Enameled, cast-iron] [FRP] [PMMA] [Porcelain-enameled, formed-steel] fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 10 subparagraphs below may be reduced or omitted.

a. Bathing Surface:  Slip resistant.

b. Size:  [48 by 30 inches (1220 by 765 mm)] [60 by 30 inches (1525 by 765 mm)] [66 by 30 inches (1680 by 765 mm)] <Insert dimensions> [with front apron] [drop-in type].

c. Color:  [White] <Insert color>.

d. Drain Location:  [Left] [Right] end.

e. Accessibility Options:  Include grab bar and bench.

f. Faucet:  [Bathtub] [Bathtub/shower] <Insert designation>.

g. Supplies:  NPS 1/2 (DN 15) copper tubing with ball, gate, or globe valves.

h. Drain:  NPS 1-1/2 (DN 40); chrome-plated exposed parts; brass pop-up waste and overflow.

i. Drain Piping:  NPS 1-1/2 (DN 40) cast-brass P-trap and waste.

Retain subparagraph above or below.

j. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap and waste.

2.24 INDIVIDUAL SHOWERS

Copy and edit paragraph and subparagraphs below for each type individual shower enclosure required.

A. Individual Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for FRP showers.

a. Aker Plastics Co., Inc.

b. Aqua Glass Corporation.

c. Clarion Bathware.

d. Florestone Products Co., Inc.

e. LASCO Bathware.

f. Praxis Industries, Inc.; Aquarius Products.

g. Sterling Plumbing Group, Inc.

h. Swan Corporation (The).

i. <Insert manufacturer's name.>

Select from list below for PMMA showers.

j. Acryline USA, Inc.

k. Aker Plastics Co., Inc.

l. Aqua Bath Company, Inc.

m. Aqua Glass Corporation.

n. Aquatic Industries, Inc.

o. Clarion Bathware.

p. Crane Plumbing, L.L.C./Fiat Products.

q. Jacuzzi, Inc.

r. Kohler Co.

s. LASCO Bathware.

t. Praxis Industries, Inc.; Aquarius Products.

u. <Insert manufacturer's name.>

4. Description:  [Accessible,] [FRP] [PMMA] shower enclosure with slip-resistant bathing surface and shower rod with curtain.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs below may be reduced or omitted.

a. Size:  [36 by 34 inches (915 by 865 mm)] [42 by 36 inches (1065 by 915 mm)] [43 by 39 inches (1090 by 990 mm)] [48 by 34 inches (1220 by 865 mm)] [52 by 36 inches (1320 by 915 mm)] [60 by 36 inches (1525 by 915 mm)] [72 by 36 inches (1830 by 915 mm)] <Insert dimensions>.

b. Surround:  One piece[ or sealed, multiple piece].

Retain subparagraph above for FRP shower or first subparagraph below for PMMA shower.

c. Surround:  One piece.

d. Color:  [White] <Insert color>.

e. Drain Location:  [Left side] [Center] [Right side].

f. Accessibility Options:  Include grab bar and bench.

g. Faucet:  Shower <Insert designation>.

h. Drain:  Grid, NPS 2 (DN 50).

Shower in paragraph below is for built-up showers and consists of shower faucet and may have a receptor.  Piping may be concealed or exposed.  Coordinate with Architectural Drawings.

Copy and edit paragraph and subparagraphs below for each type individual built-up shower required.

B. Individual Showers, <Insert drawing designation>:

1. Description:  Components for built-up shower.

a. Shower Faucet:  <Insert designation>.

b. Receptor:  [Not required] <Insert shower receptor designation>.

Copy and edit paragraph and subparagraphs below for each type individual cabinet shower required.

C. Individual Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Crane Plumbing, L.L.C./Fiat Products.

b. Mustee, E. L. & Sons, Inc.

c. Stern-Williams Co., Inc.

d. Swan Corporation (The).

e. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, [accessible, ]cabinet type with faucet and receptor.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  [30 by 30 inches (760 by 760 mm)] [32 by 32 inches (815 by 815 mm)] [36 by 36 inches (915 by 915 mm)] [36 by 39 inches (915 by 990 mm)] [45 by 39 inches (1145 by 990 mm)] <Insert dimensions>.

b. Material:  [Steel] [Composite] [Plastic], [front] [corner] [front and rear] access.

c. Color:  [Not applicable] <Insert color>.

d. Accessibility Options:  Grab bar and bench.

e. Faucet:  Shower <Insert designation>.

f. Supplies:  NPS 1/2 (DN 15) copper tubing[ with ball, gate, or globe valves].

g. Drain:  Grid, NPS 2 (DN 50).

2.25 GROUP SHOWERS

Copy and edit paragraph and subparagraphs below for each type group-shower column required.

A. Group Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. <Insert manufacturer's name.>

4. Description:  Stainless-steel column fixture with [two] [three] [four] [five] [six] individual showers.

Caution:  These fixtures require a trap with waste and vent connections for installation in the base and must have vertical vent piping through top of unit, or they may be installed with trap and vent under the floor below the fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 10 subparagraphs below may be reduced or omitted.

a. Height to Shower Heads:  [66 inches (1675 mm)] [72 inches (1830 mm)] <Insert dimension>.

b. Control:  [Thermostatic] [Pressure-balance] valve with individual hot- and cold-water mixing valve operation.

Retain and edit subparagraph above or first subparagraph below.  There are many possible combinations of options.

c. Control:  Thermostatic valve with individual tempered-water supply and [push-button] [sensor] operation.

d. Flow Control:  [2 gpm (7.6 L/min.)] [2.5 gpm (9.5 L/min.)] for each shower head.

e. Liquid Soap Dispenser:  For each shower.

f. Mounting:  Floor flange.

g. Supplies:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing with ball, gate, or globe valves from [bottom] [top].

h. Shroud:  [Not required] [Stainless steel of size to cover supplies and vent piping].

i. Drain Fitting:  [NPS 3 (DN 80)] [NPS 4 (DN 100)] outlet with NPS 2 (DN 50) vent, integral with base of column.

j. Vent Piping:  [Not required] [NPS 2 (DN 50) to ceiling].

Copy and edit paragraph and subparagraphs below for each type wall-mounting group shower required.

B. Group Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. <Insert manufacturer's name.>

4. Description:  Wall-mounting fixture with stainless-steel surface enclosure with [two] [three] individual showers.

a. Control:  [Thermostatic] [Pressure-balance] valve with individual hot- and cold-water mixing valve operation.

Retain and edit subparagraph above or first subparagraph below.  There are many possible combinations of options.

b. Control:  Thermostatic valve with individual tempered-water supply and [push-button] [sensor] operation.

c. Flow Control:  [2 gpm (7.6 L/min.)] [2.5 gpm (9.5 L/min.)] for each shower head.

d. Liquid Soap Dispenser:  For each shower.

e. Mounting:  Wall bracket.

f. Supplies:  NPS 3/4 (DN 20) copper tubing with ball, gate, or globe valves.

Copy and edit paragraph and subparagraphs below for each type plastic group shower required.

C. Group Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ShowerTower Inc.

b. <Insert manufacturer's name.>

4. Description:  Freestanding, plastic group-shower fixture.

Number of stations in two subparagraphs below must be limited to a combined total of six.  Two showers and one foot wash are typical.

a. Number of Shower Stations:  [One] [Two] [Three] [Four] <Insert number up to six> with individual self-closing control valve(s).

b. Number of Foot Wash Stations:  [One] [Two] <Insert number> with individual self-closing control valve(s).

c. Hose Bibb:  [Not] [One] required.

d. Control-Valve Mounting Height:  [50 inches (1270 mm)] [48 inches (1219 mm)].

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

e. Material:  Cast-filled-polymer plastic.

f. Color:  [Gray] <Insert color>.

g. Internal Piping:  Factory installed.

h. Mounting:  Base flange with bolt holes.

Copy and edit paragraph and subparagraphs below for each type steel group shower required.

D. Group Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Most Dependable Fountains, Inc.

b. Stern-Williams Co., Inc.

c. <Insert manufacturer's name.>

4. Description:  Freestanding, steel group-shower fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Number of Shower Stations:  [One] [Two] with individual self-closing control valve(s).

b. Number of Foot Wash Stations:  [One] [Two] with individual self-closing control valve(s).

c. Material:  Painted steel pipe.

d. Color:  [Blue] <Insert color>.

e. Internal Piping:  Factory installed.

f. Mounting:  Base flange with bolt holes.

2.26 WHIRLPOOL BATHTUBS

Whirlpool bathtubs in this Article are usually the drop-in-type mounted in a base unit.  Some units are freestanding with a front apron.  Both types require access to equipment.

Copy and edit paragraph and subparagraphs below for each type water-circulation hydromassage whirlpool bathtub required.

A. Whirlpool Bathtubs, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists below.

Select from list below for enameled, cast-iron whirlpool bathtubs.

a. Eljer.

b. Kohler Co.

c. <Insert manufacturer's name.>

Select from list below for FRP whirlpool bathtubs.

d. Aker Plastics Co., Inc.

e. Best Bath Systems; a div. of Fiberglass Systems, Inc.

f. Clarion Bathware.

g. Praxis Industries, Inc.; Aquarius Products.

h. Sterling Plumbing Group, Inc.

i. <Insert manufacturer's name.>

Select from list below for PMMA whirlpool bathtubs.

j. Aker Plastics Co., Inc.

k. American Standard Companies, Inc.

l. American Whirlpool Products Corp.

m. Aqua Glass Corporation.

n. Aquatic Industries, Inc.

o. Benjamin Manufacturing Co., Inc.

p. Clarion Bathware.

q. Clarke Products, Inc.

r. Crane Plumbing, L.L.C./Fiat Products.

s. Eljer.

t. Florestone Products Co., Inc.

u. Jacuzzi, Inc.

v. Jason International, Inc.

w. Kohler Co.

x. LASCO Bathware.

y. Lyons Industries, Inc.

z. Mansfield Plumbing Products, Inc.; Acrylic Operations.

aa. Praxis Industries, Inc.; Aquarius Products.

ab. Royal Baths Manufacturing Co.

ac. Southland Spa & Sauna Inc.

ad. <Insert manufacturer's name.>

Select from list below for porcelain-enameled, formed-steel whirlpool bathtubs.

ae. American Standard Companies, Inc.

af. Mansfield Plumbing Products, Inc.

ag. <Insert manufacturer's name.>

4. Description:  Packaged, [enameled, cast-iron] [FRP] [PMMA] [porcelain-enameled, formed-steel] hydromassage bathtub with air-entrained-water jet nozzles and water circulation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 17 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Seating Capacity:  [One] [Two] <Insert number> person(s).

b. Bathing Surface:  Slip resistant.

c. Size:  [60 by 30 inches (1525 by 765 mm)] [66 by 30 inches (1680 by 765 mm)] [60 by 42 inches (1525 by 1065 mm)] <Insert dimensions>.

d. Nominal Water Capacity:  <Insert gal. (L).>

e. Base for Drop-in Unit:  <Insert description> with access panel.

Retain subparagraph above or first subparagraph below.

f. Apron:  Matching unit, covering exposed front and sides, and with access panel.

g. Color:  [White] <Insert color>.

h. Drain Location:  [Left] [Right] end.

Add specific controls required to first subparagraph below.

i. Controls:  For pump[, timer,] [and water heater].

j. Faucet:  Fixture manufacturer's [individual valves] [mixing valve] with over-rim tub filler.

k. Supplies:  NPS 1/2 (DN 15) copper tubing with ball, gate, or globe valves.

l. Drain:  NPS 1-1/2 (DN 40); chrome-plated exposed parts; brass pop-up waste and overflow.

m. Drain Piping:  NPS 1-1/2 (DN 40) cast-brass P-trap and waste.

Retain subparagraph above or first subparagraph below.

n. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap and waste.

o. Water-Circulating System:  Electric circulating pump and plastic piping.

Retain first subparagraph below if a water heater is required.

p. Water Heater:  Electric, inline.

q. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type airmassage whirlpool bathtub required.

B. Whirlpool Bathtubs, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acryline USA, Inc.

b. American Standard Companies, Inc.

c. American Whirlpool Products Corp.

d. Aqua Glass Corporation.

e. Aquatic Industries, Inc.

f. Jacuzzi, Inc.

g. Jason International, Inc.

h. Ultra Baths, Inc.

i. <Insert manufacturer's name.>

4. Description:  Packaged, PMMA airmassage bathtub with air-injection nozzles.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 16 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Seating Capacity:  [One] [Two] <Insert number> person(s).

b. Bathing Surface:  Slip resistant.

c. Size:  [60 by 30 inches (1525 by 765 mm)] [66 by 30 inches (1680 by 765 mm)] [60 by 42 inches (1525 by 1065 mm)] <Insert dimensions>.

d. Nominal Water Capacity:  <Insert gal. (L).>

e. Base for Drop-in Unit:  <Insert description> with access panel.

Retain subparagraph above or first subparagraph below.

f. Apron:  Matching unit, covering exposed front and sides, and with access panel.

g. Color:  [White] <Insert color>.

h. Drain Location:  [Left] [Right] end.

In first subparagraph below, add specific controls if required.

i. Controls:  For blower[, timer,] [and water heater].

j. Faucet:  Fixture manufacturer's [individual valves] [mixing valve] with over-rim tub filler.

k. Supplies:  NPS 1/2 (DN 15) copper tubing with ball, gate, or globe valves.

l. Drain:  NPS 1-1/2 (DN 40); chrome-plated exposed parts; brass pop-up waste and overflow.

m. Drain Piping:  NPS 1-1/2 (DN 40) cast-brass P-trap and waste.

Retain subparagraph above or below.

n. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap and waste.

Retain first subparagraph below with either of last two subparagraphs above.

o. Air-Injection System:  Electric, [blower] [combination blower/heater] and plastic piping.

p. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert value> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

2.27 KITCHEN SINKS

Copy and edit paragraph and subparagraphs below for each type kitchen sink required.

A. Kitchen Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of five lists below.

Select from list below for enameled, cast-iron kitchen sinks.

a. Commercial Enameling Company.

b. Eljer.

c. Jacuzzi, Inc.

d. Kohler Co.

e. <Insert manufacturer's name.>

Select from list below for PMMA kitchen sinks.

f. Gerber Plumbing Fixtures LLC.

g. Lyons Industries, Inc.

h. <Insert manufacturer's name.>

Select from list below for porcelain-enameled, formed-steel kitchen sinks.

i. American Standard Companies, Inc.

j. Bootz Plumbingware Co.

k. Briggs Plumbing Products, Inc.

l. Eljer.

m. Mansfield Plumbing Products, Inc.

n. <Insert manufacturer's name.>

Select from list below for solid-surface kitchen sinks.

o. Avonite, Inc.

p. DuPont, Corian Products.

q. FHP Kindred USA.

r. Formica Corporation.

s. Franke Consumer Products, Inc., Kitchen Systems Div.

t. Lippert Corporation.

u. Rynone Manufacturing Corp.

v. Swan Corporation (The).

w. Wilsonart International.

x. <Insert manufacturer's name.>

Select from list below for stainless-steel kitchen sinks.

y. Dayton Products, Inc.

z. Elkay Manufacturing Co.

aa. Franke Consumer Products, Inc., Kitchen Systems Div.

ab. Just Manufacturing Company.

ac. Kohler Co.

ad. Moen, Inc.

ae. Revere Sink.

af. Sterling Plumbing Group, Inc.

ag. Teka USA.

ah. WhiteRock Corp.

ai. <Insert manufacturer's name.>

4. Description:  [One] [Two] [Three]-bowl, residential, counter-mounting, [enameled, cast-iron] [PMMA] [porcelain-enameled, formed-steel] [solid-surface] [stainless-steel] kitchen sink.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 13 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Overall Dimensions:  <Insert dimensions.>

b. Metal Thickness:  [0.038 inch (1.0 mm)] [0.050 inch (1.3 mm)] <Insert dimension>.

c. Bowl:

1) Dimensions:  <Insert dimensions.>

2) Drain:  3-1/2-inch (89-mm) [crumb cup] [grid] [grid with offset waste] [outlet for disposer].

a) Location:  [Centered in bowl] [Near back of bowl] <Insert location>.

Retain "Bowl" Subparagraph and associated subparagraphs above for single-bowl sink or first two or all three bowl subparagraphs and associated subparagraphs below for multibowl sink.

d. Left Bowl:

1) Dimensions:  <Insert dimensions.>

2) Drain:  3-1/2-inch (89-mm) [crumb cup] [grid] [grid with offset waste] [outlet for disposer].

a) Location:  [Centered in bowl] [Near back of bowl] <Insert location>.

e. Right Bowl:

1) Dimensions:  <Insert dimensions.>

2) Drain:  3-1/2-inch (89-mm) [crumb cup] [grid] [grid with offset waste] [outlet for disposer].

a) Location:  [Centered in bowl] [Near back of bowl] <Insert location>.

f. Center Bowl:

1) Dimensions:  <Insert dimensions.>

2) Drain:  [1-1/2-inch (38-mm)] [3-1/2-inch (89-mm)] [crumb cup] [grid] [grid with offset waste].

a) Location:  [Centered in bowl] <Insert location>.

g. Sink Faucet:  <Insert designation.>

h. Supplies:  NPS 1/2 (DN 15) chrome-plated copper with stops.

i. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; [continuous waste; ]and wall escutcheon(s).

Retain subparagraph above or first subparagraph below.

j. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap; tubular waste to wall; [continuous waste; ]and wall escutcheon(s).

k. Disposer:  [Not required] <Insert designation>.

l. Dishwasher Air-Gap Fitting:  [Required] [Not required].

m. Hot-Water Dispenser:  [Not required] <Insert designation.>

Copy and edit paragraph and subparagraphs below for each type bar sink required.

B. Bar Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of five lists below.

Select from list below for enameled, cast-iron bar sinks.

a. Commercial Enameling Company.

b. Eljer.

c. Jacuzzi, Inc.

d. Kohler Co.

e. <Insert manufacturer's name.>

Select from list below for PMMA kitchen sinks.

f. Benjamin Manufacturing Co., Inc.

g. Gerber Plumbing Fixtures LLC.

h. Lippert Corporation.

i. Lyons Industries, Inc.

j. Royal Baths Manufacturing Co.

k. <Insert manufacturer's name.>

Select from list below for porcelain-enameled, formed-steel bar sinks.

l. American Standard Companies, Inc.

m. Bootz Plumbingware Co.

n. Briggs Plumbing Products, Inc.

o. Eljer.

p. Mansfield Plumbing Products, Inc.

q. <Insert manufacturer's name.>

Select from list below for solid-surface bar sinks.

r. Avonite, Inc.

s. DuPont, Corian Products.

t. Formica Corporation.

u. Swan Corporation (The).

v. <Insert manufacturer's name.>

Select from list below for stainless-steel bar sinks.

w. Barclay Products, Ltd.

x. Dayton Products, Inc.

y. Elkay Manufacturing Co.

z. Franke Consumer Products, Inc.; Kitchen Systems Div.

aa. Just Manufacturing Company.

ab. Kohler Co.

ac. Moen, Inc.

ad. Revere Sink.

ae. Sterling Plumbing Group, Inc.

af. WhiteRock Corp.

ag. <Insert manufacturer's name.>

4. Description:  Single-bowl, residential, counter-mounting, [enameled, cast-iron] [PMMA] [stainless-steel] [porcelain-enameled, cast-iron] [solid-surface] bar sink.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs below may be reduced or omitted.

a. Overall Dimensions:  <Insert dimensions.>

b. Bowl Dimensions:  <Insert dimensions.>

c. Sink Faucet:  <Insert designation.>

d. Supplies:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] chrome-plated copper with stops.

e. Drain:  [1-1/2-inch (38-mm)] [3-1/2-inch (89-mm)] [crumb cup] [grid] [grid with offset waste].

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or first subparagraph below.

g. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap; tubular waste to wall; and wall escutcheon.

h. Protective Shielding Guard(s):  <Insert designation.>

2.28 SERVICE SINKS

Copy and edit paragraph and subparagraphs below for each type trap-standard service sink required.

A. Service Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for enameled, cast-iron service sinks.

a. American Standard Companies, Inc.

b. Commercial Enameling Company.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

Select from list below for vitreous-china service sinks.

f. Crane Plumbing, L.L.C./Fiat Products.

g. Eljer.

h. Kohler Co.

i. <Insert manufacturer's name.>

4. Description:  Trap-standard- and wall-mounting, [enameled, cast-iron fixture with roll-rim] [vitreous-china fixture] with [plain] [two faucet holes in] back and rim guard on front and sides.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs below may be reduced or omitted.

a. Size:  [22 by 18 inches (560 by 460 mm)] [24 by 20 inches (610 by 510 mm)].

Retain subparagraph above for cast-iron fixture or first subparagraph below for vitreous-china fixture.

b. Size:  [19 by 16 inches (480 by 405 mm)] [22 by 20 inches (560 by 510 mm)].

c. Color:  White.

Polished or rough, chrome-plated, solid-brass faucet is recommended.  Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.  Use type with wall brace if faucet will be mounted above back.

d. Faucet:  Sink <Insert designation>.

e. Drain:  Grid with [NPS 2 (DN 50)] [NPS 3 (DN 80)] outlet.

f. Trap Standard:  [NPS 2 (DN 50)] [NPS 3 (DN 80)] enameled, cast iron with cleanout and floor flange.

g. Fixture Support:  Sink <Insert designation>.

Copy and edit paragraph and subparagraphs below for each type floor-mounting service sink required.

B. Service Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Commercial Enameling Company.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

4. Description:  Floor-mounting, enameled, cast-iron fixture with front apron, raised back, and coated, wire rim guard.

Caution:  This type of service sink requires a drainage piping trap under the fixture.  This trap is not part of fixture fittings.

a. Size:  28 by 28 inches (710 by 710 mm).

b. Color:  White.

Polished or rough, chrome-plated, solid-brass faucet with wall brace is recommended.  Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

c. Faucet:  Sink <Insert designation>.

d. Drain:  Grid with [NPS 2 (DN 50)] [NPS 3 (DN 80)] outlet.

2.29 SERVICE BASINS

Copy and edit paragraph and subparagraphs in this Article for each type service basin required.

A. Service Basins, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for terrazzo service basins.

a. Acorn Engineering Company.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Florestone Products Co., Inc.

d. Precast Terrazzo Enterprises, Inc.

e. Stern-Williams Co., Inc.

f. <Insert manufacturer's name.>

Select from list below for plastic (cast-polymer) service basins.

g. Crane Plumbing, L.L.C./Fiat Products.

h. Florestone Products Co., Inc.

i. Mustee, E. L. & Sons, Inc.

j. Swan Corporation (The).

k. Zurn Plumbing Products Group; Light Commercial Operation.

l. <Insert manufacturer's name.>

4. Description:  Flush-to-wall, floor-mounting, [precast terrazzo] [cast-polymer] fixture with rim guard.

Caution:  This type of fixture requires a drainage piping trap under the fixture.  This trap is not part of fixture fittings.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs below may be reduced or omitted.

a. Shape:  [Square] [Rectangular] [Five sided] [Radial front].

b. Size:  [24 by 24 inches (610 by 610 mm)] [28 by 28 inches (710 by 710 mm)] [24 by 36 inches (610 by 915 mm)] [32 by 32 inches (815 by 815 mm)] [36 by 36 inches (915 by 915 mm)] <Insert dimensions>.

c. Height:  [6 inches (150 mm)] [10 inches (255 mm)] [12 inches (305 mm)] [12 inches (305 mm) with dropped front] <Insert dimensions>.

Verify availability of tiling flange in subparagraph below if required and indicate side(s) if basin is rectangular.

d. Tiling Flange:  [Not required] [On one side] [On two sides] [On three sides].

Indicate front dimension on rectangular basins if rim guard is to be only on one side.

e. Rim Guard:  On [front] [all] top surfaces.

f. Color:  [Not applicable] <Insert color>.

Polished or rough, chrome-plated, solid-brass faucet with wall brace is recommended.  Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

g. Faucet:  Sink <Insert designation>.

h. Drain:  Grid with [NPS 2 (DN 50)] [NPS 3 (DN 80)] outlet.

2.30 LAUNDRY TRAYS

Copy and edit paragraph and subparagraphs in this Article for each type laundry tray required.

A. Laundry Trays, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from list below for enameled, cast-iron laundry trays.

a. Commercial Enameling Company.

b. Eljer.

c. <Insert manufacturer's name.>

Select from list below for plastic (cast-polymer, FRP, PMMA, or PP) laundry trays.

d. Crane Plumbing, L.L.C./Fiat Products.

e. Florestone Products Co., Inc.

f. Gerber Plumbing Fixtures LLC.

g. Mustee, E. L. & Sons, Inc.

h. Swan Corporation (The).

i. Zurn Plumbing Products Group; Light Commercial Operation.

j. <Insert manufacturer's name.>

4. Description:  [Stand] [Counter]-mounting, [enameled, cast-iron] [plastic] laundry trays.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs below may be reduced or omitted.

a. Size:  [24 by 21 inches (610 by 535 mm)] [25 by 22 inches (635 by 560 mm)] <Insert dimensions>.

b. Color:  [Not applicable] <Insert color>.

Polished, chrome-plated, solid-brass faucet is recommended.

c. Faucet:  Sink <Insert designation> for [fixture-ledge] [wall] [counter] mounting.

d. Supplies:  NPS 1/2 (DN 15) [chrome-plated copper with stops] [copper tubing with ball, gate, or globe valves].

e. Drain:  Grid with NPS 1-1/2 (DN 40) outlet.

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular brass waste to wall; and wall escutcheon.

Retain subparagraph above or first subparagraph below.

g. Drain Piping:  Schedule 40 [ABS] [or] [PVC], NPS 1-1/2 (DN 40) P-trap; tubular waste to wall; and wall escutcheon.

h. Stand:  [Not required] [Painted steel].

2.31 SACRISTY SINKS

Sinks in this Article are fabricated by attaching a cover with lock to one compartment of company's standard sinks.  Catalog data are limited, but many variations are available.  Verify availability of sizes and features required.

Copy and edit paragraph and subparagraphs in this Article for each type sacristy sink required.

A. Sacristy Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Just Manufacturing Company.

c. <Insert manufacturer's name.>

4. Description:  Two-bowl, counter-mounting, stainless-steel fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  Approximately [22 by 42 inches (560 by 1070 mm)] <Insert dimensions>.

b. Cover:  Hinged with lock on [left] [right] bowl.

c. Faucet:  <Insert designation.>

d. Supplies:  NPS 1/2 (DN 15) chrome-plated copper with stops.

e. Drains:  One with stopper and one with grid.

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, tubular-brass waste.  Include one trap, one direct waste without trap, separate waste piping, and wall flanges.

2.32 OWNER-FURNISHED FIXTURES

Retain this Article for existing fixtures or if new, Owner-furnished fixtures require components specified in this Section.

Copy and edit paragraph and subparagraphs in this Article for each type Owner-furnished fixture required.

A. <Insert fixture type>, <Insert drawing designation>:  [Existing, installed] [Existing, remove-and-reinstall] [Used, Owner-furnished] [New, Owner-furnished] fixture.

1. Provide the following:

Retain required attributes and features in list below.

a. Lavatory Faucet:  <Insert designation.>

b. Lavatory, Laminar-Flow Faucet Spout:  <Insert designation.>

c. Bathtub Faucet:  <Insert designation.>

d. Bathtub/Shower Faucet:  <Insert designation.>

e. Shower Faucet:  <Insert designation.>

f. Sink Faucet:  <Insert designation.>

g. Sink, Laminar-Flow Faucet Spout:  <Insert designation.>

h. Flushometer:  <Insert designation.>

i. Toilet Seat:  <Insert designation.>

j. Direct-Connected Drain Piping:  [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] [chrome-plated, cast-brass] [cast-brass] [plastic] P-trap, and tubular waste to wall with wall flange.

k. Indirect Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] [chrome-plated-brass] [brass or copper] [plastic] tubular waste.

l. Protective Shielding Guard(s):  <Insert designation.>

m. Fixture Support:  <Insert designation.>

n. Interceptor:  <Insert designation.>

o. Shower Receptor:  <Insert designation.>

p. Disposer:  <Insert designation.>

q. Dishwasher, Air-Gap Fitting:  <Insert designation.>

r. Hot-Water Dispenser:  <Insert designation.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in of water supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before plumbing fixture installation.

B. Examine cabinets, counters, floors, and walls for suitable conditions where fixtures will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Assemble plumbing fixtures, trim, fittings, and other components according to manufacturers' written instructions.

B. Install off-floor supports, affixed to building substrate, for wall-mounting fixtures.

1. Use carrier supports with waste fitting and seal for back-outlet fixtures.

2. Use carrier supports without waste fitting for fixtures with tubular waste piping.

3. Use chair-type carrier supports with rectangular steel uprights for accessible fixtures.

First paragraph below applies to wall-mounting fixtures such as water closets and urinals.

C. Install back-outlet, wall-mounting fixtures onto waste fitting seals and attach to supports.

D. Install floor-mounting fixtures on closet flanges or other attachments to piping or building substrate.

First paragraph below applies to wall-mounting fixtures such as lavatories and most sinks.

E. Install wall-mounting fixtures with tubular waste piping attached to supports.

F. Install floor-mounting, back-outlet water closets attached to building floor substrate and wall bracket and onto waste fitting seals.

First paragraph below applies to counter-mounting fixtures such as lavatories and sinks.

G. Install counter-mounting fixtures in and attached to casework.

H. Install fixtures level and plumb according to roughing-in drawings.

I. Install water-supply piping with stop on each supply to each fixture to be connected to water distribution piping.  Attach supplies to supports or substrate within pipe spaces behind fixtures.  Install stops in locations where they can be easily reached for operation.

1. Exception:  Use ball, gate, or globe valves if supply stops are not specified with fixture.  Valves are specified in Division 15 Section "Valves."

J. Install trap and tubular waste piping on drain outlet of each fixture to be directly connected to sanitary drainage system.

K. Install tubular waste piping on drain outlet of each fixture to be indirectly connected to drainage system.

L. Install flushometer valves for accessible water closets and urinals with handle mounted on wide side of compartment.  Install other actuators in locations that are easy for people with disabilities to reach.

M. Install tanks for accessible, tank-type water closets with lever handle mounted on wide side of compartment.

N. Install toilet seats on water closets.

O. Install trap-seal liquid in dry urinals.

P. Install faucet-spout fittings with specified flow rates and patterns in faucet spouts if faucets are not available with required rates and patterns.  Include adapters if required.

Q. Install water-supply flow-control fittings with specified flow rates in fixture supplies at stop valves.

R. Install faucet flow-control fittings with specified flow rates and patterns in faucet spouts if faucets are not available with required rates and patterns.  Include adapters if required.

S. Install shower flow-control fittings with specified maximum flow rates in shower arms.

T. Install traps on fixture outlets.

1. Exception:  Omit trap on fixtures with integral traps.

2. Exception:  Omit trap on indirect wastes, unless otherwise indicated.

U. Install disposer in outlet of each sink indicated to have disposer.  Install switch where indicated or in wall adjacent to sink if location is not indicated.

V. Install dishwasher air-gap fitting at each sink indicated to have air-gap fitting.  Install [in sink deck] [on countertop at sink] <Insert location>.  Connect inlet hose to dishwasher and outlet hose to disposer.

W. Install hot-water dispensers in back top surface of sink or in countertop with spout over sink.

X. Install escutcheons at piping wall ceiling penetrations in exposed, finished locations and within cabinets and millwork.  Use deep-pattern escutcheons if required to conceal protruding fittings.  Escutcheons are specified in Division 15 Section "Basic Mechanical Materials and Methods."

Y. Set [bathtubs] [shower receptors] [and] [service basins] in leveling bed of cement grout.  Grout is specified in Division 15 Section "Basic Mechanical Materials and Methods."

Delete paragraph below if sealants are specified in Division 7 Section "Joint Sealants."

Z. Seal joints between fixtures and walls, floors, and countertops using sanitary-type, one-part, mildew-resistant silicone sealant.  Match sealant color to fixture color.  Sealants are specified in Division 7 Section "Joint Sealants."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping.  Use size fittings required to match fixtures.

C. Ground equipment according to Division 16 Section "Grounding and Bonding."

D. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Verify that installed plumbing fixtures are categories and types specified for locations where installed.

B. Check that plumbing fixtures are complete with trim, faucets, fittings, and other specified components.

C. Inspect installed plumbing fixtures for damage.  Replace damaged fixtures and components.

D. Test installed fixtures after water systems are pressurized for proper operation.  Replace malfunctioning fixtures and components, then retest.  Repeat procedure until units operate properly.

E. Install fresh batteries in sensor-operated mechanisms.

3.5 ADJUSTING

A. Operate and adjust faucets and controls.  Replace damaged and malfunctioning fixtures, fittings, and controls.

In paragraph below, delete appliances not included in this Section.

B. Operate and adjust [disposers] [hot-water dispensers] [and] [controls].  Replace damaged and malfunctioning units[ and controls].

Delete fixture types in first paragraph below not in Project.

C. Adjust water pressure at [faucets] [and] [flushometer valves] to produce proper flow and stream.

D. Replace washers and seals of leaking and dripping faucets and stops.

E. Install fresh batteries in sensor-operated mechanisms.

3.6 CLEANING

A. Clean fixtures, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.  Do the following:

1. Remove faucet spouts and strainers, remove sediment and debris, and reinstall strainers and spouts.

2. Remove sediment and debris from drains.

B. After completing installation of exposed, factory-finished fixtures, faucets, and fittings, inspect exposed finishes and repair damaged finishes.

3.7 PROTECTION

A. Provide protective covering for installed fixtures and fittings.

B. Do not allow use of plumbing fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 15410END OF SECTION 15410

PLUMBING FIXTURES
15410 - 1

