Copyright 2001 AIA
MASTERSPEC
09/01 (R 12/02)

Copyright 2001 (R 12/02), The American Institute of Architects (AIA)

SECTION 15445 - SEWAGE PUMPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following sewage pumps and accessories for sanitary drainage piping systems in buildings:

1. Wet-pit-mounted, vertical sewage pumps.

2. Submersible sewage pumps.

3. Sewage pump reverse-flow assemblies.

4. Sewage pump [basins] [basins and pits] [pits].

5. Packaged, submersible sewage pump units.

6. Packaged, wastewater pump units.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Packaged Pumping Stations" for applications in site-construction sewage pumping.

2. Division 15 Section "Sump Pumps" for applications in storm-drainage systems.

1.3 SUBMITTALS

A. Product Data:  For each type and size of sewage pump specified.  Include certified performance curves with operating points plotted on curves; and rated capacities of selected models, furnished specialties, and accessories.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Operation and Maintenance Data:  For each sewage pump to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of sewage pumps and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Retain shipping flange protective covers and protective coatings during storage.

B. Protect bearings and couplings against damage.

C. Comply with pump manufacturer's written rigging instructions for handling.

1.6 COORDINATION

Select from options in paragraph below depending on whether Part 2 "Sewage Pump Pits" or "Packaged, Wastewater Pump Units" Article is retained.

A. Coordinate size and location of concrete [bases] [bases and pits] [pits].  Concrete, reinforcement, and formwork requirements are specified in Division 3.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Refer to the sewage pump tables at the end of the Evaluations for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 WET-PIT-MOUNTED, VERTICAL SEWAGE PUMPS

Select "Sewage Pump Reverse-Flow Assemblies" Article if required.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alyan Pump Company.

2. Armstrong Pumps Inc.

3. Aurora Pump; Pentair Pump Group (The).

4. Chicago Pump Company; a division of Yeomans Chicago Corporation.

5. Deming Pumps; Crane Pumps & Systems.

6. Federal Pump Corp.

7. Paco Pumps, Inc.

8. Sterling Peerless; Sterling Fluid Systems Group.

9. Swaby Manufacturing Co.

10. Tramco Pump Company.

11. Vertiflo Pump Company.

12. Weil Pump Company, Inc.

13. Weinman Div.; Crane Pumps & Systems.

14. Yeomans Chicago Corporation.

15. <Insert manufacturer's name.>

Retain option in first paragraph below for duplex units only.

B. Description:  Factory-assembled and -tested, single-stage, centrifugal, end-suction sewage pumps complying with UL 778.  Vertical, separately coupled, suspended pumps complying with HI 1.1-1.2 and HI 1.3 for wet-pit-volute sewage pumps[ and with reverse-flow assembly].

1. Pump Arrangement:  [Simplex] [Duplex] [Multiplex].

2. Casing:  Cast iron, with open inlet and threaded connection for NPS 2 (DN 50) and smaller and flanged connection for NPS 2-1/2 (DN 65) and larger discharge piping.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced, open or semiopen, nonclog design for solids handling; overhung, single suction, and keyed and secured to shaft.

4. Pump Shaft and Sleeve Bearings:  [Stainless-steel] [Stainless-steel or steel] [Steel] shaft with bronze sleeve bearings.  Include oil-lubricated, intermediate sleeve bearings at 48-inch (1200-mm) maximum intervals if basin depth is more than 48 inches (1200 mm), and grease-lubricated, ball-type thrust bearings.

5. Pump and Motor Shaft Coupling:  Flexible, capable of absorbing torsional vibration and shaft misalignment.

C. Pump Discharge Piping:  Manufacturer's standard galvanized-steel or bronze pipe.

Select from options in first paragraph below depending on whether "Sewage Pump Basins" or "Sewage Pump Pits" Article is retained.

D. [Basin] [Pit] Cover:  Cast iron or coated steel and strong enough to support pumps, motors, and controls.  See Part 2 "Sewage Pump [Basins] [Pits]" Article for requirements.

E. Cover Shaft Seal:  Stuffing box, with graphite-impregnated braided-yarn rings and bronze packing gland.

F. Motor:  Single-speed; grease-lubricated ball bearings.  Comply with requirements in Division 15 Section "Motors."

1. Mounting:  On vertical, cast-iron pedestal.

Controls in paragraph below are rod-and-float type.  Micropressure and mercury-float switches are also available.  Retain last option for duplex and multiplex pump units.

G. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switches; with floats, float rods, and rod buttons.[ Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.]

Feature in subparagraph below is required for controlling turbulence in deep basins with rod-and-float-type controls.

1. Float Guide:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

Verify availability of alarm types with manufacturer.

2. High-Water Alarm:  Cover-mounted, [compression-probe] [mechanical-float-switch] [mercury-float-switch] [micropressure-switch] alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

H. Capacities and Characteristics:

1. System Capacity:  <Insert gpm (L/minute).>

2. Number of Pumps:  [One] [Two] <Insert other>.

3. Each Pump:

a. Capacity:  <Insert gpm (L/minute).>

b. Solids Handling Capability:  [2 inches (50 mm)] [2-1/2 inches (65 mm)] [3 inches (75 mm)] <Insert inches (mm)> minimum.

c. Total Dynamic Head:  <Insert feet (kPa).>

d. Speed:  <Insert rpm.>

e. Discharge Pipe Size:  <Insert NPS (DN).>

f. Motor Horsepower:  <Insert value.>

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phases:  [Single] [Three].

3) Hertz:  60.

h. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert value.>

4. Alternator Control Required:  [Yes] [No].

5. Reverse-Flow Assembly Required:  [Yes] [No].

2.3 SUBMERSIBLE SEWAGE PUMPS

Select "Sewage Pump Reverse-Flow Assemblies" Article if required.

Retain last option in paragraph below for duplex units only.

A. Submersible, Fixed-Position Effluent Pumps:  Factory-assembled and -tested, [simplex] [duplex] [multiplex], single-stage, centrifugal, end-suction, submersible, direct-connected effluent pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible sewage pumps.[  Include reverse-flow assembly.]

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Aermotor Pumps, Inc.

c. Barnes; Crane Pumps & Systems.

d. Bell & Gossett Domestic Pump; ITT Industries.

e. Federal Pump Corp.

f. Flygt; ITT Industries.

g. Goulds Pumps; ITT Industries.

h. Grundfos Pumps Corp.

i. HOMA Pump Technology.

j. Hydromatic Pumps; Pentair Pump Group (The).

k. KSB Inc.

l. Liberty Pumps.

m. Little Giant Pump Co.

n. McDonald, A. Y. Mfg. Co.

o. Metropolitan Industries, Inc.

p. Myers, F. E.; Pentair Pump Group (The).

q. Stancor, Inc.

r. Sta-Rite Industries, Inc.

s. Zoeller Company.

t. <Insert manufacturer's name.>

2. Casing:  Cast iron, with open inlet, legs that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

Most typical impellers are cast iron.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced, closed or semiopen design for clear wastewater; overhung, single suction, and keyed and secured to shaft.

4. Pump and Motor Shaft:  [Stainless steel] [Stainless steel or steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double mechanical seals].

5. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with Division 15 Section "Motors."

Verify that pump selected has motor features in two subparagraphs below, if required, or delete.  Add other required features.

a. Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

b. Motor Housing Fluid:  [Air] [Air or oil] [Oil].

Retain last option in paragraph below for duplex units only.

B. Submersible, Quick-Disconnect Effluent Pumps:  Factory-assembled and -tested, [simplex] [duplex] [multiplex], single-stage, centrifugal, end-suction, submersible, direct-connected effluent pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible sewage pumps and with SWPA's "Submersible Sewage Pumping Systems (SWPA) Handbook" for guide-rail supports.[  Include reverse-flow assembly.]

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Flygt; ITT Industries.

c. HOMA Pump Technology.

d. Hydromatic Pumps; Pentair Pump Group (The).

e. Metropolitan Industries, Inc.

f. Myers, F. E.; Pentair Pump Group (The).

g. <Insert manufacturer's name.>

2. Casing:  Cast iron, with open inlet, legs (or guide-rail supports) that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

Most typical impellers are cast iron.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced, closed or semiopen design for clear wastewater; overhung, single suction, and keyed and secured to shaft.

4. Pump and Motor Shaft:  [Stainless steel] [Stainless steel or steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double mechanical seals].

5. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof, power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with Division 15 Section "Motors."

Verify that pump selected has motor features in first two subparagraphs below, if required, or delete.  Add other required features.

a. Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

b. Motor Housing Fluid:  [Air] [Air or oil] [Oil].

6. Guide-Rail Supports:  Include the following for each sewage pump:

a. Guide Rails:  Vertical pipes or structural members, made of galvanized steel or other corrosion-resistant metal, attached to baseplate and basin sidewall or cover.

b. Baseplate:  Corrosion-resistant metal plate, attached to basin floor, supporting guide-rail supports and stationary elbow.

c. Pump Yoke:  Motor-mounted or casing-mounted yokes or other attachments for aligning pump during connection of flanges.

d. Movable Elbow:  Pump discharge-elbow fitting with flange, seal, and positioning device.

e. Stationary Elbow:  Fixed discharge-elbow fitting with flange that mates to movable-elbow flange and support attached to baseplate.

f. Lifting Cable:  Stainless steel; attached to pump and cover at manhole.

Retain last option in paragraph below for duplex units only.

C. Submersible, Fixed-Position Sewage Pumps:  Factory-assembled and -tested, [simplex] [duplex] [multiplex], single-stage, centrifugal, end-suction, submersible, direct-connected sewage pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible sewage pumps.[  Include reverse-flow assembly.]

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Aermotor Pumps, Inc.

c. Barnes; Crane Pumps & Systems.

d. Bell & Gossett Domestic Pump; ITT Industries.

e. EBARA International Corporation; Standard Pump Division.

f. Fairbanks Morse; Pentair Pump Group (The).

g. Flygt; ITT Industries.

h. Goulds Pumps; ITT Industries.

i. Grundfos Pumps Corp.

j. HOMA Pump Technology.

k. Hydromatic Pumps; Pentair Pump Group (The).

l. KSB Inc.

m. Liberty Pumps.

n. Little Giant Pump Co.

o. McDonald, A. Y. Mfg. Co.

p. Metropolitan Industries, Inc.

q. Myers, F. E.; Pentair Pump Group (The).

r. Paco Pumps, Inc.

s. Stancor, Inc.

t. Sta-Rite Industries, Inc.

u. Sterling Peerless; Sterling Fluid Systems Group.

v. Swaby Manufacturing Co.

w. Tsurumi (America), Inc.

x. USFilter/Davco Products.

y. Weil Pump Company, Inc.

z. Weinman Div.; Crane Pumps & Systems.

aa. Yeomans Chicago Corporation.

ab. Zoeller Company.

ac. <Insert manufacturer's name.>

2. Casing:  Cast iron, with open inlet, legs that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

Most typical impellers are cast iron.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced, open or semiopen, nonclog design and capable of handling solids; overhung, single suction, and keyed and secured to shaft.

4. Pump and Motor Shaft:  [Stainless steel] [Stainless steel or steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double mechanical seals].

5. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with Division 15 Section "Motors."

Verify that pump selected has motor features in two subparagraphs below, if required, or delete.  Add other required features.

a. Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

b. Motor Housing Fluid:  [Air] [Air or oil] [Oil].

Retain last option in paragraph below for duplex units only.

D. Submersible, Quick-Disconnect Sewage Pumps:  Factory-assembled and -tested, [simplex] [duplex] [multiplex], single-stage, centrifugal, end-suction, submersible, direct-connected sewage pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible sewage pumps and with SWPA's "Submersible Sewage Pumping Systems (SWPA) Handbook" for guide-rail supports.[  Include reverse-flow assembly.]

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Chicago Pump Company; a division of Yeomans Chicago Corporation.

b. Deming Pumps; Crane Pumps & Systems.

c. EBARA International Corporation; Standard Pump Division.

d. Fairbanks Morse; Pentair Pump Group (The).

e. Federal Pump Corp.

f. Flygt; ITT Industries.

g. Gorman-Rupp Company (The).

h. Goulds Pumps; ITT Industries.

i. HOMA Pump Technology.

j. Hydromatic Pumps; Pentair Pump Group (The).

k. KSB Inc.

l. Metropolitan Industries, Inc.

m. Myers, F. E.; Pentair Pump Group (The).

n. Paco Pumps, Inc.

o. PUMPEX, Inc.

p. Stancor, Inc.

q. Sta-Rite Industries, Inc.

r. Swaby Manufacturing Co.

s. Tsurumi (America), Inc.

t. USFilter/Davco Products.

u. Weil Pump Company, Inc.

v. Weinman Div.; Crane Pumps & Systems.

w. Yeomans Chicago Corporation.

x. Zoeller Company.

y. <Insert manufacturer's name.>

2. Casing:  Cast iron, with open inlet, legs (or guide-rail supports) that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

Most typical impellers are cast iron.

3. Impeller:  [ASTM A 48/A 48M, Class No. 25 A or higher cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [ASTM B 584, cast bronze]; statically and dynamically balanced, open or semiopen, nonclog design and capable of handling solids; overhung, single suction, and keyed and secured to shaft.

4. Pump and Motor Shaft:  [Stainless steel] [Stainless steel or steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double mechanical seals].

5. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with Division 15 Section "Motors."

Verify that pump selected has motor features in first two subparagraphs below, if required, or delete.  Add other required features.

a. Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

b. Motor Housing Fluid:  [Air] [Air or oil] [Oil].

6. Guide-Rail Supports:  Include the following for each sewage pump:

a. Guide Rails:  Vertical pipes or structural members, made of galvanized steel or other corrosion-resistant metal, attached to baseplate and basin sidewall or cover.

b. Baseplate:  Corrosion-resistant metal plate, attached to basin floor, supporting guide rails and stationary elbow.

c. Pump Yoke:  Motor-mounted or casing-mounted yokes or other attachments for aligning pump during connection of flanges.

d. Movable Elbow:  Pump discharge-elbow fitting with flange, seal, and positioning device.

e. Stationary Elbow:  Fixed discharge-elbow fitting with flange that mates to movable-elbow flange and support attached to baseplate.

f. Lifting Cable:  Stainless steel; attached to pump and cover at manhole.

E. Submersible, Quick-Disconnect Grinder Pumps:  Factory-assembled and -tested, [simplex] [duplex] [multiplex], single-stage, centrifugal, end-suction, submersible, direct-connected grinder pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible sewage pumps and with SWPA's "Submersible Sewage Pumping Systems (SWPA) Handbook" for guide-rail supports.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company.

b. EBARA International Corporation; Standard Pump Division.

c. Environment One Corporation.

d. Flygt; ITT Industries.

e. HOMA Pump Technology.

f. Hydromatic Pumps; Pentair Pump Group (The).

g. Liberty Pumps.

h. Myers, F. E.; Pentair Pump Group (The).

i. Stancor, Inc.

j. Vaughan Co., Inc.

k. Weil Pump Company, Inc.

l. Zoeller Company.

m. <Insert manufacturer's name.>

2. Casing:  Cast iron, with open inlet, legs (or guide-rail supports) that elevate pump to permit flow into impeller, and vertical discharge with companion flange for piping connection.

Most typical impellers are cast iron.

3. Impeller:  Bronze or stainless steel; statically and dynamically balanced, with stainless-steel cutter, grinder, or slicer assembly and capable of handling solids; overhung, single suction, and keyed and secured to shaft.

4. Pump and Motor Shaft:  [Stainless steel] [Stainless steel or steel] [Steel], with factory-sealed, grease-lubricated ball bearings[ and double mechanical seals].

5. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with Division 15 Section "Motors."

Verify that pump selected has motor features in first two subparagraphs below, if required, or delete.  Add other required features.

a. Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

b. Motor Housing Fluid:  [Air] [Air or oil] [Oil].

6. Guide-Rail Supports:  Include the following for each sewage pump:

a. Guide Rails:  Vertical pipes or structural members, made of galvanized steel or other corrosion-resistant metal, attached to baseplate and basin sidewall or cover.

b. Baseplate:  Corrosion-resistant metal plate, attached to basin floor, supporting guide rails and stationary elbow.

c. Pump Yoke:  Motor-mounted or casing-mounted yokes or other attachments for aligning pump during connection of flanges.

d. Movable Elbow:  Pump discharge-elbow fitting with flange, seal, and positioning device.

e. Stationary Elbow:  Fixed discharge-elbow fitting with flange that mates to movable-elbow flange and support attached to baseplate.

f. Lifting Cable:  Stainless steel; attached to pump and cover at manhole.

Edit remaining paragraphs and subparagraphs in this Article for any pump type retained above.  Edit paragraph below for other piping materials.

F. Pump Discharge Piping:  Factory or field fabricated, [ASTM A 53/A 53M, Schedule 40, galvanized-steel pipe] [bronze pipe] [copper tube] <Insert other pipe material>.

Select from options in paragraph below depending on whether "Sewage Pump Basins" or "Sewage Pump Pits" Article is retained.

G. [Basin] [Pit] Cover:  Cast iron or coated steel and suitable to support controls.  See Part 2 "Sewage Pump [Basins] [Pits]" Article for other requirements.

Retain one of first four paragraphs and associated subparagraphs below.

Controls in two paragraphs below are rod-and-float type.  Retain "Float Guide" Subparagraph for deep basins.  Use compression-probe, high-water alarm with this type of control.

Retain paragraph below for simplex pump units.

H. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switch; with floats, float rods, and rod buttons.

Retain paragraph below for duplex pump units.  Edit if unit includes three or more pumps.

I. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal-mounted float switch; with floats, float rods, and rod buttons.  Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.

Controls in two paragraphs below are float- and micropressure-switch types.  Use matching-type high-water alarm with this type of control.

Retain paragraph below for simplex pump units.

J. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal mounted unless wall mounting is indicated; with two [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure] switches in NEMA 250, Type 6 enclosures; mounting rod; and electric cables.

Retain paragraph below for duplex pump units.  Edit if unit includes three or more pumps.

K. Controls:  NEMA 250, [Type 1] <Insert other> enclosure, pedestal mounted unless wall mounting is indicated; with three [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure] switches in NEMA 250, Type 6 enclosures; mounting rod; and electric cables.  Include automatic alternator to alternate operation of pump units on successive cycles and to operate multiple units if one pump cannot handle load.

Feature in subparagraph below is required for controlling turbulence in deep basins with rod-and-float-type controls.

1. Float Guide:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

Retain one of two subparagraphs below.  Match float- or micropressure-switch alarm to its corresponding control.

2. High-Water Alarm:  Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

3. High-Water Alarm:  Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical- or mercury-float or micropressure] [mechanical-float] [mercury-float] [micropressure]-switch alarm matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

L. Capacities and Characteristics:

1. System Capacity:  <Insert gpm (L/minute).>

2. Number of Pumps:  [One] [Two] <Insert other>.

3. Each Pump:

a. Capacity:  <Insert gpm (L/minute).>

b. Solids Handling Capability:  [Not applicable] [2 inches (50 mm)] [2-1/2 inches (65 mm)] [3 inches (75 mm)] <Insert inches (mm)> minimum.

c. Total Dynamic Head:  <Insert feet (kPa).>

d. Speed:  <Insert rpm.>

e. Discharge Pipe Size:  <Insert NPS (DN).>

f. Motor Horsepower:  <Insert value.>

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phases:  [Single] [Three].

3) Hertz:  60.

h. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert value.>

4. Alternator Control Required:  [Yes] [No].

5. Guide-Rail Supports Required:  [Yes] [No].

2.4 SEWAGE PUMP REVERSE-FLOW ASSEMBLIES

Retain this Article with duplex, wet-pit-mounted, vertical sewage pumps and submersible sewage pumps if sewage will contain rags or stringy solids that would clog pump impellers.  Select large-diameter basins if used.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Chicago Pump Company; a division of Yeomans Chicago Corporation.

2. Federal Pump Corp.

3. Paco Pumps, Inc.

4. Sterling Peerless; Sterling Fluid Systems Group.

5. Weil Pump Company, Inc.

6. Yeomans Chicago Corporation.

7. <Insert manufacturer's name.>

B. Description:  Factory-fabricated, sewage pump reverse-flow assembly for factory or field assembly and installation in sewage pump [basin] [basin or pit] [pit].  Include the following corrosion-resistant-metal components:

1. Inlet Fitting:  One combination inlet-overflow strainer fitting.

2. Valves:  Two shutoff valves and two check valves.

3. Strainers:  Two strainer housings with reverse-flow, self-flushing strainers.

4. Pipe and Fittings:  Size and configuration required to connect to sewage pumps and piping.

2.5 SEWAGE PUMP BASINS

Sewage pump basins and covers in this Article are usually round with openings for simplex and multiplex pumps.

A. Description:  Factory fabricated basin with sump, pipe connections, and separate cover.

B. Sump:  Fabricate watertight, with sidewall openings for pipe connections.

Use cast-iron, fiberglass, or other material basin sumps with cast-iron or steel covers for large installations.  Welded-steel basins are available but require special coatings and may require anode protection.

Retain one of three options in first subparagraph below or delete if in schedules.

1. Material:  [Cast iron] [Cast iron or fiberglass] [Fiberglass] <Insert other>.

2. Reinforcement:  Mounting plates for pumps, fittings[, guide-rail supports,] and accessories.

Retain subparagraph below if required to anchor basin to concrete slab in case of ground-water problems.

3. Anchor Flange:  Same material as or compatible with sump, cast in or attached to sump, in location and of size required to anchor basin in concrete slab.

C. Cover:  Fabricate with openings having gaskets, seals, and bushings; for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

1. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

2. Reinforcement:  Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

If Project has more than one pump basin, delete paragraph and subparagraphs below and add basin characteristics to pump schedule on Drawings.

D. Capacities and Characteristics:

1. Material:  [Cast iron] [Fiberglass] <Insert other>.

2. Capacity:  <Insert gal (L).>

3. Diameter:  <Insert inches (mm).>

4. Depth:  <Insert inches (mm).>

5. Inlet No. 1:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flanged] [Hubbed] [Threaded] outside.

6. Inlet No. 2:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flanged] [Hubbed] [Threaded] outside.

7. Inlet No. 3:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Flanged] [Hubbed] [Threaded] outside.

8. Sidewall Outlet:

a. Discharge Pipe Size:  <Insert NPS (DN).>

b. Bottom of Sump to Centerline:  <Insert inches (mm).>

c. Type:  [Hubbed inside] [Hubbed outside] <Insert other>.

9. Cover:

a. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

b. Diameter:  <Insert inches (mm).>

c. Manhole Required:  [Yes] [No].

d. Vent Size:  <Insert NPS (DN).>

2.6 SEWAGE PUMP PITS

Sewage pump pits and covers in this Article are usually square or rectangular with openings for simplex and multiplex pumps.

A. Description:  Concrete pit with sump, pipe connections, curb frame, and separate cover.

B. Sump:  Construct of watertight, cast-in-place, reinforced concrete with sidewall openings for pipe connections.  Cast-in-place concrete, formwork, and reinforcement are specified in Division 3 "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Pipe Connections:  Sleeved openings large enough for mechanical sleeve seals for drainage piping.  Sleeves and mechanical sleeve seals are specified in Division 15 Section "Basic Mechanical Materials and Methods" and drainage piping is specified in Division 15 Section "Sanitary Waste and Vent Piping."

C. Curb Frame and Cover:

1. Curb Frame Material:  Galvanized steel or steel with bituminous coating.

a. Pattern:  [Angle-cross-section shape with flat top surface] [Z-cross-section shape with raised outer rim of height matching cover, for recessed mounting with installed cover flush with top of floor slab].

2. Cover:  Fabricate with openings having gaskets, seals, and bushings; for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

a. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

b. Reinforcement:  Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

If Project has more than one pump pit, delete paragraph and subparagraphs below and add pit characteristics to pump schedule on Drawings.

D. Capacities and Characteristics:

1. Capacity:  <Insert gal (L).>

2. Inside Dimensions:  <Insert inches (mm).>

3. Depth:  <Insert inches (mm).>

4. Inlet No. 1:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Pit to Centerline:  <Insert inches (mm).>

5. Inlet No. 2:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Pit to Centerline:  <Insert inches (mm).>

6. Inlet No. 3:

a. Drainage Pipe Size:  <Insert NPS (DN).>

b. Bottom of Pit to Centerline:  <Insert inches (mm).>

7. Sidewall Outlet:

a. Forced-Main Pipe Size:  <Insert NPS (DN).>

b. Bottom of Pit to Centerline:  <Insert inches (mm).>

8. Curb Frame:

a. Material:  [Galvanized steel] [Steel with bituminous coating].

b. Pattern:  <Insert pattern.>

9. Cover:

a. Material:  [Cast iron] [Cast iron or steel with bituminous coating] [Steel with bituminous coating].

b. Dimensions:  <Insert inches (mm).>

c. Manhole Required:  [Yes] [No].

d. Vent Size:  <Insert NPS (DN).>

2.7 PACKAGED, SUBMERSIBLE SEWAGE PUMP UNITS

Units in this Article are complete with pumps, basin and cover, piping, valves, and controls.  Units have limited applications and capacities.  Most manufacturers offer only simplex units, but duplex units are available.  Using these units as the only means of discharging sewage is not recommended.

A. Grinder Units:  Factory-assembled and -tested, [simplex] [duplex], single-stage, centrifugal, end-suction, automatic-operation, direct-connected sewage pumps complying with UL 778 and HI 1.1-1.2 and HI 1.3 for submersible, grinder sewage pumps.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Barnes; Crane Pumps & Systems.

c. Environment One Corporation.

d. Goulds Pumps; ITT Industries.

e. Liberty Pumps.

f. McDonald, A. Y. Mfg. Co.

g. Myers, F. E.; Pentair Pump Group (The).

h. Zoeller Company.

i. <Insert manufacturer's name.>

2. Casing:  Cast iron.

3. Impeller:  Stainless-steel grinder type with shredding ring.

4. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with requirements in Division 15 Section "Motors."

5. Control:  Manufacturer's standard panel for one pump.

Retain subparagraph above for simplex pump unit or first subparagraph below for duplex pump unit.

6. Controls:  Automatic, with mechanical- or mercury-float switches and alternator.

7. Pump Discharge Piping:  Factory- or field-fabricated, [ASTM A 53/A 53M, Schedule 40, galvanized-steel pipe] [bronze pipe] [copper tube] <Insert other pipe material>.

8. Basin:  Watertight and of size for [one pump] [two pumps] with inlet pipe connection and gastight cover with vent and pump discharge connections.

B. Nonclog Units:  Factory-assembled and -tested, [simplex] [duplex], single-stage, centrifugal, end-suction, automatic-operation, direct-connected sewage pumps complying with UL 778 and with HI 1.1-1.2 and HI 1.3 for submersible, nonclog sewage pumps.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aermotor Pumps, Inc.

b. Barnes; Crane Pumps & Systems.

c. Goulds Pumps; ITT Industries.

d. Grundfos Pumps Corp.

e. Hydromatic Pumps; Pentair Pump Group (The).

f. Liberty Pumps.

g. Little Giant Pump Co.

h. McDonald, A. Y. Mfg. Co.

i. Myers, F. E.; Pentair Pump Group (The).

j. Paco Pumps, Inc.

k. Sta-Rite Industries, Inc.

l. Zoeller Company.

m. <Insert manufacturer's name.>

2. Casing:  Cast iron.

3. Impeller:  Brass; statically and dynamically balanced, nonclog design, and capable of handling 2-inch- (50-mm-) diameter solids.

4. Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.  Comply with requirements in Division 15 Section "Motors."

5. Control:  Manufacturer's standard panel for one pump.

Retain subparagraph above for simplex pump unit or first subparagraph below for duplex pump unit.

6. Controls:  Automatic, with mechanical- or mercury-float switches and alternator.

7. Pump Discharge Piping:  Factory- or field-fabricated, [ASTM A 53/A 53M, Schedule 40, galvanized-steel pipe] [bronze pipe] [copper tube] <Insert other pipe material>.

8. Basin:  Watertight and of size for [one pump] [two pumps] with inlet pipe connection and gastight cover with vent and pump discharge connections.

Retain remainder of this Article with either pump type retained above.  If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. System Capacity:  <Insert gpm (L/minute).>

2. Number of Pumps:  [One] [Two].

3. Each Pump:

a. Capacity:  <Insert gpm (L/minute).>

b. Total Dynamic Head:  <Insert feet (kPa).>

c. Speed:  <Insert rpm.>

d. Discharge Pipe Size:  <Insert NPS (DN).>

e. Motor Horsepower:  <Insert value>.

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>

2) Phases:  [Single] [Three].

3) Hertz:  60.

g. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert value.>

4. Alternator Control Required:  [Yes] [No].

5. Basin:  Watertight[ plastic] and size for [one pump] [two pumps].

2.8 PACKAGED, WASTEWATER PUMP UNITS

A. Pedestal Units:  Factory-assembled and -tested, single-stage, centrifugal, end-suction, automatic-operation, basin-mounted effluent pump unit.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alyan Pump Company.

b. Federal Pump Corp.

c. Milton Roy Company; Hartell Div.

d. <Insert manufacturer's name.>

2. Pump Body and Impeller:  Corrosion-resistant materials.

3. Motor:  With built-in overload protection and mounted vertically on basin cover.  Comply with requirements in Division 15 Section "Motors."

4. Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm) and with grounding plug and cable-sealing assembly for connection at pump.

5. Control:  Float switch.

6. Basin:  Watertight coated steel or plastic with inlet pipe connection and gastight cover with vent and pump discharge connections.

a. Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

b. Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

c. Vent Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

B. Submersible Units:  Factory-assembled and -tested, single-stage, centrifugal, end-suction, automatic-operation, submersible effluent pump unit.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ABS Pumps, Inc.

b. Bell & Gossett Domestic Pump; ITT Industries.

c. Goulds Pumps; ITT Industries.

d. Grundfos Pumps Corp.

e. Liberty Pumps.

f. Little Giant Pump Co.

g. McDonald, A. Y. Mfg. Co.

h. Myers, F. E.; Pentair Pump Group (The).

i. Sta-Rite Industries, Inc.

j. Zoeller Company.

k. <Insert manufacturer's name.>

2. Pump Body and Impeller:  Corrosion-resistant materials.

3. Pump Seals:  Mechanical type.

4. Motor:  Hermetically sealed, capacitor-start type, with built-in overload protection.  Comply with requirements in Division 15 Section "Motors."

5. Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm) and with grounding plug and cable-sealing assembly for connection at pump.

6. Control:  Float switch.

7. Basin:  Watertight plastic with inlet pipe connection and gastight cover with vent and pump discharge connections.

a. Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

b. Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

c. Vent Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/minute).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Speed:  <Insert rpm.>

4. Discharge Pipe Size:  <Insert NPS (DN).>

5. Motor Horsepower:  <Insert value>.

6. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

7. Basin:

a. Material:  [Coated steel] [Coated steel or plastic] [Plastic].

b. Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

c. Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

d. Discharge Connection:  [NPS 1-1/4 (DN 32)] <Insert other> minimum.

e. Vent Connections:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

2.9 FLEXIBLE CONNECTORS

Delete this Article if flexible connectors are in Division 15 Section "Sanitary Waste and Vent Piping" or if not required.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anamet, Inc.

2. Flex-Hose Co., Inc.

3. Flexicraft Industries.

4. Flex-Pression, Ltd.

5. Flex-Weld, Inc.

6. Hyspan Precision Products, Inc.

7. Mercer Rubber.

8. Metraflex, Inc.

9. Proco Products, Inc.

10. Tozen America Corporation.

11. Unaflex Inc.

12. <Insert manufacturer's name.>

B. Description:  [125-psig (860-kPa)] <Insert other> minimum working-pressure rating and ends matching pump connections:

1. Bronze Flexible Connectors:  Corrugated, bronze inner tubing covered with bronze wire braid.  Include copper-tube ends or bronze flanged ends, braze-welded to tubing.

2. Stainless-Steel Flexible Connectors:  Corrugated, stainless-steel inner tubing covered with stainless-steel wire braid.  Include stainless-steel nipples or flanges, welded to tubing.

2.10 BUILDING AUTOMATION SYSTEM INTERFACE

A. Provide auxiliary contacts in pump controllers for interface to building automation system.  Include the following:

1. On-off status of each pump.

2. Alarm status.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for plumbing piping to verify actual locations of sanitary drainage and vent piping connections before sewage pump installation.

3.2 CONCRETE

Retain this Article if Part 2 "Sewage Pump Pits" or "Packaged, Wastewater Pump Units" Article is retained.  Coordinate sizes and locations of concrete bases and pits and verify requirements with structural engineer.

A. Install concrete bases of dimensions indicated for pumps and controllers.  Refer to Division 15 Section "Basic Mechanical Materials and Methods."

Revise subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

B. Cast-in-place concrete materials and placement requirements are specified in Division 3.

3.3 INSTALLATION

A. Excavating, trenching, and backfilling are specified in Division 2 Section "Earthwork."

B. Install sewage pumps according to applicable requirements in HI 1.4.

C. Install pumps and arrange to provide access for maintenance including removal of motors, impellers, couplings, and accessories.

Retain first paragraph below for wet-pit-mounted, vertical sewage pumps.

D. Suspend wet-pit-mounted, vertical sewage pumps from [basin] [basin and pit] [pit] covers.  Make direct connections to sanitary drainage piping.

E. Set submersible sewage pumps on [basin] [basin and pit] [pit] floors.  Make direct connections to sanitary drainage piping.

Delete subparagraph below if quick-disconnect guide-rail supports are not specified.

1. Anchor guide-rail supports to [basin] [basin and pit] [pit] bottoms and sidewalls or covers.  Install pumps so pump and discharge pipe disconnecting flanges make positive seals when pumps are lowered into place.

F. Install sewage pump basins and connect to drainage and vent piping.  Brace interior of basins according to manufacturer's written instructions to prevent distortion or collapse during concrete placement.  Set basin cover and fasten to basin top flange.  Install cover so top surface is flush with finished floor.

G. Construct sewage pump pits and connect to drainage and vent piping.  Set pit curb frame recessed in and anchored to concrete.  Fasten pit cover to pit curb flange.  Install cover so top surface is flush with finished floor.

Retain paragraph below for packaged, submersible sewage pumps.

H. Install packaged, submersible sewage pump units and make direct connections to drainage and vent piping.

Retain first paragraph below for packaged, wastewater pumps.

I. Install packaged, wastewater pump unit basins on floor or concrete base unless recessed installation is indicated.  Make direct connections to drainage and vent piping.

J. Support piping so weight of piping is not supported by pumps.

3.4 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in Division 15 Section "Drainage and Vent Piping."  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to sewage pumps to allow service and maintenance.

C. Connect sanitary drainage and vent piping to pumps.  Install discharge piping equal to or greater than size of pump discharge piping.  Install vent piping equal to or greater than size of pump basin vent connection.  Refer to Division 15 Section "Sanitary Drainage and Vent Piping."

1. Install flexible connectors adjacent to pumps in discharge piping.

2. Install check and shutoff valves on discharge piping from each pump.  Install unions on pumps having threaded pipe connections.  Install valves same size as connected piping.  Refer to Division 15 Section "Valves" for general-duty valves for sanitary waste piping.

D. Ground equipment according to Division 16 Section "Grounding and Bonding."

E. Connect wiring according to Division 16 Section "Conductors and Cables."

3.5 STARTUP SERVICE

Delete first paragraph and subparagraphs below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Verify bearing lubrication.

3. Disconnect couplings and check motors for proper direction of rotation.

4. Verify that each pump is free to rotate by hand.  If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

5. Verify that pump controls are correct for required application.

6. <Insert additional startup steps if any.>

B. Start pumps without exceeding safe motor power:

1. Start motors.

2. Open discharge valves slowly.

3. Check general mechanical operation of pumps and motors.

C. Test and adjust controls and safeties.

D. Remove and replace damaged and malfunctioning components.

Insert specific liquid levels to start and stop pumps and energize alarms to suit design requirements.

1. Pump Controls:  Set pump controls for automatic start, stop, and alarm operation as required for system application.

2. Set field-adjustable switches and circuit-breaker trip ranges as indicated, or if not indicated, for normal operation.

E. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to two visits to Project outside normal occupancy hours for this purpose.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain[ controls and] pumps.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15445

SEWAGE PUMPS
15445 - 23

