Copyright 2004 AIA
MASTERSPEC Full Length
12/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15530 - FURNACES
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include furnaces may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. [Gas-fired, noncondensing] [Gas-fired, condensing] [Oil-fired] [Electric] furnaces and accessories complete with controls.

2. Air filters.

3. Air cleaners.

4. Ultraviolet germicidal lights.

5. Humidifiers.

6. Ventilation heat exchangers.

7. Refrigeration components.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 1 Section "LEED Requirements" for additional LEED requirements.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each of the following:

1. Furnace.

2. Thermostat.

3. Humidistat.

4. Air filter.

5. Air cleaner.

6. Ultraviolet germicidal light.

7. Humidifier.

8. Ventilation heat exchanger.

9. Refrigeration components.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Operation and Maintenance Data:  For each furnace to include in emergency, operation, and maintenance manuals for each of the following:

1. Furnace and accessories complete with controls.

2. Air filter.

3. Air cleaner.

4. Ultraviolet germicidal light.

5. Humidifier.

6. Ventilation heat exchanger.

7. Refrigeration components.

D. LEED Submittals:

Retain first subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for solvent cements and adhesive primers.

3. Product Data for Credit EQ 4.1:  For solvent cements and adhesive primers, including printed statement of VOC content.

E. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

D. Comply with NFPA 70.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

Retain paragraph below if Project includes roof-mounted refrigeration components.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of furnaces that fail in materials or workmanship within specified warranty period:

1. Warranty Period, Commencing on Date of Substantial Completion:

Verify available warranties for units and components and insert numbers in subparagraphs below.

a. Furnace Heat Exchanger:  [10 years] [20 years] [Lifetime] <Insert value>.

b. Integrated Ignition and Blower Control Circuit Board:  [Five years] <Insert value>.

c. Draft-Inducer Motor:  [Five years] <Insert value>.

d. High-Efficiency Oil Furnace Burner:  [Three years] <Insert value>.

e. Refrigeration Compressors:  [10 years] [Lifetime] <Insert value>.

f. Evaporator and Condenser Coils:  [Five years] <Insert value>.

g. <Insert components requiring extended warranty>.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Disposable Air Filters:  Furnish [two] <Insert number> complete sets.

2. Disposable Air-Cleaner Media:  Furnish [one] <Insert number> complete set(s).

3. Fan Belts:  Furnish [one] <Insert number> set(s) for each furnace fan.

4. Disposable Humidifier Media:  Furnish [one] <Insert number> set(s).

PART 2 -  PRODUCTS

2.1 GAS-FIRED FURNACES, NONCONDENSING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Adams Manufacturing Company.

2. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

3. American Standard Companies, Inc.

4. Arcoaire Air Conditioning & Heating; a division of International Comfort Products, LLC.

5. Armstrong Air Conditioning Inc.

6. Bard Manufacturing Company.

7. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

8. Carrier Corporation; Div. of United Technologies Corp.

9. Clare Brothers.

10. Comfort-Aire; a division of Heat Controller, Inc.

11. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

12. Dornback Furnace.

13. Goodman Manufacturing Company, L.P.

14. Heil Heating & Cooling Products; a division of International Comfort Products, LLC.

15. Lennox Industries Inc.

16. Luxaire Corporation; a division of Unitary Products Group.

17. Rheem Manufacturing Company; Air Conditioning Division.

18. Ruud Air Conditioning Division.

19. Tempstar Heating & Cooling Products; a division of International Comfort Products, LLC.

20. Thermo Products, Inc.; a division of Burnham Holdings Inc.

21. Trane.

22. York International Corp.; a division of Unitary Products Group.

23. <Insert manufacturer's name>.

D. General Requirements for Gas-Fired, Noncondensing Furnaces:  Factory assembled, piped, wired, and tested; complying with ANSI Z21.47/CSA 2.3, "Gas-Fired Central Furnaces," and with NFPA 54.

In first paragraph below, galvanized steel is offered by some but not all manufacturers.

E. Cabinet:  [Steel] [Galvanized steel].

1. Cabinet interior around heat exchanger shall be factory-installed insulation.

2. Lift-out panels shall expose burners and all other items requiring access for maintenance.

3. Factory paint external cabinets in manufacturer's standard color.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

F. Fan:  Centrifugal, factory balanced, resilient mounted, [direct drive] [belt drive] [direct or belt drive] [drive type indicated on Drawings].

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors:  Comply with requirements in Division 15 Section "Motors."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features:  Single speed, Premium (TM) efficiency, as defined in Division 15 Section "Motors," and with internal thermal protection and permanent lubrication.

3. Special Motor Features:  Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features:  Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Type of Gas:  [Natural] [Propane].

H. Heat Exchanger:  [Aluminized] [Stainless] steel.

I. Burner:

In first subparagraph below, two-stage and modulating gas valves are options.

1. Gas Valve:  100 percent safety [two-stage] [modulating] main gas valve, main shutoff valve, pressure regulator, safety pilot with electronic flame sensor, limit control, transformer, and combination ignition/fan timer control board.

2. Ignition:  Electric pilot ignition, with hot-surface igniter or electric spark ignition.

J. Gas-Burner Safety Controls:

1. Electronic Flame Sensor:  Prevents gas valve from opening until pilot flame is proven; stops gas flow on ignition failure.

2. Flame Rollout Switch:  Installed on burner box; prevents burner operation.

3. Limit Control:  Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

K. Combustion-Air Inducer:  Centrifugal fan with thermally protected motor and sleeve bearings prepurges heat exchanger and vents combustion products; pressure switch prevents furnace operation if combustion-air inlet or flue outlet is blocked.

L. Furnace Controls:  Solid-state board integrates ignition, heat, cooling, and fan speeds; and adjustable fan-on and fan-off timing; terminals for connection to accessories.

M. Vent Materials:  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for Type B metal vents.

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

N. Capacities and Characteristics:

1. Airflow Configuration:  [Upflow] [Counterflow] [Horizontal].

2. Gas:

a. Type:  [Natural] [Propane].

b. Venting Type:  [Power venter] [Power venter with combustion-air intake].

Retain one of first three subparagraphs below.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

c. Minimum Efficiency AFUE:  <Insert value> percent.

d. Minimum Thermal Efficiency:  <Insert value> percent.

e. Minimum Combustion Efficiency:  <Insert value> percent.

f. Input:  <Insert MBh (kW)>.

g. Heat Output:  <Insert MBh (kW)>.

h. Gas Connection Size:  <Insert NPS (DN)>.

i. Draft-Inducer Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

j. Combustion-Air Inlet Size:  <Insert inches (mm)>.

k. Combustion-Air Inlet Material:  [Galvanized steel] [Stainless steel] [PVC].

l. Heat-Exchanger Condensate Drain Size:  <Insert Nps (DN)>.

m. Vent Size:  <Insert inches (mm)>.

3. Fan:

a. Airflow:  <Insert cfm (L/s)>.

b. External Static Pressure:  <Insert inches wg (Pa)>.

c. Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

d. Volts:  <Insert value>.

e. Phase:  <Insert value>.

f. Hertz:  <Insert value>.

g. Full-Load Amperes:  <Insert value>.

h. Minimum Circuit Ampacity:  <Insert value>.

i. Maximum Overcurrent Protection:  <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts:  <Insert value>.

b. Phase:  <Insert value>.

c. Hertz:  <Insert value>.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.2 GAS-FIRED FURNACES, CONDENSING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Adams Manufacturing Company.

2. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

3. American Standard Companies, Inc.

4. Arcoaire Air Conditioning & Heating; a division of International Comfort Products, LLC.

5. Armstrong Air Conditioning Inc.

6. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

7. Carrier Corporation; Div. of United Technologies Corp.

8. Clare Brothers.

9. Comfort-Aire; a division of Heat Controller, Inc.

10. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

11. Dornback Furnace.

12. Goodman Manufacturing Company, L.P.

13. Heil Heating & Cooling Products; a division of International Comfort Products, LLC.

14. Lennox Industries Inc.

15. Luxaire Corporation; a division of Unitary Products Group.

16. Rheem Manufacturing Company; Air Conditioning Division.

17. Ruud Air Conditioning Division.

18. Tempstar Heating & Cooling Products; a division of International Comfort Products, LLC.

19. Thermo Products, Inc.; a division of Burnham Holdings Inc.

20. Trane.

21. York International Corp.; a division of Unitary Products Group.

22. <Insert manufacturer's name>.

D. General Requirements for Gas-Fired, Condensing Furnaces:  Factory assembled, piped, wired, and tested; complying with ANSI Z21.47/CSA 2.3, "Gas-Fired Central Furnaces," and with NFPA 54.

In first paragraph below, galvanized steel is offered by some but not all manufacturers.

E. Cabinet:  [Steel] [Galvanized steel].

1. Cabinet interior around heat exchanger shall be factory-installed insulation.

2. Lift-out panels shall expose burners and all other items requiring access for maintenance.

3. Factory paint external cabinets in manufacturer's standard color.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

F. Fan:  Centrifugal, factory balanced, resilient mounted, direct drive.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors:  Comply with requirements in Division 15 Section "Motors."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features:  Single speed, Premium (TM) efficiency, as defined in Division 15 Section "Motors," and with internal thermal protection and permanent lubrication.

3. Special Motor Features:  Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features:  Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Type of Gas:  [Natural] [Propane].

H. Heat Exchanger:

1. Primary:  [Aluminized] [Stainless] steel.

2. Secondary:  [Polyethylene-coated] [Stainless] steel.

I. Burner:

1. Gas Valve:  100 percent safety [two-stage] [modulating] main gas valve, main shutoff valve, pressure regulator, safety pilot with electronic flame sensor, limit control, transformer, and combination ignition/fan timer control board.

2. Ignition:  Electric pilot ignition, with hot-surface igniter or electric spark ignition.

J. Gas-Burner Safety Controls:

1. Electronic Flame Sensor:  Prevents gas valve from opening until pilot flame is proven; stops gas flow on ignition failure.

2. Flame Rollout Switch:  Installed on burner box; prevents burner operation.

3. Limit Control:  Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

K. Combustion-Air Inducer:  Centrifugal fan with thermally protected motor and sleeve bearings prepurges heat exchanger and vents combustion products; pressure switch prevents furnace operation if combustion-air inlet or flue outlet is blocked.

L. Furnace Controls:  Solid-state board integrates ignition, heat, cooling, and fan speeds; adjustable fan-on and fan-off timing; terminals for connection to accessories[; diagnostic light with viewport].

M. Accessories:

1. Combination Combustion-Air Intake and Vent:  PVC plastic fitting to combine combustion-air inlet and vent through [outside wall] [roof].

2. CPVC Plastic Vent Materials.

Retain one of two subparagraphs and associated subparagraphs below.

a. CPVC Plastic Pipe:  Schedule 40, complying with ASTM F 441/F 441M.

b. CPVC Plastic Fittings:  Schedule 40, complying with ASTM F 438, socket type.

c. CPVC Solvent Cement:  ASTM F 493.

Retain first two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1) Use CPVC solvent cement that has a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

3. PVC Plastic Vent Materials:

a. PVC Plastic Pipe:  Schedule 40, complying with ASTM D 1785.

b. PVC Plastic Fittings:  Schedule 40,  complying with ASTM D 2466, socket type.

c. PVC Solvent Cement:  ASTM D 2564.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1) Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

N. Capacities and Characteristics:

1. Airflow Configuration:  [Upflow] [Counterflow] [Horizontal].

2. Gas:

a. Type:  [Natural] [Propane].

b. Venting Type:  [Power venter] [Power venter with combustion-air intake].

Retain one of first three subparagraphs below.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

c. Minimum Efficiency AFUE:  <Insert value> percent.

d. Minimum Thermal Efficiency:  <Insert value> percent.

e. Minimum Combustion Efficiency:  <Insert value> percent.

f. Input:  <Insert MBh (kW)>.

g. Heat Output:  <Insert MBh (kW)>.

h. Gas Connection Size:  <Insert NPS (DN)>.

i. Draft-Inducer Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

j. Combustion-Air Inlet Size:  <Insert inches (mm)>.

k. Combustion-Air Inlet Material:  [CPVC] [PVC].

l. Heat-Exchanger Condensate Drain Size:  <Insert Nps (DN)>.

m. Vent Size:  <Insert inches (mm)>.

n. Vent Material:  [CPVC] [PVC].

3. Fan:

a. Airflow:  <Insert cfm (L/s)>.

b. External Static Pressure:  <Insert inches wg (Pa)>.

c. Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

d. Volts:  <Insert value>.

e. Phase:  <Insert value>.

f. Hertz:  <Insert value>.

g. Full-Load Amperes:  <Insert value>.

h. Minimum Circuit Ampacity:  <Insert value>.

i. Maximum Overcurrent Protection:  <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts:  <Insert value>.

b. Phase:  <Insert value>.

c. Hertz:  <Insert value>.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.3 OIL-FIRED FURNACES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Adams Manufacturing Company.

2. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

3. American Standard Companies, Inc.

4. Arcoaire Air Conditioning & Heating; a division of International Comfort Products, LLC.

5. Armstrong Air Conditioning Inc.

6. Bard Manufacturing Company.

7. Carrier Corporation; Div. of United Technologies Corp.

8. Clare Brothers.

9. Comfort-Aire a division of Heat Controller, Inc.

10. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

11. Dornback Furnace.

12. Heil Heating & Cooling Products; a division of International Comfort Products, LLC.

13. Lennox Industries Inc.

14. Luxaire Corporation; a division of Unitary Products Group.

15. Rheem Manufacturing Company; Air Conditioning Division.

16. Ruud Air Conditioning Division.

17. Thermo Products, Inc.; a division of Burnham Holdings Inc.

18. York International Corp.; a division of Unitary Products Group.

19. <Insert manufacturer's name>.

D. General Requirements for Oil-Fired Furnaces:  Factory assembled, piped, wired, and tested; complying with UL 727 and with NFPA 31.

In first paragraph below, galvanized steel is offered by some but not all manufacturers.

E. Cabinet:  [Steel] [Galvanized steel].

1. Cabinet interior around heat exchanger shall be factory-installed insulation.

2. Lift-out panels shall expose burners and all other items requiring access for maintenance.

3. Factory paint external cabinets in manufacturer's standard color.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

F. Fan:  Centrifugal, factory balanced, resilient mounted, [direct drive] [belt drive] [direct or belt drive] [drive type indicated on Drawings].

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors:  Comply with requirements in Division 15 Section "Motors."

Retain either or both of two subparagraphs below, as applicable.

2. Special Motor Features:  Single speed, Premium (TM) efficiency, as defined in Division 15 Section "Motors," and with internal thermal protection and permanent lubrication.

3. Special Motor Features:  Multitapped, multispeed with internal thermal protection and permanent lubrication.

G. Heat Exchanger:  Welded steel with [ceramic-fiber liner] [refractory insert] at the burner in the combustion chamber.  Minimum 2-inch- (50-mm-) diameter access ports in heat exchanger to permit access for cleaning.

H. Burner:  High-pressure atomizing type, with rubber-mounted, adjustable, combustion-air blower; integrated fuel pump; hinged, flame-inspection port; cadmium-sulfide flame sensor; electrodes; ignition transformer; and oil nozzle.

1. Time-Delay Relay:  Limits time for establishing main flame.

2. Flame Sensor:  Monitors flame and stops burner on flame failure.

3. Limit Control:  Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

I. Barometric Draft Regulator:  Match furnace; for mounting in flue.

J. Furnace Controls:  Solid-state board integrates ignition, heat, cooling, and fan speeds; and adjustable fan-on and fan-off timing; terminals for connection to accessories.

K. Vent Materials:  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for Type B metal vents.

If Project has more than one furnace, delete paragraph below and schedule furnace and other components.

L. Capacities and Characteristics:

1. Airflow Configuration:  [Upflow] [Counterflow] [Horizontal].

Retain one of first two subparagraphs below.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

2. Minimum Efficiency AFUE:  <Insert value> percent.

3. Minimum Thermal Efficiency:  <Insert value> percent.

4. Oil:

a. Input:  <Insert gph (L/s)>.

b. Heat Output:  <Insert MBh (kW)>.

c. Burner Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

d. Vent Size:  <Insert inches (mm)>.

5. Fan:

a. Airflow:  <Insert cfm (L/s)>.

b. External Static Pressure:  <Insert inches wg (Pa)>.

c. Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

d. Volts:  <Insert value>.

e. Phase:  <Insert value>.

f. Hertz:  <Insert value>.

g. Full-Load Amperes:  <Insert value>.

h. Minimum Circuit Ampacity:  <Insert value>.

i. Maximum Overcurrent Protection:  <Insert amperage>.

6. Furnace Electrical Connection:

a. Volts:  <Insert value>.

b. Phase:  <Insert value>.

c. Hertz:  <Insert value>.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.4 ELECTRIC FURNACES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amana Heating & Air Conditioning; Goodman Manufacturing Company, L.P.

2. Armstrong Air Conditioning Inc.

3. Bryant Heating & Cooling Systems; Div. of United Technologies Corp.

4. Carrier Corporation; Div. of United Technologies Corp.

5. Comfort-Aire; a division of Heat Controller, Inc.

6. Comfortmaker Air Conditioning & Heating; a division of International Comfort Products, LLC.

7. Eubank Manufacturing Enterprise, Inc.

8. Lennox Industries Inc.

9. Luxaire Corporation; a division of Unitary Products Group.

10. Rheem Manufacturing Company; Air Conditioning Division.

11. Ruud Air Conditioning Division.

12. York International Corp.; a division of Unitary Products Group.

13. <Insert manufacturer's name>.

D. General Requirements for Electric Furnaces:  Factory assembled, piped, wired, and tested.

E. Cabinet:  Steel, with duct liner[ downstream from cooling coil].

1. Duct Liner:  Fiberglass, minimum [1/2 inch (13 mm)] [3/4 inch (19 mm)] thick, complying with ASTM C 1071 and having a coated surface exposed to airstream complying with NFPA 90A or NFPA 90B and with NAIMA's "Fibrous Glass Duct Liner Standard."

Retain first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

a. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

2. Factory paint external cabinets in manufacturer's standard color.

F. Fan:  Centrifugal, factory balanced, resilient mounted, direct drive.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

1. Fan Motors:  Comply with requirements in Division 15 Section "Motors."

Retain one or more of three subparagraphs below, as applicable.

2. Special Motor Features:  Single speed, Premium (TM) efficiency, as defined in Division 15 Section "Motors," and with internal thermal protection and permanent lubrication.

3. Special Motor Features:  Multitapped, multispeed with internal thermal protection and permanent lubrication.

4. Special Motor Features:  Electronically controlled motor (ECM) controlled by integrated furnace/blower control.

G. Electric-Resistant Heating Elements:  Helix-wound, nickel-chromium wire-heating elements in ceramic insulators mounted on steel supports.

H. Heating-Element Control:  Sequencer relay with relay for each element; switches elements on and off, with delay between each increment; initiates, stops, or changes fan speed.

I. Summer Fan Switch:  Connected to permit independent on-off switch of unit fan.

If Project has more than one furnace, delete paragraph and subparagraphs below and schedule furnace and other components.

J. Capacities and Characteristics:

1. Airflow Configuration:  [Upflow] [Counterflow] [Horizontal].

2. Electric Heating Element:

a. Capacity:  <Insert MBh (kW)>.

b. Number of Steps:  <Insert number>.

c. Volts:  <Insert value>.

d. Phase:  <Insert value>.

e. Hertz:  <Insert value>.

f. Full-Load Amperes:  <Insert value>.

g. Minimum Circuit Ampacity:  <Insert value>.

h. Maximum Overcurrent Protection:  <Insert amperage>.

3. Fan:

a. Airflow:  <Insert cfm (L/s)>.

b. External Static Pressure:  <Insert inches wg (Pa)>.

c. Motor:

1) Size:  <Insert horsepower>.

2) Speed:  <Insert rpm>.

d. Volts:  <Insert value>.

e. Phase:  <Insert value>.

f. Hertz:  <Insert value>.

g. Full-Load Amperes:  <Insert value>.

h. Minimum Circuit Ampacity:  <Insert value>.

i. Maximum Overcurrent Protection:  <Insert amperage>.

4. Furnace Electrical Connection:

a. Volts:  <Insert value>.

b. Phase:  <Insert value>.

c. Hertz:  <Insert value>.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

2.5 THERMOSTATS[ AND HUMIDISTATS]

Retain one of five paragraphs below.

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 6.4.3, defines requirements for controls.

A. Solid-State Thermostat:  [Wall-mounting] [Freestanding] [Wireless], programmable, microprocessor-based unit with [automatic] [manual] switching from heating to cooling, preferential rate control, seven-day programmability with minimum of four temperature presets per day, [vacation mode, ]and battery backup protection against power failure for program settings.

B. Single-Stage, Heating-Cooling Thermostat:  Adjustable, heating-cooling, wall-mounting unit with fan on-automatic selector.

C. Two-Stage, Heating-Cooling Thermostat:  Adjustable, heating-cooling, wall-mounting unit with fan on-automatic selector.

D. [Single] [Two]-Stage, Heating-Only Thermostat:  Wall-mounting unit with fan on-automatic selector.

E. Solid-State, Combination Thermostat and Humidistat:  [Wall-mounting] [Freestanding] [Wireless], programmable, microprocessor-based unit with automatic switching from heating to cooling and humidifying to dehumidifying, preferential rate control, seven-day programmability with minimum of four temperature presets per day, [vacation mode, ]and battery backup protection against power failure for program settings.

Retain first paragraph below if humidifier is specified.

F. Humidistat:  Adjustable, [wall] [duct]-mounting unit.

G. Control Wiring:  Unshielded twisted-pair cabling.

1. No. 24 AWG, 100 ohm, four pair.

2. Cable Jacket Color:  [Blue] <Insert color>.

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  Retain paragraph below if applying for LEED certification or requiring compliance with ASHRAE/IESNA 90.1-2004.

H. Controls shall comply with requirements in ASHRAE/IESNA 90.1-2004, "Controls."

2.6 AIR FILTERS

Retain this Article for air filtration using air filters.  Retain one or more of four paragraphs below, as applicable.  If Project has more than one filter type, indicate filter type for each unit on Drawings.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.  First paragraph below does not comply; second paragraph complies.

A. Washable Filters:  1-inch- (25-mm-) thick, urethane pad.

B. Disposable Filters:  [1-inch- (25-mm-)] <Insert thickness> thick fiberglass media[ with ASHRAE 52.2 MERV rating of 6 or higher,] in sheet metal frame.

C. Charged Media Air Filters:  Sheet metal housing arranged to be ducted in return-air duct connection to furnace, generates electrostatic charge; MERV 10 rating.

D. HEPA Air Filter Units:  Sheet metal housing with fan arranged to be ducted to return-air duct connection to furnace, with activated carbon prefilter, high-efficiency particulate air (HEPA) disposable filter[, and carbon VOC].  HEPA shall be as follows:

1. Standard:  UL 586, "High-Efficiency, Particulate, Air Filter Units."

2. Rating:  ASHRAE 52.1, dust-spot efficiency of 65 percent; ASHRAE 52.2, 99.97 percent efficiency to 0.03-micrometer particle size.

2.7 AIR CLEANERS

Retain this Article for air filtration using air cleaners.  If Project uses both air filters and air cleaners, indicate type for each unit on Drawings.

A. Electronic Air Cleaners:  Packaged system, including sheet metal housing, prefilter, power supply, and automatic control device, arranged for mounting in return-air duct at furnace; equip with on-off and test switches and pilot light.

1. Standard:  UL 586, "High-Efficiency, Particulate, Air Filter Units."

2. Rating:  ASHRAE 52.2, particle size to 0.01 micrometer.

3. Static Pressure Drop:  Maximum 0.14-inch wg (35 Pa) at 300-fpm (1.52-m/s) air velocity.

If Project has more than one air cleaner, delete paragraph and subparagraphs below and schedule air cleaner and other components.

B. Capacities and Characteristics:

1. Volts:  <Insert value>.

2. Phase:  <Insert value>.

3. Hertz:  <Insert value>.

4. Minimum Circuit Ampacity:  <Insert value>.

5. Maximum Overcurrent Protection:  <Insert amperage>.

2.8 ULTRAVIOLET GERMICIDAL LIGHTS

A. Description:  Lighting unit in metal housing arranged for installation in supply-air duct and controlled to cycle on and off with furnace fan, with [one] [two] 75-W ultraviolet-light bulb(s).

2.9 HUMIDIFIERS

LEED-NC Credit EQ 7.1 requires humidity control.

A. Minimum capacity rating indicated according to ARI 610, "Central System Humidifiers for Residential Applications."

Retain one of five paragraphs below.  Indicate location, mounting arrangement, and piping connections on Drawings.

B. Media-wheel bypass type with bypass damper and motor-driven media wheel in reservoir with float-valve level control; arranged for mounting on return duct or plenum with bypass connection to supply duct.

C. Wetted-pad, continuous-drain, bypass type with bypass damper and water-flow control orifice; arranged for mounting on return duct or plenum with bypass connection to supply duct.

D. Fan-powered, wetted-pad, continuous-drain type with water-flow control orifice and motor; arranged for mounting on duct or plenum.

E. Pumped, fan-powered, wetted-pad type with reservoir-level control and pump and fan motors; arranged for mounting on duct or plenum.

F. Steam type with electric heating element in stainless-steel reservoir with float-valve level control; arranged for attachment to duct or plenum and for control by humidistat.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which defines requirements for drain pans, humidifier water quality, obstructions, and accessibility.

G. Comply with applicable requirements in ASHRAE 62.1-2004.

If Project has more than one humidifier, delete paragraph and subparagraphs below and schedule humidifier and other components.

H. Capacities and Characteristics:

1. Type:  [Steam] [Media wheel] [Wetted pad with reservoir] [Wetted pad with continuous drain] [Wetted-pad bypass].

Retain subparagraph below for steam humidifiers.

2. Steam Capacity:  <Insert lb/h (kg/h)>.

Retain two subparagraphs below for media wheel and wetted-pad humidifiers.

3. Water Connection Size:  <Insert Nps (Dn)>.

4. Drain Connection Size:  <Insert Nps (Dn)>.

Retain subparagraphs below for media-wheel, fan-powered, and pumped, fan-powered humidifiers.

5. Volts:  <Insert value>.

6. Phase:  <Insert value>.

7. Hertz:  <Insert value>.

8. Minimum Circuit Ampacity:  <Insert value>.

9. Maximum Overcurrent Protection:  <Insert amperage>.

2.10 VENTILATION AIR HEAT EXCHANGER

A. Cabinet:  Steel, with factory-installed interior insulation and manufacturer's standard factory finish.  Fabricate with space for piping and electrical conduits.

B. Heat-Recovery Device:  Fixed-plate, polypropylene copolymer (high-density plastic) heat-exchanger plates evenly spaced and sealed and arranged for counter airflow.

C. Supply and Exhaust Fans:  Forward curved centrifugal with direct drive.  Motors comply with requirements in Division 15 Section "Motors."

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

D. Filters:  1-inch- (25-mm-) thick disposable type[ with ASHRAE 52.2 MERV rating of 6 or higher], in galvanized-steel frame, mounted upstream of unit in both supply and exhaust airstreams.

E. Wiring:  Wire motors and controls so only external connections are required during installation.

2.11 REFRIGERATION COMPONENTS

A. General Refrigeration Component Requirements:

LEED-NC Prerequisite EA 3 requires using CFC-free refrigerants in new HVAC&R systems..

1. Refrigeration compressor, coils, and specialties shall be designed to operate with CFC-free refrigerants.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

2. Energy Efficiency:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1-2004, "Energy Standard for Buildings except Low-Rise Residential Buildings."

Retain option in paragraph below to comply with LEED-NC Prerequisite EQ 1.

B. Refrigerant Coil:  Copper tubes mechanically expanded into aluminum fins.  Comply with ARI 210/240, "Unitary Air-Conditioning and Air-Source Heat Pump Equipment." Match size with furnace.  Include condensate drain pan with accessible drain outlet[ complying with ASHRAE 62.1-2004].

1. Refrigerant Coil Enclosure:  Steel, matching furnace and evaporator coil, with access panel and flanges for integral mounting at or on furnace cabinet and galvanized sheet metal drain pan coated with black asphaltic base paint.

Retain one of first two paragraphs and associated subparagraph below for refrigerant piping.  Retain first paragraph for precharged refrigerant line kits if Project conditions allow standard lengths of tubing without joints; retain second for refrigerant tubing if distance does not allow refrigerant tubing kits.

C. Refrigerant Line Kits:  Annealed-copper suction and liquid lines factory cleaned, dried, pressurized with nitrogen, sealed, and with suction line insulated.  Provide in standard lengths for installation without joints, except at equipment connections.

LEED-NC Prerequisite EA 2 requires minimum pipe insulation thickness equal to requirements in ASHRAE/IESNA 90.1-2004, "Minimum Pipe Insulation Thickness."  Requirements for minimum insulation thickness vary by pipe size and temperature.

1. Flexible Elastomeric:  Closed-cell, sponge- or expanded-rubber materials.  Comply with ASTM C 534, Type I, [1/2 inch (13 mm)] [1 inch (25 mm)] <Insert thickness> thick.

D. Refrigerant Piping:  Comply with requirements in Division 15 Section "Refrigerant Piping."

E. Air-Cooled, Compressor-Condenser Unit:

1. Casing:  Steel, finished with baked enamel, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Provide brass service valves, fittings, and gage ports on exterior of casing.

2. Compressor:  Hermetically sealed [reciprocating] [scroll] [reciprocating or scroll] type.

a. Crankcase heater.

b. [Restrained vibration] [Vibration] isolation mounts for compressor.

c. Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

d. Two-speed compressor motors shall have manual-reset high-pressure switch and automatic-reset low-pressure switch.

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

e. Refrigerant Charge:  [R-22] [R-407C] [R-410A] <Insert type>.

f. Refrigerant:  R-407C or R-410A.

3. Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins, complying with ARI 210/240, and with liquid subcooler.

4. Heat-Pump Components:  Reversing valve and low-temperature air cut-off thermostat.

5. Fan:  Aluminum-propeller type, directly connected to motor.

6. Motor:  Permanently lubricated, with integral thermal-overload protection.

7. Low Ambient Kit:  Permits operation down to 45 deg F (7 deg C).

8. Mounting Base:  Polyethylene.

If Project has more than one refrigeration component, delete paragraph and subparagraphs below and schedule refrigeration component and other components.

F. Capacities and Characteristics:

1. Refrigerant Coil:

a. Total Cooling Capacity:  <Insert Btu/h (kW)>.

b. Sensible Cooling Capacity:  <Insert Btu/h (kW)>.

c. Heating Capacity:  <Insert Btu/h (kW)>.

d. Maximum Air Pressure Drop:  <Insert inches wg (Pa)>.

e. Condensate Drain Size:  <Insert Nps (DN)>.

2. Compressor-Condenser Unit:

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, "Air Conditioners and Condensing Units" for cooling only equipment and "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements" for heat pump applications.

a. Cooling Energy Efficiency[ (EER)] [ (SEER)]:  <Insert value>.

Retain first subparagraph below for heat pump applications.

b. Heating Coefficient of Performance:  <Insert value>.

c. Volts:  <Insert value>.

d. Phase:  <Insert value>.

e. Hertz:  <Insert value>.

f. Full-Load Amperes:  <Insert value>.

g. Minimum Circuit Ampacity:  <Insert value>.

h. Maximum Overcurrent Protection:  <Insert amperage>.

i. Fan Motor Full-Load Amperes:  <Insert value>.

j. Compressor Running Load Amperes:  <Insert value>.

k. Compressor Motor Full-Load Amperes:  <Insert value>.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

B. Examine factory-installed insulation before furnace installation.  Reject units that are wet, moisture damaged, or mold damaged.

C. Examine roughing-in for [gas] [oil] [and refrigerant] piping systems to verify actual locations of piping connections before equipment installation.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain paragraph below for gas-fired furnaces.

A. Install gas-fired furnaces and associated fuel and vent features and systems according to NFPA 54.

Retain first paragraph below for oil-fired furnaces.

B. Install oil-fired furnaces and associated fuel and vent piping according to NFPA 31.

C. Suspended Units:  Suspend from structure using threaded rods, spring hangers, and building attachments.  Secure rods to unit hanger attachments.  Adjust hangers so unit is level and plumb.

Delete subparagraph below if Project site is aseismic.

1. Install seismic restraints to limit movement of furnace by resisting code-required seismic acceleration.

D. Base-Mounted Units:  Secure units to substrate.  Provide optional bottom closure base if required by installation conditions.

Delete subparagraph below if Project site is aseismic.

1. Anchor furnace to substrate to resist code-required seismic acceleration.

E. Controls:  Install thermostats and humidistats at mounting height of 60 inches (1500 mm) above floor.

F. Wiring Method:  Install control wiring in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used.  Conceal control wiring except in unfinished spaces.

Retain one of first two paragraphs below.

G. Install ground-mounted, compressor-condenser components on 4-inch- (100-mm-) thick, reinforced concrete base; 4 inches (100 mm) larger on each side than unit.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete." Coordinate anchor installation with concrete base.

H. Install ground-mounted, compressor-condenser components on polyethylene mounting base.

I. Install roof-mounted, compressor-condenser components on equipment supports specified in Division 7 Section "[Roof Accessories] <Insert Section title>." Anchor units to supports with removable, cadmium-plated fasteners.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain at least one of first two paragraphs below to indicate type of fuel.

A. Gas piping installation requirements are specified in Division 15 Section "Fuel Gas Piping." Drawings indicate general arrangement of piping, fittings, and specialties.  Connect gas piping with union or flange and appliance connector valve.

B. Oil piping installation requirements are specified in Division 15 Section "Fuel Oil Piping." Drawings indicate general arrangement of piping, fittings, and specialties.  Connect oil piping with union or flange and [ball] [gate] valve.

C. Install piping adjacent to equipment to allow service and maintenance.

Retain paragraph below for furnaces with humidifiers.

D. Water piping installation requirements are specified in Division 15 Section "Domestic Water Piping." Drawings indicate general arrangement of piping, fittings, and specialties.  Connect water piping with union and ball valve.

Retain one of first three paragraphs and associated subparagraphs below to indicate type of venting required, or revise to suit Project.

E. Vent Connection, Noncondensing, Gas-Fired Furnaces:  Connect Type B vents to furnace vent connection and extend outdoors.  Type B vents and their installation requirements are specified in Division 15 Section "Breechings, Chimneys, and Stacks."

F. Vent and Outside-Air Connection, Condensing, Gas-Fired Furnaces:  Connect plastic piping vent material to furnace connections and extend outdoors.  Terminate vent outdoors with a cap and in an arrangement that will protect against entry of birds, insects, and dirt.

1. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

2. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

3. Plastic Piping Solvent-Cement Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

a. Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

b. CPVC Piping:  Join according to ASTM D 2846/D 2846M Appendix.

c. PVC Pressure Piping:  Join schedule number ASTM D 1785, PVC pipe and PVC socket fittings according to ASTM D 2672.  Join other-than-schedule-number PVC pipe and socket fittings according to ASTM D 2855.

Retain first subparagraph and associated subparagraphs below for LEED-NC Credit EQ 4.1.

d. Requirements for Low-Emitting Materials:

1) Use CPVC solvent cement that has a VOC content of 490 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2) Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

3) Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

4. Slope pipe vent back to furnace or to outside terminal.

G. Vent Connections, Oil-Fired Furnaces:  Connect Type L vents to furnace vent connection and extend outdoors.  Type L vents and their installation requirements are specified in Division 15 Section "Breechings, Chimneys, and Stacks."

H. Connect ducts to furnace with flexible connector.  Comply with requirements in Division 15 Section "Duct Accessories."

Retain one of two paragraphs and associated subparagraphs below for refrigerant piping.  Retain first paragraph for precharged refrigerant line kits if Project conditions allow standard lengths of tubing without joints; retain second for refrigerant tubing if distance does not allow refrigerant tubing kits.

I. Connect refrigerant tubing kits to refrigerant coil in furnace and to air-cooled, compressor-condenser unit.

Retain one of three subparagraphs below.  See the Evaluations in Division 15 Section "Refrigerant Piping" for a discussion on soldering and brazing refrigerant piping.

1. Flared Joints:  Use ASME B16.26 fitting and flared ends, following procedures in CDA's "Copper Tube Handbook."

2. Soldered Joints:  Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube end.  Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.

3. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8.

J. Comply with requirements in Division 15 Section "Refrigerant Piping" for installation and joint construction of refrigerant piping.

3.4 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Perform electrical test and visual and mechanical inspection.

2. Leak Test:  After installation, charge systems with refrigerant and oil and test for leaks.  Repair leaks, replace lost refrigerant and oil, and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper operation, product capability, and compliance with requirements.

4. Verify that fan wheel is rotating in the correct direction and is not vibrating or binding.

5. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

B. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

3.5 STARTUP SERVICE

A. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Inspect for physical damage to unit casings.

2. Verify that access doors move freely and are weathertight.

3. Clean units and inspect for construction debris.

4. Verify that all bolts and screws are tight.

5. Adjust vibration isolation and flexible connections.

6. Verify that controls are connected and operational.

Retain first paragraph below for units with belt-driven fans.

B. Adjust fan belts to proper alignment and tension.

C. Start unit according to manufacturer's written instructions and complete manufacturer's operational checklist.

D. Measure and record airflows.

E. Verify proper operation of capacity control device.

Retain option in paragraph below for units with belt-driven condenser fans.

F. After startup and performance test, lubricate bearings[ and adjust belt tension].

3.6 ADJUSTING

A. Adjust initial temperature and humidity set points.

B. Set controls, burner, and other adjustments for optimum heating performance and efficiency.  Adjust heat-distribution features, including shutters, dampers, and relays, to provide optimum heating performance and system efficiency.

3.7 CLEANING

A. After completing installation, clean furnaces internally according to manufacturer's written instructions.

B. Install new filters in each furnace within 14 days after Substantial Completion.

3.8 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain condensing units.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15530END OF SECTION 15530

FURNACES
15530 - 1

