Copyright 2004 AIA
MASTERSPEC Full Length
06/04 (R 06/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15541 - GAS-FIRED DUCT HEATERS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include duct heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes gas-fired duct heaters.

1.3 SUBMITTALS

A. Product Data:  For each type of gas-fired duct heater indicated.  Include rated capacities, operating characteristics, and accessories.

In paragraph below, retain first option if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Shop Drawings:  [For gas-fired duct heaters; signed and sealed by a qualified professional engineer.  Include] [For gas-fired duct heaters.  Include] plans, elevations, sections, details, and attachments to other work.

1. Prepared by or under the supervision of a qualified professional engineer detailing fabrication and assembly of gas-fired duct heaters, as well as procedures and diagrams.

2. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

3. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain subparagraph below if thermostat is specified in this Section; delete if thermostats for these units are specified in Division 15 Section "HVAC Instrumentation and Controls."

4. Wiring Diagrams:  Signal and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members to which equipment will be attached.

2. Items penetrating roof and the following:

a. Duct, vent, and gas piping rough-ins and connections.

b. <Insert item.>

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Mechanical Vibration and Seismic Controls."

D. Manufacturer Seismic Qualification Certification:  Submit certification that gas-fired duct heaters, accessories, and components will withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For gas-fired duct heaters to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

B. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace heat exchanger of gas-fired duct heater that fails in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.  Two-year warranty is applicable to aluminized heat exchangers; five-year warranty, to stainless-steel heat exchangers.

1. Warranty Period:  [Two] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURED UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Lennox Industries, Inc.

2. Modine Manufacturing Company.

3. Reznor/Thomas & Betts Corporation.

4. Sterling HVAC Products; Div. of Mestek Technology Inc.

5. <Insert manufacturer's name.>

D. Description:  Factory assembled, piped, and wired; and complying with ANSI Z83.8/CSA 2.6.

E. Fuel Type:  Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Retain paragraph and subparagraph below unless more than one type of venting is required; in which case, delete below and indicate type of venting in a schedule on Drawings.  See the sample schedule in the Evaluations.

F. Type of Venting:  [Gravity] [Power] [Indoor, separated combustion, power] vented.

Retain subparagraph below with third option in paragraph above.

1. Concentric, Terminal Vent Assembly:  Combined combustion-air inlet and power-vent outlet with wall or roof caps.  Include adapter assembly for connection to inlet and outlet pipes, and flashing for wall or roof penetration.

Retain one or both of first two paragraphs and associated subparagraphs below, or revise to suit selected equipment.

G. Indoor External Housing:  Steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

1. External Casings and Cabinets:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface.

Retain subparagraph and associated subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

2. Suspension Attachments:  Reinforce suspension attachments at connection to gas-fired duct heaters.

a. Seismic Fabrication Requirements:  Fabricate suspension attachments of gas-fired duct heaters, accessories mountings, and components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Mechanical Vibration and Seismic Controls" when gas-fired duct heater is anchored to building structure.

H. Outdoor External Housing:  Weatherproof steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

1. External Casings and Cabinets:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface.

I. Internal Casing:  Aluminized steel, arranged to contain airflow, with duct flanges at inlet and outlet.

Retain paragraph below unless more than one heat-exchanger material is required; in which case, delete below and indicate heat-exchanger material in a schedule on Drawings.  See the sample schedule in the Evaluations.

J. Heat Exchanger:  [Aluminized] [Stainless] steel.

Retain paragraph below unless more than one burner material is required; in which case, delete below and indicate burner material in a schedule on Drawings.  See the sample schedule in the Evaluations.

K. Burner Material:  [Aluminized steel with stainless-steel inserts] [Stainless steel].

Retain first paragraph below for power-vented model.

L. Power Venter:  Integral, motorized centrifugal fan interlocked with gas valve.

M. Controls:  Regulated redundant gas valve containing pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

1. Gas Control Valve:  [Single stage] [Two stage] [Modulating].

2. Ignition:  [Standing pilot] [Electronically controlled electric spark with flame sensor].

3. Fan Thermal Switch:  Operates fan on heat-exchanger temperature.

First option in first subparagraph below is for gravity-vented units; second option is for units with a power venter.

4. Vent Flow Verification:  [Flame rollout switch] [Differential pressure switch to verify open vent].

5. Control transformer.

6. High Limit:  Thermal switch or fuse to stop burner.

7. Thermostat:  Devices and wiring are specified in Division 15 Section "HVAC Instrumentation and Controls."

Retain subparagraph above or one of four subparagraphs below, or revise to suit selected equipment.

8. Thermostat:  Single-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

9. Thermostat:  2-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

10. Thermostat:  Single-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

11. Thermostat:  2-stage type with duct-mounting sensor and 50 to 90 deg F (10 to 32 deg C) operating range.

If Project has more than one type or configuration of gas-fired duct heater, delete paragraph and subparagraphs below and schedule duct heaters on Drawings.

N. Capacities and Characteristics:

1. Flue Outlet:  <Insert inches (mm)> diameter.

2. Gas Input:  <Insert Btu/h (kW).>

3. Gas Output:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

4. Minimum Combustion Efficiency:  [80] <Insert value> percent.

5. Minimum Airflow:  <Insert cfm (L/s).>

6. External Static Pressure:  <Insert inches wg (kPa).>

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain first option in first paragraph below for projects in the U.S.; retain second option for projects in Canada.

A. Install and connect gas-fired duct heaters and associated fuel and vent features and systems according to [NFPA 54] [CAN/CSA B149.1], applicable local codes and regulations, and manufacturer's written installation instructions.

B. Suspended Units:  Suspend from substrate using threaded rods, spring hangers, and building attachments.  Secure rods to unit hanger attachments.  Adjust hangers so unit is level and plumb.

1. Spring hangers[ and seismic restraints] are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Delete subparagraph below if Project site is aseismic.

2. Restrain the unit to resist code-required horizontal acceleration.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to gas-fired duct heaters to allow service and maintenance.

C. Gas Piping:  Comply with Division 15 Section "Fuel Gas Piping." Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

D. Vent Connections:  Comply with Division 15 Section "Breechings, Chimneys, and Stacks."

E. Duct Connections:  Comply with Division 15 Section "[Metal Ducts] [Nonmetal Ducts]."

F. Electrical Connections:  Comply with applicable requirements in Division 16 Sections.

1. Install electrical devices furnished with heaters but not specified to be factory mounted.

3.3 FIELD QUALITY CONTROL

Retain one of first two paragraphs below.  Retain first to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by either entity in two paragraphs above.

C. Tests and Inspections:

1. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

2. Verify bearing lubrication.

3. Verify proper motor rotation.

4. Test Reports:  Prepare a written report to record the following:

a. Test procedures used.

b. Test results that comply with requirements.

c. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

D. Remove and replace malfunctioning units and retest as specified above.

3.4 ADJUSTING

A. Adjust initial temperature set points.

B. Adjust burner and other unit components for optimum heating performance and efficiency.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain gas-fired duct heaters.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15541END OF SECTION 15541

GAS-FIRED DUCT HEATERS
15541 - 1

