Copyright 2001 AIA
MASTERSPEC Full Length
12/01 (R 06/06)

Copyright 2001 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15562 - INDIRECT-FIRED H&V UNITS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include fuel-fired H&V units may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes indirect-fired H&V units with the following accessories:

Adjust list below to suit Project.

1. [Gas] [Oil] furnace.

2. Evaporative cooling package.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Breechings, Chimneys, and Stacks" for vent piping.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories.

B. LEED Submittal:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

Professional engineer qualifications in first paragraph below are specified in Division 1 Section "Quality Requirements."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, and methods of field assembly, components, and location and size of each field connection.  Prepare the following by or under the supervision of a qualified professional engineer:

Retain subparagraphs below to delegate design responsibility to Contractor or to require structural data to be submitted for review as another way to verify compliance with requirements.  Retain first subparagraph if restrained vibration isolation roof rails are retained in Part 3 "Installation" Article.

1. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

Retain first subparagraph below if roof curb is supplied by unit manufacturer.

2. Mounting Details:  For securing and flashing roof curb to roof structure.  Indicate coordinating requirements with roof membrane system.

3. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, and base weights.

4. Wiring Diagrams:  Power, signal, and control wiring.

D. Coordination Drawings:  Roof-mounted units and roof-curb mounting details drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Size and location of rooftop unit mounting rails and anchor points and methods for anchoring units to curb.

2. Required roof penetrations for ducts, pipes, and electrical raceways, including size and location of each penetration.

E. Startup service reports.

F. Operation and Maintenance Data:  For indirect-fired H&V units to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 Section "Product Requirements."

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of indirect-fired H&V units and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

D. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

E. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

B. Coordinate size, location, installation, and structural capacity of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

Retain paragraph above if roof curbs and equipment supports are specified in Division 7; retain paragraph below if roof curbs are to be provided by unit manufacturer and are specified in this Section.

C. Coordinate size, location and installation of unit manufacturer's roof curbs and equipment supports with roof Installer.

Retain subparagraph below, where units are required to withstand seismic forces, with either of last two paragraphs above.

1. Coordinate installation of restrained vibration isolation roof-curb rails, which are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to replace components listed below of indirect-fired H&V units that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.  Warranty periods vary among manufacturers and unit sizes.

1. Warranty Period for Heat Exchangers:  Manufacturer's standard, but not less than [five] [10] <Insert number> years from date of Substantial Completion.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Retain first subparagraph below for units with filters.

1. Filters:  [One] <Insert number> set(s) for each unit.

2. Fan Belts:  [One] <Insert number> set(s) for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. AbsolutAire, Inc.

2. Advanced Climate Technologies, Inc.

3. Air Dynamics Co.

4. Air Economy Corp.

5. Applied Air; Mestek, Inc.

6. ARES; Mars Air Products.

7. Bananza Air Management Systems Inc.; Div. of Rapid Engineering, Inc.

8. BessamAire, Inc.

9. Cambridge Engineering, Inc.

10. E. K. Campbell Co.; Mechanical Products Division of Thomas & Betts Corporation.

11. Captive-Air Systems, Inc.

12. CES Group; Ventrol Air Handling Systems, Inc.

13. Des Champs Laboratories Incorporated; a unit of Entrodyne Corporation.

14. Energy Jet U.S.

15. Engineered Air.

16. Greenheck.

17. Hastings Industries; Division of Eric, Inc.

18. Industrial Commercial Engineering.

19. Jackson & Church; Div. of Donlee Technologies Inc.

20. KING.

21. LC Systems.

22. Modine Mfg. Co.; Commercial HVAC&R Division.

23. Powrmatic, Inc.

24. Rapid Engineering, Inc.

25. Reznor-Thomas & Betts Corporation; Mechanical Products Division.

26. Sterling Gas; Mestek, Inc.

27. Temprite; Mestek, Inc.

28. Titan Air Incorporated.

29. Trane Company (The); Unitary Products Group.

30. Weather-Rite, Inc.

31. <Insert manufacturer's name.>

2.2 PACKAGED UNITS

A. Factory-assembled, prewired, self-contained unit consisting of cabinet, supply fan, controls, [filters,] [evaporative cooling package,] and indirect-fired [gas] [oil] furnace to be installed [outside] [inside] the building.

2.3 CABINET

A. Cabinet:  [Single] [Double]-wall galvanized-steel panels, formed to ensure rigidity and supported by galvanized-steel channels or structural channel supports with lifting lugs.[ Cabinet shall be fully weatherized for outside installation.]

B. Access Panels:  [Lift-out] [Piano hinged with cam-lock fasteners] for furnace and fan motor assemblies on both sides of unit.

Retain first option in first paragraph below for outside unit, second option for inside unit.  Verify insulation thickness.  Not all manufacturers furnish units with 2-inch (50-mm) thickness.

C. Internal Insulation:  Fibrous-glass duct lining, comply with ASTM C 1071, Type II, applied on [complete unit] [furnace and fan sections only].

1. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)].

2. Insulation Adhesive:  Comply with ASTM C 916, Type I.

3. Mechanical Fasteners:  Galvanized steel suitable for adhesive attachment, mechanical attachment, or welding attachment to casing without damaging liner when applied as recommended by manufacturer and without causing air leakage.

D. Finish:  Heat-resistant, baked enamel.

Retain first paragraph below if units are not connected to ducts.

E. Discharge:  [Horizontal] [Vertical]-pattern, galvanized-steel assembly with diffusers incorporating individually adjustable vanes.

F. Roof Curb:  Full-perimeter curb of sheet metal, minimum [16 inches (400 mm)] <Insert dimension> high, with wood nailer, neoprene sealing strip, and welded Z-bar flashing.

Retain paragraph below to comply with LEED-NC Prerequisite EQ 1.

G. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

2.4 SUPPLY-AIR FAN

A. Fan Type:  Centrifugal, rated according to AMCA 210; statically and dynamically balanced, galvanized steel; mounted on solid-steel shaft with heavy-duty[, self-aligning, permanently lubricated ball bearings] [, pillow-block bearings rated for L50 or 200,000 hours with external grease fittings].

B. Motor:  [Open dripproof] [Totally enclosed], single-speed motor.

C. Drive:  V-belt drive with matching fan pulley and adjustable motor sheaves and belt assembly.

Retain "restrained" option in paragraph below for units installed in seismic areas, and select between elastomeric- and spring-type isolators.

D. Mounting:  Fan wheel, motor, and drives shall be mounted in fan casing with [restrained,] [elastomeric] [spring] isolators.

2.5 OUTDOOR-AIR INTAKE

Retain this Article for outside units only.  Select or insert percentage of outdoor air to match maximum amount of makeup air required or outdoor air to meet ventilation requirements of authorities having jurisdiction.

A. Outdoor-Air Hood:  Galvanized steel with rain baffles, bird screen[ complying with ASHRAE 62.1-2004], and finish to match cabinet; and sized to supply maximum [30] [100] <Insert number> percent outdoor air.

2.6 AIR FILTERS

Retain this Article for units that circulate some return air.  Filters are not often used for 100 percent outdoor-air, indirect-fired heating-only units.  For units that circulate some return air, filters can be added for return air.  Standard filters are 1-inch- (25-mm-) thick, low-efficiency, washable media and replaceable glass-fiber media.  Optional, 2-inch- (50-mm-) thick, low-efficiency, glass-fiber or polyester filters, and medium-efficiency filters, are available from most manufacturers.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

A. Comply with NFPA 90A.

B. Cleanable Filters:  [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, cleanable metal mesh.

Retain paragraph above or paragraph and subparagraphs below.

C. Disposable Panel Filters:  [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, factory-fabricated, flat-panel-type, disposable air filters with holding frames[, with a minimum efficiency report value of 6 according to ASHRAE 52.2 and 90 percent average arrestance according to ASHRAE 52.1].

1. Media:  Interlaced [glass] [polyester] fibers.

2. Frame:  Galvanized steel.

2.7 DAMPERS

Low-leak dampers can be furnished for return air.  Retain option in first paragraph below for units that circulate varying amounts of return air.  Return-air dampers modulate proportionally with outdoor-air dampers to vary the amount of return and outdoor air delivered to the space.

A. Outdoor-Air [and Return-Air ]Damper:  Galvanized-steel, opposed-blade dampers with vinyl blade seals and stainless-steel jamb seals, having a maximum leakage of 10 cfm/sq. ft. (51 L/s per sq. m) of damper area, at differential pressure of 2-inch wg (448 Pa).

B. Damper Operator:  Direct coupled, electronic with spring return or fully modulating as required by the control sequence.

2.8 INDIRECT-FIRED GAS FURNACE

Retain this Article for gas-fired units.

A. Description:  Factory assembled, piped, and wired; and complying with ANSI Z21.47, "Gas-Fired Central Furnaces," and NFPA 54, "National Fuel Gas Code."

1. AGA Approval:  Designed and certified by and bearing label of AGA.

2. Burners:  [Aluminized steel with stainless-steel inserts] [Stainless steel].

a. Gas Control Valve:  [Single stage] [Two stage] [Modulating].

b. Fuel:  [Natural] [Propane] gas.

c. Minimum Combustion Efficiency:  80 percent.

d. Ignition:  Electronically controlled electric spark with flame sensor.

High-altitude feature below is available from some manufacturers.

e. High-Altitude [Model] [Kit]:  For Project elevation above sea level.

Retain one of two paragraphs below.

B. Venting:  Gravity vented.

C. Power Vent:  Integral, motorized centrifugal fan interlocked with gas valve.

Intake in paragraph below is available on inside units only.

D. Combustion-Air Intake:  Separate combustion-air intake and vent terminal assembly.

Select one of first two paragraphs and associated subparagraph below or edit to suit equipment selected.

E. Inside Unit External Housing:  Steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

F. Outside Unit External Housing:  Weatherproof steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

1. External Casing and Cabinet Finish:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface in color to match fan section.

G. Internal Casing:  Aluminized steel, arranged to contain airflow, with duct flanges at inlet and outlet.

H. Heat Exchanger:  [Aluminized] [Stainless] steel.

I. Heat-Exchanger Drain Pan:  Stainless steel.

J. Safety Controls:

1. Vent Flow Verification:  [Differential pressure switch to verify open vent] [Flame rollout switch].

2. Control Transformer:  24-V ac.

3. High Limit:  Thermal switch or fuse to stop burner.

4. Gas Train:  Regulated, redundant, 24-V ac gas valve assembly containing pilot solenoid valve, [hydraulic] [electronic]-modulating temperature control valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

5. Purge-period timer shall automatically delay burner ignition and bypass low-limit control.

Owner's insurance underwriter may require FMG or IRI gas train.

6. Gas Manifold:  Safety switches and controls to comply with ANSI standards [and] [FMG] [IRI].

Airflow proving switch below is an option provided by some manufacturers.

7. Airflow Proving Switch:  Differential pressure switch senses correct airflow before energizing pilot.

8. Automatic-Reset, High-Limit Control Device:  Stops burner and closes main gas valve if high-limit temperature is exceeded.

9. Safety Lockout Switch:  Locks out ignition sequence if burner fails to light after three tries.  Controls are reset manually by turning the unit off and on.

2.9 OIL-FIRED FURNACE

Retain this Article for oil-fired units.

A. Description:  Factory assembled, piped, and wired; and complying with UL 727, "Oil-Fired Central Furnaces."

Select one of first two paragraphs and associated subparagraph below or edit to suit equipment selected.

B. Inside Unit External Housing:  Steel cabinet with integral support inserts and removable bottom arranged to serve as a drain pan.

C. Outside Unit External Housing:  Weatherproof steel cabinet with integral support inserts and removable bottom arranged to serve as drain pan.

1. External Casing and Cabinet Finish:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface in color to match fan section.

D. Internal Casing:  Aluminized steel, arranged to contain airflow, with duct flanges at inlet and outlet.

E. Heat Exchanger:  Welded, [stainless ]steel with flame observation port, carbon dioxide sample port, and access panels for clean-out and service.

F. Burners:  Flame-retention, pressure-atomizing, forced-draft, gun type; with integral fuel pump and electronic spark ignition.

1. Fuel:  No. [2] <Insert number> fuel oil.

ASHRAE/IESNA 90.1 requires minimum 80 percent efficiency up to 225,000 Btu/h (66 kW/h) and 81 percent over that capacity.  Some manufacturers claim higher efficiencies.

2. Minimum Thermal Efficiency:  [80] [81] <Insert number> percent.

3. Ignition:  Electronically controlled electric spark with flame sensor.

G. Safety Controls:

1. Factory piped and wired to electrical junction box mounted on unit.

2. Oil-pressure switch.

3. Control Transformer:  Integrally mounted 24-V ac.

4. Cad-cell safety system.

5. Manual reset flame safety.

H. Accessories:

1. Factory mounted and wired to electrical junction box on unit.

2. Oil Booster Pump:  [30-gph (108-L/h)] [70-gph (252-L/h)] capacity; motor and 2-stage fuel unit with pressure-regulating valve and strainer.

3. Oil-pressure relief valve.

4. Outdoor Combustion-Air Adapter:  Sealed to housing and fitted with quick access cover, or door and fitting for terminating outdoor-air duct.

2.10 EVAPORATIVE COOLING PACKAGE

A. Cabinet:  [Single] [Double]-wall, galvanized- or aluminized-steel panels[ lined with ABS polymer], formed to ensure rigidity and supported by galvanized-steel channels or structural channel supports with lifting lugs and having a stainless-steel reservoir with overflow and drain with full-port, brass-fitted ball valve.[ Cabinet shall be fully weatherized for outside installation.]

1. External Casing and Cabinet Finish:  [Baked enamel] [Powder coating] over corrosion-resistant-treated surface in color to match fan section.

B. Media:  UL 900, Class 2, [6-inch- (150-mm-)] [8-inch- (200-mm-)] [12-inch- (300-mm-)] thick [cellulose] [glass-fiber] media with rigidizing agents, fungicides, and wetting agents.  Minimum [90] <Insert number> percent contact factor.

Retain subparagraph below for units with more than 600-fpm (3.05-m/s) face velocity.

1. Moisture elimination pad.

C. Water-Circulation System:  Submersible centrifugal sump pump with inlet strainer, brass balancing valve located in pump discharge, and thermally protected motor; water distribution troughs or piping at top of media pads; and float-operated, makeup water and bleed-off valves.

Subparagraph below is an optional feature.  Retain for automatic seasonal filling and draining of sump.

1. Automatic Fill and Drain Kit:  Water supply and drain, solenoid valves for initial sump fill and for draining sump.

Retain paragraph and subparagraph above or paragraph below.  See controls in "Controls" Article for operating sequence.

D. Water-Saver System:  Timer, solenoid valve, and water distribution piping to apply the water supply to the media.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.13 - "Humidifiers and Water-Spray Systems," sets requirements for water-spray systems.  ASHRAE 62.1-2004 also defines requirements for drain pans, water quality, obstructions, and accessibility.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.

E. Comply with applicable requirements in ASHRAE 62.1-2004.

2.11 CONTROLS

A. Factory-wired, fuse-protected control transformer, connection for power supply and field-wired unit to remote control panel.

B. Control Panel:  [Surface-mounted] [Recessed, with trim ring,] remote panel, with engraved plastic cover, and the following lights and switches:

1. [On-off] [On-off-auto] fan switch.

2. [Summer-winter-off] [Heat-vent-cool] switch.[ Automatic changeover.]

3. Supply-fan operation indicating light.

4. Heating operation indicating light.

5. Thermostat.

6. Damper position potentiometer.

Retain first subparagraph below for units with evaporative cooling package.

7. Cooling operation indicating light.

8. Dirty-filter indicating light operated by unit-mounted differential pressure switch.

9. Safety-lockout indicating light.

C. Refer to Division 15 Section "HVAC Instrumentation and Controls" for control equipment and sequence of operation.

If retaining paragraph above, delete the remainder of this Article.

D. Control Devices:

1. Remote Thermostat:  Adjustable room thermostat with temperature readout.

2. Remote Setback Thermostat:  Adjustable room thermostat without temperature readout.

3. Static-Pressure Transmitter:  Nondirectional sensor with suitable range for expected input, and temperature compensated.

4. Fire-Protection Thermostats:  Fixed or adjustable settings to operate at not less than 75 deg F (24 deg C) above normal maximum operating temperature.

5. Timers:  Seven-day, programming-switch timer with synchronous-timing motor and seven-day dial; continuously charged, nickel-cadmium-battery-driven, eight-hour, power-failure carryover; multiple-switch trippers; minimum of two and maximum of eight signals per day with two normally open and two normally closed output contacts.

Retain subparagraph above or first subparagraph below.  Programmable clock below is best option for applications requiring more than one timer.

6. Timers:  Solid-state, programmable time control with 4 separate programs; 24-hour battery carryover; individual on-off-auto switches for each program; 365-day calendar with 20 programmable holidays; choice of fail-safe operation for each program; and system fault alarm.

7. Ionization-Type Smoke Detectors:  24-V dc, nominal; self-restoring; plug-in arrangement; integral visual-indicating light; sensitivity that can be tested and adjusted in place after installation; integral addressable module; remote controllability; responsive to both visible and invisible products of combustion; self-compensating for changes in environmental conditions.

E. Fan Control:  Interlock fan to start with exhaust fan(s).  See Division 15 Section "[Axial Fans] [Centrifugal Fans] [Power Ventilators] [Sequence of Operation]" for exhaust fan controls.

Retain paragraph above or paragraph and subparagraphs below.  Retain below to control both exhaust fans and makeup air units with a single device; delete if exhaust fans are separately controlled.

F. Fan Control:  Timer starts and stops indirect-fired H&V unit and exhaust fan(s).

Retain first subparagraph below for units with evaporative cooling package.

1. Fan-Discharge Thermostat:  Stops fan on burner failure when outdoor-air temperature is less than 40 deg F (4 deg C).

2. Smoke detectors, located in supply[ and return] air, shall stop fans when the presence of smoke is detected.

Retain one of first two paragraphs and associated subparagraphs below.  Retain first for units that supply 100 percent outdoor air.

G. Outdoor-Air Damper Control, 100 Percent Outdoor-Air Units:  Outdoor-air damper shall open when supply fan starts, and close when fan stops.

Retain first paragraph and subparagraphs below for units that circulate varying amounts of outdoor and return air.

H. Mixed Outdoor- and Return-Air Damper Control:  When fan is running, outdoor- and return-air dampers shall modulate to supply minimum outdoor air as follows:

1. Minimum [30] <Insert number> percent outdoor air.

2. Outdoor-air quantity adjusted by potentiometer on control panel.

3. Outdoor-air quantity to maintain minimum building static pressure.

I. Temperature Control:  Operates gas valve to maintain supply-air temperature.

1. Operates gas valve to maintain discharge-air temperature with factory-mounted sensor in blower outlet.

Retain subparagraph above or first subparagraph below.

2. Operates gas valve to maintain space temperature with wall-mounting, field-wired sensor[ with temperature adjustment,] [and unit-mounted control adjustment] [and adjustment on remote-control panel].

3. Timer shall select remote setback thermostat to maintain space temperature at [50 deg F (10 deg C)] <Insert deg F (deg C)>.

4. Furnace Control:  Two or four steps of control using one or two furnace sections in series.

Retain subparagraph above or below.

5. Furnace Control:  20 to 100 percent modulation of the firing rate.  10 to 100 percent with dual furnace units.

Retain paragraph and subparagraphs below for units with evaporative cooling package.

J. Evaporative Cooling Controls:

Retain subparagraph below if specifying water-circulation system.  Delete if using water-saver system.

1. Start and stop water-circulation-system sump pump to maintain space temperature.

Retain two subparagraphs below if "Automatic Fill and Drain Kit" Subparagraph is retained in "Evaporative Cooling Package" Article.  This optional feature allows for seasonal filling and draining of sump.

2. Automatic Fill Control:  A switch in the unit control panel shall close sump drain valve and open makeup water valve.

3. Automatic Drain Control:  Opens sump drain valve and closes makeup water valve [from a switch in the unit control panel] [when an outside thermostat senses 40 deg F (4 deg C) or less].

Water-saver system below is an optional feature.  Delete if using water-circulation system.

4. Water-Saver System:  Remote thermostat shall open water-supply valve to maintain dry-bulb temperature in space.  Timer shall activate thermostat circuit.

Retain paragraph and subparagraphs below if units must be linked to DDC system.

K. DDC:  Stand-alone control module for link between unit controls and DDC system.  Control module shall be compatible with temperature-control system specified in Division 15 Section "HVAC Instrumentation and Controls."

1. Provide start and stop interface relay, and relay to notify DDC system alarm condition.

2. Provide hardware interface or additional sensors as follows:

a. Room temperature.

b. Discharge-air temperature.

c. Furnace operating.

2.12 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." Add other characteristics to this Article if required to suit Project.

A. Comply with requirements in Division 15 Section "Motors."

2.13 CAPACITIES AND CHARACTERISTICS

Delete this Article if capacities and characteristics are scheduled on Drawings.

A. Fan:

1. Airflow in CFM (L/s):  <Insert quantity.>

2. External Static Pressure:  <Insert inches wg (kPa).>

3. Maximum RPM:  <Insert number.>

4. Minimum Size:  <Insert inches (mm).>

B. Fan Motor:

1. HP:  <Insert hp.>

2. RPM:  <Insert value.>

C. Single-Point Electrical Connection:

1. Volts:  [120] [240] [277] [480] <Insert voltage>.

2. Phase:  [Single] [Three].

3. Hertz:  60.

4. Full-Load Amperes:  <Insert amperes.>

5. Minimum Circuit Ampacity:  <Insert amperes.>

6. Maximum Overcurrent Protection:  <Insert amperes.>

Retain paragraph and subparagraphs below for gas furnaces.

D. Indirect-Fired Gas Furnace:

1. Entering-Air Temperature:  <Insert deg F (deg C).>

2. Leaving-Air Temperature:  <Insert deg F (deg C).>

Delete first subparagraph below if same as fan.

3. Airflow:  <Insert cfm (L/s).>

4. Gas Input:  <Insert MBh (kW).>

5. Output:  <Insert MBh (kW).>

Retain paragraph and subparagraphs below for oil furnaces.

E. Indirect-Fired Oil Furnace:

1. Oil Input:  <Insert gph (L/s).>

2. Output:  <Insert MBh (kW).>

3. Fuel Supply Connection Size:  <Insert NPS (DN).>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting installation of indirect-fired H&V units.

B. Examine roughing-in for piping, ducts, and electrical systems to verify actual locations of connections before equipment installation.

Retain first paragraph below for roof-mounted units.

C. Examine roof curbs and equipment supports for suitable conditions where rooftop replacement-air units will be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain paragraph below for gas-fired units.

A. Install gas-fired units according to NFPA 54, "National Fuel Gas Code."

Retain paragraph below for oil-fired units.

B. Install oil-fired duct heaters and associated fuel and vent piping according to NFPA 31 and applicable local codes and regulations.

Retain one of two paragraphs below for roof-mounting units.  Retain first if unit manufacturer furnishes curbs.  Retain second for projects located in seismic areas.  Delete both if unit is installed on field-fabricated curbs or pilings specified in Division 7 Section "Roof Accessories."

C. Install roof curb on roof structure, according to [ARI Guideline B.] [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] Install and secure indirect-fired H&V units on curbs, and coordinate roof penetrations and flashing with roof construction.

D. Install restrained vibration isolation roof-curb rails on roof structure according to [ARI Guideline B.] [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] Install and secure indirect-fired H&V units on rails, and coordinate roof penetrations and flashing with roof construction.  Restrained isolation roof-curb rails are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Retain one of first two paragraphs below for inside units.  Retain first for suspended units and second for floor-mounted units.

E. Install suspended units from spring hangers with minimum 1-inch (25-mm) static deflection; refer to Division 15 Section "Mechanical Vibration and Seismic Controls."

F. Install floor-mounted units on[ restrained,] spring isolators with minimum 1-inch (25-mm) static deflection; refer to Division 15 Section "Mechanical Vibration and Seismic Controls."

G. Install controls and equipment shipped by manufacturer for field installation with indirect-fired H&V units.

3.3 CONNECTIONS

Coordinate installations and specialty arrangements with schematics on Drawings and with requirements specified in individual piping, duct, and electrical sections.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping Connections:  Drawings indicate general arrangement of piping, fittings, and specialties.  Install piping adjacent to machine to allow service and maintenance.

Retain subparagraph below for gas-fired units.

1. Gas Piping:  Comply with requirements in Division 15 Section "Fuel Gas Piping." Connect gas piping with shutoff valve and union and with sufficient clearance for burner removal and service.  Provide AGA-approved flexible connectors.

Retain subparagraph below for oil-fired units.

2. Fuel Oil Piping:  Comply with requirements in Division 15 Section "Fuel Oil Piping." Connect to fuel oil supply and return piping with shutoff valve and union at each connection.

Retain two subparagraphs below for evaporative cooler package.

3. Makeup Water:  Comply with requirements in Division 15 Section "Domestic Water Piping" for valves and accessories on piping connections to evaporative cooling units.

4. Drain:  Comply with requirements in Division 15 Section "Sanitary Waste and Vent Piping" for traps and accessories on piping connections to evaporative cooling units.

B. Duct Connections:  Duct installation requirements are specified in Division 15 Section "Metal Ducts." Drawings indicate the general arrangement of ducts.  Connect supply[ and return] ducts to indirect-fired H&V units with flexible duct connectors.  Flexible duct connectors are specified in Division 15 Section "Duct Accessories."

C. Ground equipment according to Division 16 Section "Grounding and Bonding."

D. Connect wiring according to Division 16 Section "Conductors and Cables."

3.4 STARTUP SERVICE

Retain first paragraph below if factory-authorized service representative is required.

A. Engage a factory-authorized service representative to perform startup service.

B. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Inspect for visible damage to furnace combustion chamber.

2. Inspect casing insulation for integrity, moisture content, and adhesion.

3. Verify that clearances have been provided for servicing.

4. Verify that controls are connected and operable.

Retain first subparagraph below if filters are required.

5. Verify that filters are installed.

6. Purge gas line.

7. Inspect and adjust vibration isolators[ and seismic restraints].

8. Verify bearing lubrication.

9. Inspect fan-wheel rotation for movement in correct direction without vibration and binding.

10. Adjust fan belts to proper alignment and tension.

11. Start unit according to manufacturer's written instructions.

12. Complete startup sheets and attach copy with Contractor's startup report.

13. Inspect and record performance of interlocks and protective devices; verify sequences.

14. Operate unit for run-in period recommended by manufacturer.

15. Perform the following operations for both minimum and maximum firing and adjust burner for peak efficiency:

a. Gas Burner:

1) Measure gas pressure at manifold.

2) Measure combustion-air temperature at inlet to combustion chamber.

3) Measure supply-air temperature and volume when burner is at maximum firing rate and when burner is off.  Calculate useful heat to supply air.

b. Oil Burner:

1) Cycle the burner through prepurge, purge, ignition, and post purge.

2) Remove flame sensor from sight pipe, and initiate burner operation to demonstrate proper flame safety operation.

3) Restart the burner to verify proper operation of burner and flame safety.

4) Adjust the burner to obtain manufacturer's recommended carbon dioxide and smoke ratings in the flue at high fire, low fire, and modulation through full range.

5) Measure combustion-air temperature at inlet to combustion chamber.

6) Measure supply-air temperature and volume when burner is at maximum firing rate and when burner is off.  Calculate useful heat to supply air.

16. Calibrate thermostats.

17. Adjust and inspect high-temperature limits.

18. Inspect dampers, if any, for proper stroke and interlock with return-air dampers.

Retain first subparagraph and associated subparagraphs below only for units with evaporative cooler package.

19. Start evaporative cooler system and measure and record the following:

a. Leaving-air, dry- and wet-bulb temperatures.

b. Entering-air, dry- and wet-bulb temperatures.

20. Inspect controls for correct sequencing of heating, mixing dampers, refrigeration, and normal and emergency shutdown.

21. Measure and record airflow.  Plot fan volumes on fan curve.

22. Verify operation of remote panel, including pilot-operation and failure modes.  Inspect the following:

a. High-limit heat.

b. Alarms.

23. After startup and performance testing, change filters, verify bearing lubrication, and adjust belt tension.

C. Remove and replace malfunctioning components that do not pass tests and inspections and retest as specified above.

D. Prepare written report of the results of startup services.

3.5 ADJUSTING

A. Adjust initial temperature set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain indirect-fired H&V units.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 15562END OF SECTION 15562

INDIRECT-FIRED H&V UNITS
15562 - 1

