Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15731 - PACKAGED TERMINAL AIR CONDITIONERS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include packaged terminal air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes packaged terminal air conditioners and their accessories and controls, in the following configurations:

1. [Through-the-wall] [Freestanding] [Through-the-wall and freestanding] air conditioners.

2. Cooling-only units.

3. Heat-pump units.

4. Cooling units with electric heat.

5. Cooling units with hydronic heat.

6. Cooling units with indirect-fired gas heat.

1.3 SUBMITTALS

First four paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, furnished specialties, electrical characteristics, and accessories.

B. LEED Submittals:

See "LEED Rating System" Article in the Evaluations for discussion on LEED-NC prerequisites and credits.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  For packaged terminal air conditioners.  Include plans, elevations, sections, details for wall penetrations,[ seismic bracing,] and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams:  For power, signal, and control wiring.

D. Color Samples:  For unit cabinet, discharge grille, and exterior louver, and for each color and texture specified.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

E. Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for packaged terminal air conditioners.

F. Field quality-control reports.

G. Operation and Maintenance Data:  For packaged terminal air conditioners to include in emergency, operation, and maintenance manuals.

H. Warranty:  Sample of special warranty.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  In addition to establishing minimum ventilation rates, ASHRAE 62.1-2004 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004,  Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - "Ventilation Rate Procedures," and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

C. ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004.

1.5 COORDINATION

A. Coordinate layout and installation of packaged terminal air conditioners and wall construction with other construction that penetrates walls or is supported by them.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of packaged terminal air conditioners that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2.

1. Warranty Period for Sealed Refrigeration System:  Manufacturer's standard, but not less than [five] <Insert number> years from date of Substantial Completion, including components and labor.

2. Warranty Period for Nonsealed System Parts:  Manufacturer's standard, but not less than [five] <Insert number> years from date of Substantial Completion, including only components and excluding labor.

3. Warranty Period for Heat Exchangers:  Manufacturer's standard, but not less than [five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two paragraphs and list of manufacturers in this article.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Carrier Corporation; a United Technologies company.

2. ClimateMaster, Inc.

3. Friedrich Air Conditioning Co.

4. General Electric Company; GE Consumer & Industrial - Appliances.

5. McQuay International.

6. Suburban Manufacturing Company; a subsidiary of AIRXCEL, Inc.

7. Trane; a business of American Standard Companies.

8. <Insert manufacturer's name>.

2.2 MANUFACTURED UNITS

Retain first option in paragraph below for heating and cooling units and for heat pumps with supplemental heat.

A. Description:  Factory-assembled and -tested, self-contained, packaged terminal air conditioner with room cabinet, electric refrigeration system,[ heating,] and temperature controls; fully charged with refrigerant and filled with oil; with [cord-connected] [hardwired] chassis.

2.3 CHASSIS

A. Cabinet:  [0.052-inch- (1.32-mm-)] <Insert dimension> thick steel with removable front panel with concealed latches.

Retain first three subparagraphs below if units are not scheduled on Drawings.

1. Mounting:  [Wall with wall sleeve] [Floor with subbase].

2. Discharge Grille:  [Punched-louver discharge grille allowing four-way discharge-air pattern] [Extruded-aluminum discharge grille] [Reversible polycarbonate discharge grille allowing upward and horizontal airflow].

3. Louvers:  [Extruded aluminum with enamel finish] [Stamped aluminum with clear-anodized finish] [Stamped steel with enamel finish]; [white] [bronze] [brown] [beige] <Insert color> color.

4. Finish:  [Epoxy coating] [Baked enamel].

5. Access Door:  Hinged door in top of cabinet for access to controls.

6. Cabinet Extension:  Matching cabinet in construction and finish, allowing diversion of airflow to adjoining room; with grille.

Retain first subparagraph below to comply with LEED-NC Prerequisite EQ 1.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

7. Finish of Interior Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain first subparagraph below for floor-mounted units.

8. Subbase:  Enameled steel with adjustable leveling feet and adjustable end plates[, with factory-installed and -wired, fused disconnect switch and receptacle sized for unit].

9. Wall Sleeves:  [Galvanized steel with polyester finish] [Molded polymer] [Molded fiberglass-reinforced polyester].

B. Refrigeration System:  Direct-expansion indoor coil with capillary restrictor; and hermetically sealed scroll compressor with vibration isolation and overload protection.

1. Indoor and Outdoor Coils:  Seamless copper tubes mechanically expanded into aluminum fins[ with capillary tube distributor on indoor coil].

Retain first three subparagraphs below for heat-pump units.

2. Accumulator.

3. Constant-pressure expansion valve.

4. Reversing valve.

Retain one of two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  Retain second or third option in first subparagraph or retain second subparagraph to comply with LEED-NC Credit EA 4.

5. Charge:  [R-22] [R-407C] [R-410A].

6. Charge:  R-407C or R-410A.

C. Indoor Fan:  Forward curved, centrifugal; with motor and positive-pressure ventilation damper with [concealed manual] [electric] operator.

Filters in first paragraph below are optional feature.  Washable filters may not comply with requirements in ASHRAE 62.1-2004 for a minimum MERV 6, which would not fulfill LEED-NC Prerequisite EQ 1.  Verify filter efficiency with manufacturers.

D. Filters:  Washable polyurethane in molded plastic frame.

E. Condensate Drain:  Drain pan [to direct condensate to outdoor coil for re-evaporation] [and piping to direct condensate to building waste and vent piping].

In subparagraph below, verify drain pan construction and connection requirements with manufacturers if applying for LEED credits.  ASHRAE 62.1-2004 has specific requirements for drain pan construction and connections.

1. Comply with ASHRAE 62.1-2004 for drain pan construction and connections.

F. Outdoor Fan:  [Forward curved, centrifugal] [Propeller] [Forward curved, centrifugal or propeller] type [with separate] [driven by indoor fan] motor.

Default motor characteristics are specified in Division 15 Section "Common Motor Requirements for HVAC Equipment."

1. Indoor and Outdoor Fan Motors:  Two speed; comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 15 Section "Common Motor Requirements for HVAC Equipment."

a. Fan Motors:  Permanently lubricated split capacitor.

b. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

c. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 16 Sections.

2.4 HEATING

Retain one of three paragraphs below for heating and cooling units or for heat pumps with supplemental heat.

A. Electric-Resistance Heating Coil:  Nickel-chromium-wire, electric-resistance heating elements with contactor and high-temperature-limit switch.

B. Hot-Water Heating Coil:  Seamless copper tubes mechanically expanded into aluminum fins with two-way modulating control valve and air vent.

C. Gas Heat:

1. General Requirements for Gas-Fired, Noncondensing Furnaces:  Factory assembled, piped, wired, and tested; complying with ANSI Z21.86/CSA 2.32, "Vented Gas-Fired Space Heating Appliances," and with NFPA 54.

2. Type of Gas:  [Natural] [Propane].

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

3. Heat Exchanger:  [Aluminized] [Stainless] steel.

4. Burner:

In first subparagraph below, two-stage and modulating gas valves are optional features.

a. Gas Valve:  100 percent safety [two-stage] [modulating] main gas valve, main shutoff valve, pressure regulator, safety pilot with electronic flame sensor, limit control, transformer, and combination ignition/fan timer control board.

b. Ignition:  Electric pilot ignition with hot-surface igniter or electric spark ignition.

5. Gas-Burner Safety Controls:

a. Electronic Flame Sensor:  Prevents gas valve from opening until pilot flame is proven; stops gas flow on ignition failure.

b. Flame Rollout Switch:  Installed on burner box; prevents burner operation.

c. Limit Control:  Fixed stop at maximum permissible setting; de-energizes burner on excessive bonnet temperature; automatic reset.

6. Combustion-Air Inducer:  Centrifugal fan prepurges heat exchanger and vents combustion products; thermally protected motor with sleeve bearings; pressure switch prevents operation if combustion-air inlet or flue outlet is blocked.

7. Furnace Controls:  Solid-state board integrates ignition, heat, cooling, and fan speeds; adjustable fan-on and fan-off timing; and terminals for connection to accessories.

2.5 CONTROLS

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment," for ventilation system controls.  If applying for LEED credits, verify that manufacturers can provide units with controls that comply with requirements.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

A. Control Module:  Unit-mounted digital panel with touchpad temperature control and with touchpad for heating, cooling, and fan operation.  Include the following features:

1. Low Ambient Lockout Control:  Prevents cooling-cycle operation below 40 deg F (5 deg C) outdoor air temperature.

Retain first subparagraph below for heat-pump units.

2. Heat-Pump Ambient Control:  Field-adjustable switch changes to heat-pump heating operation above 40 deg F (5 deg C) and to supplemental heating below plus 25 deg F (minus 4 deg C).

Retain option in first subparagraph below for heating and cooling units and for heat pumps.

3. Temperature-Limit Control:  Prevents occupant from exceeding preset[ setback or] setup temperature.

4. Building Automation System Interface:  Allows remote on-off control with setback temperature control.

5. Reverse-Cycle Defrost:  Solid-state sensor monitors frost buildup on [indoor] [outdoor] coil and reverses unit to melt frost.

B. Remote Control:  Standard unit-mounted controls with remote-mounted, low-voltage adjustable thermostat with heat anticipator, [heat-off-cool-auto] [heat-off-cool] switch, and[ on-auto] fan switch.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

C. Outdoor Air:  [Manual] [Motorized] intake damper.[  Open intake when unit indoor air fan runs.]

2.6 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of packaged terminal air conditioners, delete this article and schedule packaged terminal air conditioners on Drawings.

A. Airflow:  <Insert cfm (L/s)>.

LEED-NC Prerequisite EQ 1 requires minimum ventilation rates according to ASHRAE 62.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

B. Outdoor Air-Intake Rate:  <Insert cfm (L/s)>.

C. Cooling Capacity:

1. Total:  <Insert Btu/h (kW)>.

2. Sensible:  <Insert Btu/h (kW)>.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

3. Energy-Efficiency Ratio:  <Insert number>.

4. Indoor Coil Entering-Air Dry Bulb Temperature:  <Insert deg F (deg C)>.

5. Indoor Coil Entering-Air Wet Bulb Temperature:  <Insert deg F (deg C)>.

6. Indoor Coil Leaving-Air Dry Bulb Temperature:  <Insert deg F (deg C)>.

7. Indoor Coil Leaving-Air Wet Bulb Temperature:  <Insert deg F (deg C)>.

8. Outdoor Coil Entering-Air Temperature:  <Insert deg F (deg C)>.

D. Heat-Pump Capacity:

1. Total:  <Insert Btu/h (kW)>.

2. Outdoor Temperature:  <Insert deg F (deg C)>.

E. Electric Heat Capacity:  <Insert Btu/h (kW)>.

F. Hydronic Heat Capacity:

1. Total:  <Insert Btu/h (kW)>.

2. Entering-Air Temperature:  <Insert deg F (deg C)>.

3. Leaving-Air Temperature:  <Insert deg F (deg C)>.

4. Water Flow:  <Insert gpm (L/s)>.

5. Entering-Water Temperature:  <Insert deg F (deg C)>.

6. Leaving-Water Temperature:  <Insert deg F (deg C)>.

G. Gas Heat Capacity:

1. Input:  <Insert Btu/h (kW)>.

2. Output:  <Insert Btu/h (kW)>.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

3. AFUE:  [80] <Insert number> percent.

H. Sound:

1. Indoor:  <Insert Bels>.

2. Outdoor:  <Insert Bels>.

I. Electrical Characteristics:

1. Volts:  <Insert value>.

2. Phase:  [Single] [Three].

3. Hertz:  60.

4. Full-Load Amperes:  <Insert value>.

5. Minimum Circuit Ampacity:  <Insert value>.

6. Maximum Overcurrent Protection:  <Insert amperage>.

2.7 SOURCE QUALITY CONTROL

A. Sound-Power Level Ratings:  Factory test to comply with ARI 300, "Sound Rating and Sound Transmission Loss of Packaged Terminal Equipment."

B. Unit Performance Ratings:  Factory test to comply with ARI 310/380/CSA C744, "Packaged Terminal Air-Conditioners and Heat Pumps."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install units level and plumb, maintaining manufacturer's recommended clearances and tolerances.

B. Install wall sleeves in finished wall assembly; seal and weatherproof.  Joint-sealant materials and applications are specified in Division 7 Section "Joint Sealants."

Retain paragraph below in seismic areas.  Equipment protection may be required for some types of buildings.  Verify requirements with model building codes and ASCE/SEI 7.

C. Install and anchor wall sleeves to withstand, without damage to equipment and structure, seismic forces required by building code.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain first paragraph below for units with hot-water supplemental heating.

A. Comply with requirements for piping specified in Division 15 Section "Hydronic Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first paragraph below for units with gas-fired supplemental heating.

B. Comply with requirements for piping specified in Division 15 Section "Facility Natural-Gas Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

C. Install piping adjacent to machine to allow service and maintenance.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Inspect for and remove shipping bolts, blocks, and tie-down straps.

2. After installing packaged terminal air conditioners and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

D. Packaged terminal air conditioners will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

3.4 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

B. After installation, verify the following:

1. Unit is level on base and is flashed in exterior wall.

2. Unit casing has no visible damage.

3. Compressor, air-cooled condenser coil, and fans have no visible damage.

4. Labels are clearly visible.

5. Controls are connected and operable.

6. Shipping bolts, blocks, and tie-down straps are removed.

7. Filters are installed and clean.

8. Drain pan and drain line are installed correctly.

9. Electrical wiring installation complies with manufacturer's submittal and installation requirements in Division 16 Sections.

10. Installation.  Perform startup checks according to manufacturer's written instructions, including the following:

a. Lubricate bearings on fan.

b. Check fan-wheel rotation for correct direction without vibration and binding.

C. After startup service and performance test, change filters.

3.5 ADJUSTING

A. Adjust initial temperature set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

3.6 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain packaged terminal air conditioners.

END OF SECTION 15731

PACKAGED TERMINAL AIR CONDITIONERS
15731 - 1

