Copyright 2004 AIA
MASTERSPEC Full Length
12/04 (R 06/06)

SCopyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15732 - PACKAGED, OUTDOOR, CENTRAL-STATION AIR-HANDLING UNITS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, outdoor, central-station air-handling units (rooftop units) with the following components and accessories:

1. Direct-expansion cooling.

2. Heat-pump refrigeration components.

3. Hot-gas reheat.

4. Electric-heating coils.

5. Gas furnace.

6. Economizer outdoor- and return-air damper section.

7. Integral, space temperature controls.

8. Roof curbs.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Direct-Fired H&V Units" for outdoor units providing 100 percent tempered outdoor air without heat exchangers.

2. Division 15 Section "Indirect-Fired H&V Units" for outdoor units providing 100 percent tempered outdoor air with heat exchangers.

3. Division 15 Section "Rooftop Replacement-Air Units" for outdoor equipment air conditioning 100 percent outdoor air to replace air exhausted from a building.

1.3 DEFINITIONS

Retain abbreviations and terms that remain after this Section has been edited.

A. DDC:  Direct-digital controls.

B. ECM:  Electrically commutated motor.

C. Outdoor-Air Refrigerant Coil:  Refrigerant coil in the outdoor-air stream to reject heat during cooling operations and to absorb heat during heating operations.  "Outdoor air" is defined as the air outside the building or taken from outdoors and not previously circulated through the system.

D. Outdoor-Air Refrigerant-Coil Fan:  The outdoor-air refrigerant-coil fan in RTUs.  "Outdoor air" is defined as the air outside the building or taken from outdoors and not previously circulated through the system.

E. RTU:  Rooftop unit.  As used in this Section, this abbreviation means packaged, outdoor, central-station air-handling units.  This abbreviation is used regardless of whether the unit is mounted on the roof or on a concrete base on ground.

F. Supply-Air Fan:  The fan providing supply air to conditioned space.  "Supply air" is defined as the air entering a space from air-conditioning, heating, or ventilating apparatus.

G. Supply-Air Refrigerant Coil:  Refrigerant coil in the supply-air stream to absorb heat (provide cooling) during cooling operations and to reject heat (provide heating) during heating operations.  "Supply air" is defined as the air entering a space from air-conditioning, heating, or ventilating apparatus.

H. VVT:  Variable-air volume and temperature.

1.4 PERFORMANCE REQUIREMENTS

Retain paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design RTU supports to comply with [wind] [and] [seismic] performance requirements, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain paragraph below with "Delegated-Design Submittal" Paragraph in "Submittals" Article for projects requiring wind-restraint design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

B. Wind-Restraint Performance:

Obtain values for items in subparagraphs below from Project structural engineer or from SEI/ASCE 7.

1. Basic Wind Speed:  <Insert value>.

2. Building Classification Category:  [I] [II] [III] [IV].

3. Minimum 10 lb/sq. ft (48.8 kg/sq. m) multiplied by the maximum area of the mechanical component projected on a vertical plane that is normal to the wind direction, and 45 degrees either side of normal.

Retain paragraph and subparagraph below with "Delegated-Design Submittal" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  RTUs shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

1.5 SUBMITTALS

A. Product Data:  Include manufacturer's technical data for each RTU, including rated capacities, dimensions, required clearances, characteristics, furnished specialties, and accessories.

B. LEED Submittals:

Retain first subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

Paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

D. Delegated-Design Submittal:  For RTU supports indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

2. Detail mounting, securing, and flashing of roof curb to roof structure.  Indicate coordinating requirements with roof membrane system.

3. [Wind-] [and] [Seismic-]Restraint Details:  Detail fabrication and attachment of wind and seismic restraints and snubbers.  Show anchorage details and indicate quantity, diameter, and depth of penetration of anchors.

Retain paragraph and subparagraphs below if required by wind design criteria applicable to Project.

E. Manufacturer Wind Loading Qualification Certification:  Submit certification that specified equipment will withstand wind forces identified in "Performance Requirements" Article and in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculations.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of wind force and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

F. Manufacturer Seismic Qualification Certification:  Submit certification that RTUs, accessories, and components will withstand seismic forces defined in "Performance Requirements" Article and in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

G. Coordination Drawings:  Plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Structural members to which RTUs will be attached.

2. Roof openings

3. Roof curbs and flashing.

H. Field quality-control test reports.

I. Operation and Maintenance Data:  For RTUs to include in emergency, operation, and maintenance manuals.

J. Warranty:  Special warranty specified in this Section.

1.6 QUALITY ASSURANCE

A. ARI Compliance:

1. Comply with ARI 210/240 and ARI 340/360 for testing and rating energy efficiencies for RTUs.

2. Comply with ARI 270 for testing and rating sound performance for RTUs.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  LEED-NC Credit EA 1 requires efficiency in excess of minimum efficiency required by ASHRAE/IESNA 90.1-2004.

B. ASHRAE Compliance:

1. Comply with ASHRAE 15 for refrigeration system safety.

2. Comply with ASHRAE 33 for methods of testing cooling and heating coils.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

3. Comply with applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

D. NFPA Compliance:  Comply with NFPA 90A and NFPA 90B.

If retaining first paragraph below, delete compliance with ASHRAE 15 in subparagraph above and compliance with NFPA 90A or NFPA 90B in paragraph above.  Some manufacturers test and label their equipment according to UL 1995, which requires compliance with ASHRAE 15, NFPA 90A, and NFPA 90B.

E. UL Compliance:  Comply with UL 1995.

F. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to replace components of RTUs that fail in materials or workmanship within specified warranty period.

Verify available warranties for RTUs and components and insert number in subparagraphs below.  Periods indicated are included with manufacturer's published data and vary among manufacturers and unit sizes.

1. Warranty Period for Compressors:  Manufacturer's standard, but not less than [five] [10] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Gas Furnace Heat Exchangers:  Manufacturer's standard, but not less than [five] [10] [15] [20] <Insert number> years from date of Substantial Completion.

3. Warranty Period for Solid-State Ignition Modules:  Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

4. Warranty Period for Control Boards:  Manufacturer's standard, but not less than [three] <Insert number> years from date of Substantial Completion.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Fan Belts:  [One set] [<Insert number> sets] for each belt-driven fan.

2. Filters:  [One set] [<Insert number> sets] of filters for each unit.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AAON, Inc.

2. Addison Products Company.

3. Carrier Corporation.

4. Engineered Air.

5. Lennox Industries Inc.

6. McQuay International.

7. Trane; American Standard Companies, Inc.

8. YORK International Corporation.

9. <Insert manufacturer's name>.

2.2 CASING

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.14 - "Access for Inspection, Cleaning, and Maintenance," sets requirements for equipment access.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.

A. General Fabrication Requirements for Casings:  Formed and reinforced double-wall insulated panels, fabricated to allow removal for access to internal parts and components, with joints between sections sealed.

B. Exterior Casing Material:  Galvanized steel with factory-painted finish, with pitched roof panels and knockouts with grommet seals for electrical and piping connections and lifting lugs.

If Project has more than one RTU and the configurations, materials, and thicknesses for each are different, delete subparagraph below and schedule casing materials and thicknesses on Drawings.  See sample schedule in the Evaluations.

1. Exterior Casing Thickness:  [0.052 inch (1.3 mm)] [0.0626 inch (1.6 mm)] [0.079 inch (2.0 mm)] <Insert thickness> thick.

C. Inner Casing Fabrication Requirements:

1. Inside Casing:  Galvanized steel, [0.034 inch (0.86 mm)] [0.028 inch (0.7 mm)] <Insert thickness> thick[, perforated 40 percent free area].

D. Casing Insulation and Adhesive:  Comply with NFPA 90A or NFPA 90B.

1. Materials:  ASTM C 1071, Type I.

2. Thickness:  [1/2 inch (13 mm)] [1 inch (25 mm)].

3. Liner materials shall have air-stream surface coated with an erosion- and temperature-resistant coating or faced with a plain or coated fibrous mat or fabric.

4. Liner Adhesive:  Comply with ASTM C 916, Type I.

Retain third option in first paragraph below to comply with LEED-NC Prerequisite EQ 1.

E. Condensate Drain Pans:  Formed sections of [galvanized] [stainless]-steel sheet, a minimum of 2 inches (50 mm) deep[, and complying with ASHRAE 62.1-2004].

1. Double-Wall Construction:  Fill space between walls with foam insulation and seal moisture tight.

2. Drain Connections:  Threaded nipple[ both sides of drain pan].

Retain subparagraph below for galvanized-steel drain pans and delete for stainless-steel drain pans.

3. Pan-Top Surface Coating:  Corrosion-resistant compound.

Retain paragraph below to comply with LEED-NC Prerequisite EQ 1.

F. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

2.3 FANS

Retain one of first two paragraphs below.  Retain both if multiple-type RTUs are required.  If retaining both, indicate fan type in a schedule.

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 6.5.3 - "Air System Design and Control," sets requirements for fans and fan controls.  If applying for LEED certification, comply with requirements in ASHRAE/IESNA 90.1-2004.

A. Direct-Driven Supply-Air Fans:  Double width, [forward curved] [backward inclined], centrifugal; with permanently lubricated, [multispeed] [ECM] motor resiliently mounted in the fan inlet.  Aluminum or painted-steel wheels, and galvanized- or painted-steel fan scrolls.

B. Belt-Driven Supply-Air Fans:  Double width, forward curved, centrifugal; with permanently lubricated, single-speed motor installed on an adjustable fan base resiliently mounted in the casing.  Aluminum or painted-steel wheels, and galvanized- or painted-steel fan scrolls.

C. Condenser-Coil Fan:  Propeller, mounted on shaft of permanently lubricated motor.

D. Relief-Air Fan:  [Propeller] [Forward curved] [Backward inclined], shaft mounted on permanently lubricated motor.

E. Seismic Fabrication Requirements:  Fabricate fan section, internal mounting frame and attachment to fans, fan housings, motors, casings, accessories, and other fan section components with reinforcement strong enough to withstand seismic forces defined in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when fan-mounted frame and RTU-mounted frame are anchored to building structure.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs to paragraph below to suit Project.

F. Fan Motor:  Comply with requirements in Division 15 Section "Motors."

2.4 COILS

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.12 - "Finned-Tube Coils and Heat Exchangers," sets requirements for coils.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.

A. Supply-Air Refrigerant Coil:

1. [Aluminum] [Copper]-plate fin and seamless[ internally grooved] copper tube in steel casing with equalizing-type vertical distributor.

Retain first subparagraph below for copper-plate fin coils.

2. Polymer strip shall prevent all copper coil from contacting steel coil frame or condensate pan.

3. Coil Split:  Interlaced.

Retain first subparagraph below if desired for aluminum-plate fin/copper tube coils; delete if scheduled.

4. [Baked phenolic] [Cathodic epoxy] coating.

Retain third option in subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Condensate Drain Pan:  [Galvanized steel with corrosion-resistant coating] [Stainless steel] formed with pitch and drain connections[ complying with ASHRAE 62.1-2004].

B. Outdoor-Air Refrigerant Coil:

1. [Aluminum] [Copper]-plate fin and seamless[ internally grooved] copper tube in steel casing with equalizing-type vertical distributor.

Retain subparagraph below for copper-plate fin coils.

2. Polymer strip shall prevent all copper coil from contacting steel coil frame or condensate pan.

Retain subparagraph below if desired for aluminum-plate fin/copper tube coils; delete if scheduled.

3. [Baked phenolic] [Cathodic epoxy] coating.

C. Hot-Gas Reheat Refrigerant Coil:

1. [Aluminum] [Copper]-plate fin and seamless[ internally grooved] copper tube in steel casing with equalizing-type vertical distributor.

Retain subparagraph below for copper-plate fin coils.

2. Polymer strip shall prevent all copper coil from contacting steel coil frame or condensate pan.

Retain subparagraph below if desired for aluminum-plate fin/copper tube coils; delete if scheduled.

3. [Baked phenolic] [Cathodic epoxy] coating.

D. Electric-Resistance Heating:

1. Open Heating Elements:  Resistance wire of 80 percent nickel and 20 percent chromium, supported and insulated by floating ceramic bushings recessed into casing openings, fastened to supporting brackets, and mounted in galvanized-steel frame.  Terminate elements in stainless-steel machine-staked terminals secured with stainless-steel hardware.

2. Overtemperature Protection:  Disk-type, automatically reset, thermal-cutout, safety device; serviceable through terminal box.

3. Overcurrent Protection:  Manual-reset thermal cutouts, factory wired in each heater stage.

4. Control Panel:  Unit mounted with disconnecting means and overcurrent protection.  Include the following controls:

a. [Magnetic] [Mercury] contactors.

Retain one or both of first two subparagraphs below.  If retaining both, identify devices to specific units in a schedule.

b. Step Controller:  Pilot lights and override toggle switch for each step.

c. SCR Controller:  Pilot lights operate on load ratio, a minimum of five steps.

d. Time-delay relay.

e. Airflow proving switch.

2.5 REFRIGERANT CIRCUIT COMPONENTS

Retain paragraph below if Project includes only one RTU.  If Project requires multiple RTUs, delete paragraph and indicate number of circuits for each RTU in a schedule.

A. Number of Refrigerant Circuits:  [One] [Two] <Insert number>.

Verify availability of crankcase heater in first paragraph below with manufacturer.

B. Compressor:  [Hermetic, reciprocating] [Semihermetic, reciprocating] [Hermetic, scroll], mounted on vibration isolators; with internal overcurrent and high-temperature protection, internal pressure relief[, and crankcase heater].

C. Refrigeration Specialties:

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

1. Refrigerant:  [R-22] [R-407C] [R-410A] <Insert type>.

2. Refrigerant:  R-407C or R-410A.

3. Expansion valve with replaceable thermostatic element.

4. Refrigerant filter/dryer.

5. Manual-reset high-pressure safety switch.

6. Automatic-reset low-pressure safety switch.

7. Minimum off-time relay.

8. Automatic-reset compressor motor thermal overload.

9. Brass service valves installed in compressor suction and liquid lines.

Four subparagraphs below are optional features.  Verify availability with manufacturers.

10. Low-ambient kit high-pressure sensor.

11. Hot-gas reheat solenoid valve with a replaceable magnetic coil.

12. Hot-gas bypass solenoid valve with a replaceable magnetic coil.

13. Four-way reversing valve with a replaceable magnetic coil, thermostatic expansion valves with bypass check valves, and a suction line accumulator.

2.6 AIR FILTRATION

Verify available filter types with manufacturer.  Indicate filter thickness in "Capacities and Characteristics" Article or in a schedule.

A. Minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or both subparagraphs below.  If retaining both, indicate filter type in "Capacities and Characteristics" Article or in a schedule.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

1. Glass Fiber:  Minimum [80] <Insert percent> percent arrestance, and MERV [5] <Insert value>.

2. Pleated:  Minimum [90] <Insert percent> percent arrestance, and MERV [7] <Insert value>.

2.7 GAS FURNACE

A. Description:  Factory assembled, piped, and wired; complying with ANSI Z21.47 and NFPA 54.

1. CSA Approval:  Designed and certified by and bearing label of CSA.

B. Burners:  Stainless steel.

1. Fuel:  [Natural] [Propane] gas.

2. Ignition:  Electronically controlled electric spark or hot-surface igniter with flame sensor.

Verify availability of high-altitude feature with manufacturers.

3. High-Altitude [Model] [Kit]:  For Project elevations more than 2000 feet (610 m) above sea level.

C. Heat-Exchanger and Drain Pan:  Stainless steel.

Retain one of first two paragraphs below.

D. Venting:  Gravity vented[ with vertical extension].

E. Power Vent:  Integral, motorized centrifugal fan interlocked with gas valve[ with vertical extension].

F. Safety Controls:

1. Gas Control Valve:  [Single stage] [Two stage] [Modulating].

2. Gas Train:  Single-body, regulated, redundant, 24-V ac gas valve assembly containing pilot solenoid valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff.

2.8 DAMPERS

If only a single RTU is required for Project, retain one of two paragraphs and associated subparagraphs below.  If Project includes multiple RTUs, retain both paragraphs and indicate which unit gets each component in a schedule.  First paragraph is for limited outdoor air; second is for units with economizer controls.  ASHRAE/IESNA 90.1-2004 sets requirements for dampers.  If applying for LEED certification, retain second option in first paragraph below to comply with requirements in ASHRAE/IESNA 90.1-2004.

A. Outdoor-Air Damper:  Linked damper blades, for 0 to 25 percent outdoor air, with [manual] [motorized] damper filter.

B. Outdoor- and Return-Air Mixing Dampers:  Parallel- or opposed-blade galvanized-steel dampers mechanically fastened to cadmium plated for galvanized-steel operating rod in reinforced cabinet.  Connect operating rods with common linkage and interconnect linkages so dampers operate simultaneously.

1. Damper Motor:  Modulating with adjustable minimum position.

2. Relief-Air Damper:  Gravity actuated or motorized, as required by ASHRAE/IESNA 90.1-2004, with bird screen and hood.

2.9 ELECTRICAL POWER CONNECTION

Retain this Article to require RTU manufacturer to provide a single-point disconnecting means.  Delete this Article if disconnecting means is specified in Division 16 Sections and indicated on Electrical Drawings.  Unit-mounted disconnect in option below can be equipped to provide constant power to duplex, 115-V receptacles described in "Accessories" Article.  Field-mounted disconnects specified in Division 16 and shown on Electrical Drawings will disconnect power to these outlets unless they are powered from another source.

A. Provide for single connection of power to unit with[ unit-mounted disconnect switch accessible from outside unit and] control-circuit transformer with built-in overcurrent protection.

2.10 CONTROLS

Retain first paragraph below to specify temperature controls in Division 15 Sections "HVAC Instrumentation and Controls" and "Sequence of Operation." Delete first paragraph and retain second paragraph and subparagraphs to require controls integral to the RTU to be provided by RTU manufacturer.

A. Control equipment and sequence of operation are specified in Division 15 Section "HVAC Instrumentation and Controls."

Controls in first paragraph and subparagraphs below contain standard features available on most RTUs.  Include those required for Project.  Verify control features with manufacturer.

B. Basic Unit Controls:

1. Control-voltage transformer.

2. Wall-mounted thermostat or sensor with the following features:

a. Heat-cool-off switch.

b. Fan on-auto switch.

c. Fan-speed switch.

d. [Manual] [Automatic] changeover.

e. Adjustable deadband.

f. [Concealed] [Exposed] set point.

g. [Concealed] [Exposed] indication.

h. [Degree F] [Degree C] indication.

i. Unoccupied-period-override push button.

j. Data entry and access port to input temperature[ and humidity] set points, occupied and unoccupied periods, and output room temperature[ and humidity], supply-air temperature, operating mode, and status.

Retain first subparagraph and associated subparagraphs below for hot-gas reheat feature.

3. Wall-mounted humidistat or sensor with the following features:

a. [Concealed] [Exposed] set point.

b. [Concealed] [Exposed] indication.

4. [Remote Wall] [Unit]-Mounted Annunciator Panel for Each Unit:

a. Lights to indicate power on, cooling, heating, fan running, filter dirty, and unit alarm or failure.

b. DDC controller or programmable timer and interface with HVAC instrumentation and control system.

c. Digital display of outdoor-air temperature, supply-air temperature, return-air temperature, economizer damper position, indoor-air quality, and control parameters.

C. [Electronic] [DDC] Controller:

1. Controller shall have volatile-memory backup.

2. Safety Control Operation:

a. Smoke Detectors:  Stop fan and close outdoor-air damper if smoke is detected.  Provide additional contacts for alarm interface to fire alarm control panel.

b. Firestats:  Stop fan and close outdoor-air damper if air greater than [130 deg F (54 deg C)] <Insert temperature> enters unit.  Provide additional contacts for alarm interface to fire alarm control panel.

c. Fire Alarm Control Panel Interface:  Provide control interface to coordinate with operating sequence described in Division 13 Section "Fire Alarm."

Retain subparagraph below for low-ambient feature.

d. Low-Discharge Temperature:  Stop fan and close outdoor-air damper if supply air temperature is less than [40 deg F (4 deg C)] <Insert temperature>.

Retain first subparagraph below for air-to-air heat-pump feature.

e. Defrost Control for Condenser Coil:  Pressure differential switch to initiate defrost sequence.

3. Scheduled Operation:  Occupied and unoccupied periods on [seven] [365]-day clock with a minimum of [two] [four] programmable periods per day.

4. Unoccupied Period:

a. Heating Setback:  [10 deg F (5.6 deg C)] <Insert temperature>.

b. Cooling Setback:  System off.

c. Override Operation:  [Two] <Insert number> hours.

5. Supply Fan Operation:

a. Occupied Periods:  Run fan continuously.

b. Unoccupied Periods:  Cycle fan to maintain setback temperature.

6. Refrigerant Circuit Operation:

a. Occupied Periods:  Cycle or stage compressors[, and operate hot-gas bypass] to match compressor output to cooling load to maintain [room] [discharge] temperature[ and humidity].  Cycle condenser fans to maintain maximum hot-gas pressure.  Operate low-ambient control kit to maintain minimum hot-gas pressure.

Refrigerant coil may be cooling or heating with air-to-air heat pump.  Retain second option in first subparagraph below for air-to-air heat pumps.

b. Unoccupied Periods:  [Compressors off] [Cycle compressors and condenser fans for heating to maintain setback temperature].

c. Switch reversing valve for heating or cooling mode on air-to-air heat pump.

7. Hot-Gas Reheat-Coil Operation:

a. Occupied Periods:  Humidistat opens hot-gas valve to provide hot-gas reheat, and cycles compressor.

b. Unoccupied Periods:  Reheat not required.

8. Gas Furnace Operation:

a. Occupied Periods:  [Cycle] [Stage] [Modulate] burner to maintain [room] [discharge] temperature.

b. Unoccupied Periods:  Cycle burner to maintain setback temperature.

9. Electric-Heating-Coil Operation:

a. Occupied Periods:  [Cycle] [Stage] [Modulate] coil to maintain [room] [discharge] temperature.

b. Unoccupied Periods:  Energize coil to maintain setback temperature.

Retain subparagraph below for air-to-air heat pump.

c. Operate supplemental electric heating coil with compressor for heating with outdoor temperature below [25 deg F (minus 4 deg C)] <Insert temperature>.

Retain subparagraph and associated subparagraphs below for fixed outdoor-air intake.

10. Fixed Minimum Outdoor-Air Damper Operation:

a. Occupied Periods:  Open to [25] <Insert percent> percent.

b. Unoccupied Periods:  Close the outdoor-air damper.

Retain subparagraph and associated subparagraphs below for economizer cycle.

11. Economizer Outdoor-Air Damper Operation:

a. Occupied Periods:  Open to [10] [25] <Insert percent> percent fixed minimum intake, and maximum 100 percent of the fan capacity to comply with ASHRAE Cycle II.  Controller shall permit air-side economizer operation when outdoor air is less than [60 deg F (15 deg C)] <Insert temperature>.  Use [outdoor-air temperature] [mixed-air and outdoor-air temperature] [outdoor-air enthalpy] [mixed-air temperature and select between outdoor-air and return-air enthalpy] to adjust mixing dampers.[  Start relief-air fan with end switch on outdoor-air damper.] During economizer cycle operation, lock out cooling.

b. Unoccupied Periods:  Close outdoor-air damper and open return-air damper.

Retain first subparagraph below if monitoring outdoor-air intake rate to comply with LEED-NC Credit EA 5.

c. Outdoor-Airflow Monitor:  Accuracy maximum plus or minus 5 percent within 15 and 100 percent of total outdoor air.  Monitor microprocessor shall adjust for temperature, and output shall range from [2- to 10-V dc] [4 to 20 mA] <Insert value>.

12. Carbon Dioxide Sensor Operation:

a. Occupied Periods:  Reset minimum outdoor-air ratio down to minimum [10] <Insert percent> percent to maintain maximum [1000-ppm] <Insert concentration> concentration.

b. Unoccupied Periods:  Close outdoor-air damper and open return-air damper.

13. VVT Relays:

a. Provide heating- and cooling-mode changeover relays compatible with VVT terminal control system required in Division 15 Sections "Air Terminal Units" and "HVAC Instrumentation and Controls."

D. Interface Requirements for HVAC Instrumentation and Control System:

1. Interface relay for scheduled operation.

2. Interface relay to provide indication of fault at the central workstation and diagnostic code storage.

3. Provide [BACnet] [or] [LonWorks] compatible interface for central HVAC control workstation for the following:

a. Adjusting set points.

b. Monitoring supply fan start, stop, and operation.

c. Inquiring data to include[ outdoor-air damper position,] supply- and room-air temperature[ and humidity].

d. Monitoring occupied and unoccupied operations.

Retain subparagraphs below to comply with requirements for LEED-NC Credit EA 5.  Verify availability of control feature with manufacturers.

e. Monitoring constant and variable motor loads.

f. Monitoring variable-frequency drive operation.

g. Monitoring cooling load.

h. Monitoring economizer cycles.

i. Monitoring air-distribution static pressure and ventilation air volume.

2.11 ACCESSORIES

A. Electric heater with integral thermostat maintains minimum 50 deg F (10 deg C) temperature in gas burner compartment.

B. Duplex, 115-V, ground-fault-interrupter outlet with 15-A overcurrent protection.  Include transformer if required.[  Outlet shall be energized even if the unit main disconnect is open.]

C. Low-ambient kit using [staged] [damper on] [variable-speed] condenser fans for operation down to [35 deg F (1.7 deg C)] <Insert temperature>.

D. Filter differential pressure switch with sensor tubing on either side of filter.  Set for final filter pressure loss.

Retain one or both of first two paragraphs below; if retaining both, identify guard requirements for each RTU in a schedule.

E. Coil guards of painted, galvanized-steel wire.

F. Hail guards of galvanized steel, painted to match casing.

G. Concentric diffuser with white louvers and polished aluminum return grilles, insulated diffuser box with mounting flanges, and interior transition.

2.12 ROOF CURBS

Retain one of first two paragraphs and associated subparagraphs below.  Retain first for curbs with vibration isolation and seismic or wind restraints; retain second for curbs provided by RTU manufacturer without vibration isolation and seismic or wind restraints.

A. Roof curbs with vibration isolators and wind or seismic restraints are specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

B. Materials:  Galvanized steel with corrosion-protection coating, watertight gaskets, and factory-installed wood nailer; complying with NRCA standards.

1. Curb Insulation and Adhesive:  Comply with NFPA 90A or NFPA 90B.

a. Materials:  ASTM C 1071, Type I or II.

b. Thickness:  [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert thickness>.

2. Application:  Factory applied with adhesive and mechanical fasteners to the internal surface of curb.

a. Liner Adhesive:  Comply with ASTM C 916, Type I.

b. Mechanical Fasteners:  Galvanized steel, suitable for adhesive attachment, mechanical attachment, or welding attachment to duct without damaging liner when applied as recommended by manufacturer and without causing leakage in cabinet.

c. Liner materials applied in this location shall have air-stream surface coated with a temperature-resistant coating or faced with a plain or coated fibrous mat or fabric depending on service air velocity.

d. Liner Adhesive:  Comply with ASTM C 916, Type I.

C. Curb Height:  [14 inches (355 mm)] [24 inches (610 mm)] [36 inches (910 mm)] <Insert height>.

D. Wind and Seismic Restraints:  Metal brackets compatible with the curb and casing, painted to match RTU, used to anchor unit to the curb, and designed for loads at Project site.  Comply with requirements in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for wind-load requirements.

2.13 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of RTU, delete this Article and schedule RTUs on Drawings.

A. Supply-Air Fan:

1. Airflow:  <Insert cfm (L/s)>.

2. External Static Pressure:  <Insert inches wg (kPa)>.

3. Fan Speed:  <Insert rpm>.

4. Motor Horsepower:  <Insert value>.

5. Motor Speed:  <Insert rpm>.

B. Relief-Air Fan:

1. Airflow:  <Insert cfm (L/s)>.

2. External Static Pressure:  <Insert inches wg (kPa)>.

3. Fan Speed:  <Insert rpm>.

4. Motor Horsepower:  <Insert value>.

5. Motor Speed:  <Insert rpm>.

C. Outdoor-Air-Intake Relief-Air Fan:

1. Airflow:  <Insert cfm (L/s)>.

2. Static Pressure:  <Insert inches wg (kPa)>.

3. Fan Speed:  <Insert rpm>.

4. Motor Horsepower:  <Insert value>.

5. Motor Speed:  <Insert rpm>.

D. Supply-Air Refrigerant Coil:

1. Total Cooling Capacity:  <Insert Btu/h (kW)>.

2. Sensible Cooling Capacity:  <Insert Btu/h (kW)>.

3. Entering-Air Dry-Bulb Temperature:  <Insert deg F (deg C)>.

4. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

5. Coating:  [Baked phenolic] [Cathodic epoxy].

E. Outdoor-Air Refrigerant Coil:

1. Ambient-Air Temperature:  <Insert deg F (deg C)>.

2. Coating:  [Baked phenolic] [Cathodic epoxy].

3. Fan Motor:  <Insert value>.

4. Number of Fans:  <Insert number>.

F. Hot-Gas Reheat Coil:

1. Heating Capacity:  <Insert Btu/h (kW)>.

2. Entering-Air Temperature:  <Insert deg F (deg C)>.

3. Air-Temperature Rise:  <Insert deg F (deg C)>.

4. Coating:  [Baked phenolic] [Cathodic epoxy].

G. Electric-Resistance Heating Coil:

1. Capacity:  <Insert kilowatts>.

2. Number of Steps:  <Insert number>.

H. Compressors:

1. Suction Temperature:  <Insert deg F (deg C)>.

2. Power Input:  <Insert kilowatts>.

Retain one of three subparagraphs below.  If applying for LEED certification, efficiency shall be at least equal to ASHRAE/IESNA 90.1-2004.

3. Energy-Efficiency Ratio (EER):  <Insert value>.

4. Seasonal Energy-Efficiency Ratio (SEER):  <Insert value>.

5. Coefficient of Performance (COP):  <Insert value>.

I. Gas Furnace:

1. Airflow:  <Insert cfm (L/s)>.

Retain one of first three subparagraphs below.  LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

2. Minimum AFUE:  <Insert value> percent.

3. Minimum Thermal Efficiency:  <Insert value> percent.

4. Minimum Combustion Efficiency:  <Insert value> percent.

5. Input:  <Insert Btu/h (kW)>.

6. Output:  <Insert Btu/h (kW)>.

7. Entering-Air Temperature:  <Insert deg F (deg C)>.

8. Air-Temperature Rise:  <Insert deg F (deg C)>.

J. Recirculating-Air Filters:

1. Minimum Face Area:  <Insert sq. ft. (sq. m)>.

2. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)] <Insert thickness>.

3. Initial Resistance:  <Insert inches wg (kPa)>.

4. Final Resistance:  <Insert inches wg (kPa)>.

K. Outdoor-Air Filters:

1. Minimum Face Area:  <Insert sq. ft. (sq. m)>.

2. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)] <Insert thickness>.

3. Initial Resistance:  <Insert inches wg (kPa)>.

4. Final Resistance:  <Insert inches wg (kPa)>.

L. Electrical Characteristics for Single-Point Connection:

1. Voltage:  <Insert value>.

2. Phase:  <Insert value>.

3. Hertz:  <Insert value>.

4. Full-Load Amperes:  <Insert value>.

5. Minimum Circuit Ampacity:  <Insert value>.

6. Maximum Overcurrent Protection:  <Insert amperage>.

M. Sound Power:  Radiated from condenser casing.

1. 1st Octave:  <Insert value> dB.

2. 2nd Octave:  <Insert value> dB.

3. 3rd Octave:  <Insert value> dB.

4. 4th Octave:  <Insert value> dB.

5. 5th Octave:  <Insert value> dB.

6. 6th Octave:  <Insert value> dB.

7. 7th Octave:  <Insert value> dB.

8. 8th Octave:  <Insert value> dB.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of RTUs.

B. Examine roughing-in for RTUs to verify actual locations of piping and duct connections before equipment installation.

C. Examine roofs for suitable conditions where RTUs will be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain paragraph and subparagraphs below for units mounted on a concrete equipment base on-grade.  Coordinate concrete work in this Article with Division 3 Section "Cast-in-Place Concrete" or "Cast-in-Place Concrete (Limited Applications)."

A. Concrete Bases:  Anchor equipment to concrete base according to equipment manufacturer's written instructions and according to seismic codes at Project.

1. Construct concrete bases of dimensions indicated, but not less than 4 inches (100 mm) larger than supported equipment and minimum 6 inches (150 mm) above finished ground elevation.

2. Place and secure anchorage devices.  Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

3. Install anchor bolts to elevations required for proper attachment to supported equipment.

4. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

5. Use [3000-psi (20.7-MPa)] <Insert value>, 28-day compressive-strength concrete and reinforcement as specified in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

Retain one of two paragraphs and associated subparagraph below.  Coordinate with Drawings and Sections specifying vibration and seismic controls.  Retain or insert amount of required deflection.

Retain paragraph and subparagraph below for equipment supported on a concrete equipment base on-grade.

B. Equipment Mounting:  Install RTUs on concrete base using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements for concrete base specified in Division 3 Section "[Cast-in-Place Concrete] [Cast-in-Place Concrete (Limited Applications)]."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1 inch (25 mm)] <Insert dimension>.

Retain paragraph below if curbs are provided by RTU manufacturer.

C. Roof Curb:  Install on roof structure or concrete base, level and secure, according to [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] [ARI Guideline B.] Install RTUs on curbs and coordinate roof penetrations and flashing with roof construction specified in Division 7 Section "Roof Accessories." Secure RTUs to upper curb rail, and secure curb base to roof framing or concrete base with anchor bolts.

Retain paragraph below if unit is installed on field-fabricated curbs or pilings.

D. Unit Support:  Install unit level on structural [curbs] [pilings].  Coordinate wall penetrations and flashing with wall construction.  Secure RTUs to structural support with anchor bolts.

Retain paragraph below for RTUs requiring wind or seismic restraints.

E. Install wind and seismic restraints according to manufacturer's written instructions.[  Wind and seismically restrained vibration isolation roof-curb rails are specified in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."]

3.3 CONNECTIONS

Coordinate piping and duct installations and specialty arrangements with schematics on Drawings and with requirements specified in piping and duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Verify condensate drainage requirements of authorities having jurisdiction.

A. Install condensate drain, minimum connection size, with trap and indirect connection to nearest roof drain or area drain.

B. Install piping adjacent to RTUs to allow service and maintenance.

Retain subparagraph below for RTUs with gas-fired heating.

1. Gas Piping:  Comply with applicable requirements in Division 15 Section "Fuel Gas Piping." Connect gas piping to burner, full size of gas train inlet, and connect with union and shutoff valve with sufficient clearance for burner removal and service.

C. Duct installation requirements are specified in other Division 15 Sections.  Drawings indicate the general arrangement of ducts.  The following are specific connection requirements:

1. Install ducts to termination at top of roof curb.

2. Remove roof decking only as required for passage of ducts.  Do not cut out decking under entire roof curb.

3. Connect supply ducts to RTUs with flexible duct connectors specified in Division 15 Section "Duct Accessories."

4. Install return-air duct continuously through roof structure.

See Evaluations for discussion of concrete inside curbs.

5. Install normal-weight, 3000-psi (20.7-MPa), compressive strength (28-day) concrete mix inside roof curb, [4 inches (100 mm)] <Insert thickness> thick.  Concrete, formwork, and reinforcement are specified in Division 3.

3.4 FIELD QUALITY CONTROL

Retain one of two paragraphs and associated subparagraph below to identify who shall perform tests and inspections.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.  Report results in writing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. After installing RTUs and after electrical circuitry has been energized, test units for compliance with requirements.

2. Inspect for and remove shipping bolts, blocks, and tie-down straps.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

D. Remove and replace malfunctioning units and retest as specified above.

3.5 STARTUP SERVICE

Retain first paragraph below to require a factory-authorized service representative to perform startup service.

A. Engage a factory-authorized service representative to perform startup service.

B. Complete installation and startup checks according to manufacturer's written instructions and do the following:

1. Inspect for visible damage to unit casing.

2. Inspect for visible damage to furnace combustion chamber.

3. Inspect for visible damage to compressor, coils, and fans.

4. Inspect internal insulation.

5. Verify that labels are clearly visible.

6. Verify that clearances have been provided for servicing.

7. Verify that controls are connected and operable.

8. Verify that filters are installed.

9. Clean condenser coil and inspect for construction debris.

Retain first two subparagraphs below for gas-fired RTUs.

10. Clean furnace flue and inspect for construction debris.

11. Connect and purge gas line.

12. Remove packing from vibration isolators.

Retain first subparagraph below for barometric relief dampers.

13. Inspect operation of barometric relief dampers.

14. Verify lubrication on fan and motor bearings.

15. Inspect fan-wheel rotation for movement in correct direction without vibration and binding.

16. Adjust fan belts to proper alignment and tension.

17. Start unit according to manufacturer's written instructions.

a. Start refrigeration system.

b. Do not operate below recommended low-ambient temperature.

c. Complete startup sheets and attach copy with Contractor's startup report.

18. Inspect and record performance of interlocks and protective devices; verify sequences.

19. Operate unit for an initial period as recommended or required by manufacturer.

Retain first subparagraph and associated subparagraphs below for gas-fired RTUs.

20. Perform the following operations for both minimum and maximum firing.  Adjust burner for peak efficiency.

a. Measure gas pressure on manifold.

b. Inspect operation of power vents.

c. Measure combustion-air temperature at inlet to combustion chamber.

d. Measure flue-gas temperature at furnace discharge.

e. Perform flue-gas analysis.  Measure and record flue-gas carbon dioxide and oxygen concentration.

f. Measure supply-air temperature and volume when burner is at maximum firing rate and when burner is off.  Calculate useful heat to supply air.

21. Calibrate thermostats.

22. Adjust and inspect high-temperature limits.

23. Inspect outdoor-air dampers for proper stroke and interlock with return-air dampers.

24. Start refrigeration system and measure and record the following when ambient is a minimum of 15 deg F (8 deg C) above return-air temperature:

a. Coil leaving-air, dry- and wet-bulb temperatures.

b. Coil entering-air, dry- and wet-bulb temperatures.

c. Outdoor-air, dry-bulb temperature.

d. Outdoor-air-coil, discharge-air, dry-bulb temperature.

25. Inspect controls for correct sequencing of heating, mixing dampers, refrigeration, and normal and emergency shutdown.

26. Measure and record the following minimum and maximum airflows.  Plot fan volumes on fan curve.

a. Supply-air volume.

b. Return-air volume.

c. Relief-air volume.

d. Outdoor-air intake volume.

27. Simulate maximum cooling demand and inspect the following:

a. Compressor refrigerant suction and hot-gas pressures.

b. Short circuiting of air through condenser coil or from condenser fans to outdoor-air intake.

28. Verify operation of remote panel including pilot-light operation and failure modes.  Inspect the following:

a. High-temperature limit on gas-fired heat exchanger.

b. Low-temperature safety operation.

c. Filter high-pressure differential alarm.

d. Economizer to minimum outdoor-air changeover.

e. Relief-air fan operation.

f. Smoke and firestat alarms.

29. After startup and performance testing and prior to Substantial Completion, replace existing filters with new filters.

3.6 CLEANING AND ADJUSTING

A. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to site during other-than-normal occupancy hours for this purpose.

B. After completing system installation and testing, adjusting, and balancing RTU and air-distribution systems, clean filter housings and install new filters.

3.7 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain RTUs.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15732END OF SECTION 15732

PACKAGED, OUTDOOR, CENTRAL-STATION AIR-HANDLING UNITS
15732 - 1

