Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15816 - NONMETAL DUCTS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Fibrous-glass ducts and fittings.

2. Phenolic-foam ducts and fittings.

3. Thermoset FRP ducts and fittings.

4. PVC ducts and fittings.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 15 Section "Metal Ducts" for single- and double-wall, rectangular and round ducts.

2. Division 15 Section "HVAC Casings" for factory- and field-fabricated casings for mechanical equipment.

3. Division 15 Section "Duct Accessories" for dampers, duct-mounting access doors and panels, turning vanes, and flexible ducts.

4. Division 15 Section "Testing, Adjusting, and Balancing" for testing, adjusting, and balancing requirements for nonmetal ducts.

1.3 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for duct construction design.

A. Delegated Duct Design:  Duct construction, including duct closure, reinforcements, and hangers and supports, shall comply with SMACNA's "Fibrous Glass Duct Construction Standards" and performance requirements and design criteria indicated.

Retain subparagraph below if static-pressure classes are not indicated on Drawings.  See the "Static-Pressure Classes" Article in the Evaluations for information about static-pressure limitations for fibrous-glass ducts.

According to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Contractor can assume a default static-pressure class of 1- or 2-inch wg (250 or 500 Pa) if static-pressure class is not indicated, which may apply to thermoset FRP and PVC ducts.

1. Static-Pressure Classes:

a. Supply Ducts (except in Mechanical Rooms):  [1-inch wg (250 Pa)] <Insert value>.

b. Supply Ducts (Upstream from Air Terminal Units):  [2-inch wg (500 Pa)] <Insert value>.

c. Supply Ducts (Downstream from Air Terminal Units):  [1-inch wg (250 Pa)] <Insert value>.

d. Supply Ducts (in Mechanical Equipment Rooms):  [2-inch wg (500 Pa)] <Insert value>.

e. Return Ducts (Negative Pressure):  [1-inch wg (250 Pa)] <Insert value>.

f. Exhaust Ducts (Negative Pressure):  [1-inch wg (250 Pa)] <Insert value>.

g. <Insert duct systems and static-pressure class>.

Retain seismic options and design criteria in first paragraph below that are approved by authorities having jurisdiction for Project sites that require seismic restraints and if overhead thermoset FRP and PVC ducts are specified.

B. Structural Performance:  Duct hangers and supports[ and seismic restraints] shall withstand the effects of gravity[ and seismic] loads and stresses within limits and under conditions to comply with [ASCE/SEI 7.] [SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."] <Insert document.>

Retain one of three subparagraphs below if retaining "SMACNA's 'Seismic Restraint Manual:  Guidelines for Mechanical Systems'" option in paragraph above. If using other seismic design criteria, delete three subparagraphs below.

1. Seismic Hazard Level A:  Seismic force to weight ratio, 0.48.

2. Seismic Hazard Level B:  Seismic force to weight ratio, 0.30.

3. Seismic Hazard Level C:  Seismic force to weight ratio, 0.15.

Retain paragraph below to comply with LEED-NC Prerequisite EQ 1.

C. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

1.4 SUBMITTALS

First three paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of the following products:

1. Fibrous-glass duct materials.

2. Phenolic-foam duct materials.

3. Thermoset FRP duct materials.

4. PVC duct materials.

B. LEED Submittals:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that duct systems comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

2. Product Data for Prerequisite EA 2:  Documentation indicating that duct systems comply with ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

Retain first subparagraph below if leak testing is retained in "Field Quality Control" Article.

3. Leakage Test Report for Prerequisite EA 2:  Documentation of work performed for compliance with ASHRAE/IESNA 90.1-2004, Section 6.4.4.2.2 - "Duct Leakage Tests."

Retain first subparagraph below if retaining "Duct Cleaning" Article.

4. Duct-Cleaning Test Report for Prerequisite EQ 1:  Documentation of work performed for compliance with ASHRAE 62.1-2004, Section 7.2.4 - "Ventilation System Start-Up."

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesives and sealants.

5. Product Data for Credit EQ 4.1:  For adhesives and sealants, including printed statement of VOC content.

C. Shop Drawings:

1. Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

2. Duct layout indicating sizes and pressure classes.

3. Elevation of top of ducts.

4. Dimensions of main duct runs from building grid lines.

5. Fittings.

6. Reinforcement and spacing.

7. Seam and joint construction.

8. Penetrations through fire-rated and other partitions.

9. Equipment installation based on equipment being used on Project.

10. Hangers and supports, including methods for duct and building attachment[, seismic restraints,] and vibration isolation.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain with "Performance Requirements" Article if design responsibilities have been delegated to Contractor.

D. Delegated-Design Submittal:

1. Duct materials and thicknesses.

2. Joint and seam construction and sealing.

3. Reinforcement details and spacing.

Retain subparagraph below if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

4. Design Calculations:  Calculations[, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation] for selecting hangers and supports[ and seismic restraints].

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

E. Coordination Drawings:  Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Duct installation in congested spaces, indicating coordination with general construction, building components, and other building services.  Indicate proposed changes to duct layout.

2. Suspended ceiling components.

3. Structural members to which duct will be attached.

4. Size and location of initial access modules for acoustical tile.

5. Penetrations of smoke barriers and fire-rated construction.

6. Items penetrating finished ceiling including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item>.

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

F. Welding certificates.

G. Field quality-control reports.

1.5 QUALITY ASSURANCE

Retain one of first two paragraphs below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.  Retain first paragraph if only one AWS standard is applicable.  Retain second paragraph if more than one AWS standard is referenced.

A. Welding Qualifications:  Qualify procedures and personnel according to [AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports] [AWS D1.2/D1.2M, "Structural Welding Code - Aluminum," for aluminum supports].

B. Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

2. AWS D1.2/D1.2M, "Structural Welding Code - Aluminum," for aluminum supports.

Retain first two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.

C. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-Up."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

E. NFPA Compliance:

1. NFPA 90A, "Installation of Air Conditioning and Ventilating Systems."

2. NFPA 90B, "Installation of Warm Air Heating and Air Conditioning Systems."

Retain paragraph below for special construction.  Mockups are normally required only for static-pressure classes in excess of 3-inch wg (750 Pa) when verification of maximum allowable leakage is important.  If retaining, indicate location, size, and other details of mockups on Drawings and retain "Leakage Tests" Paragraph in "Field Quality Control" Article.

ASHRAE/IESNA 90.1 requires leakage testing for representative sections totaling no less than 25 percent of installed duct area for ducts designated to operate at a static-pressure class in excess of 3-inch wg (750 Pa).  Consider building a mockup of typical portions of the system that can be tested early in the construction process.  This standard, as enforced by some authorities having jurisdiction, requires duct systems with static-pressure classes in excess of 3-inch wg (750 Pa) to be identified on Drawings.

F. Mockups:

1. Before installing duct systems, build mockups representing static-pressure classes [3-inch wg (750 Pa)] <Insert static-pressure class> and higher.  Build mockups to comply with the following requirements, using materials indicated for the completed Work:

a. [Five] <Insert number> transverse joints.

b. [One] <Insert number> access door(s).

c. [Two] <Insert number> typical branch connections, each with at least one elbow.

d. [Two] <Insert number> typical flexible duct or flexible-connector connections for each duct and apparatus.

e. [One] <Insert number> 90-degree turn(s) with turning vanes.

f. [One] <Insert number> fire damper(s).

g. Perform leakage tests specified in "Field Quality Control" Article.  Revise mockup construction and perform additional tests as required to achieve specified minimum acceptable results.

Retain subparagraph below if mockups are installed as part of building rather than erected separately and the intention is to make an exception to the default requirement in Division 1 Section "Quality Requirements" for demolishing and removing mockups when directed unless otherwise indicated.

2. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

PART 2 -  PRODUCTS

2.1 FIBROUS-GLASS DUCTS AND FITTINGS

Maximum performance parameters are static-pressure classes from minus 2- to plus 2-inch wg (minus 500 to plus 500 Pa), velocity up to 2400 fpm (12.2 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed.  Fibrous-glass ducts are not appropriate for outdoor installation.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. CertainTeed Corporation; Insulation Group.

2. Johns Manville.

3. Knauf Insulation.

4. Owens Corning.

5. <Insert manufacturer's name>.

B. Fibrous-Glass Duct Materials:  Resin-bonded fiberglass, faced on the outside surface with fire-resistive FSK vapor retarder and with a smooth fiberglass mat finish on the air-side surface.

1. Duct Board:  Factory molded into rectangular boards.

2. Round Duct:  Factory molded into straight round duct and smooth fittings.

3. Temperature Limits:  40 to 250 deg F (5 to 121 deg C) inside ducts; 150 deg F (66 deg C) ambient temperature surrounding ducts.

4. Maximum Thermal Conductivity:  [0.24 Btu x in./h x sq. ft. x deg F (0.035 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

5. Moisture Absorption:  Not exceeding 5 percent by weight at 120 deg F (49 deg C) and 95 percent relative humidity for 96 hours when tested according to ASTM C 1104/C 1104M.

6. Permeability:  0.02 perms (1.15 ng/Pa x s x sq. m) maximum when tested according to ASTM E 96/E 96M, Procedure A.

7. Antimicrobial Agent:  Compound shall be tested for efficacy by an NRTL, and registered by the EPA for use in HVAC systems.

8. Noise-Reduction Coefficient:  0.65 minimum when tested according to ASTM C 423, Mounting A.

9. Required Markings:  EI rating, UL label, and other markings required by UL 181 on each full sheet of duct board.

C. Closure Materials:

Retain one of three subparagraphs below, or retain all to permit Contractor's choice.

1. Pressure-Sensitive Tape:  Comply with UL 181A; imprinted by the manufacturer with the coding "181A-P," the manufacturer's name, and a date code.

a. Tape:  Aluminum foil-scrim tape imprinted with listing information.

b. Minimum Tape Width:  2-1/2 inches (64 mm); 3 inches (76 mm) for duct board thicker than 1 inch (25 mm).

c. Staples:  1/2-inch (13-mm) outward clinching, 2 inches (51 mm) o.c. in tabs, one tab per joint.

d. Water resistant.

e. Mold and mildew resistant.

2. Heat-Activated Tape:  Comply with UL 181A; imprinted by the manufacturer with the coding "181A-H," the manufacturer's name, and a date code.

a. Tape:  Aluminum foil-scrim tape imprinted with listing information.

b. Minimum Tape Width:  3 inches (76 mm).

c. Heat-Sensitive Imprint:  Printed indicator on tape to show proper heating during application has been achieved.

d. Water resistant.

e. Mold and mildew resistant.

3. Two-Part Tape Sealing System:  Comply with UL 181A; imprinted by the manufacturer with the coding "181A-M," the manufacturer's name, and a date code.

a. Tape:  Woven glass fiber impregnated with mineral gypsum.

b. Minimum Tape Width:  3 inches (76 mm).

c. Sealant:  Modified styrene acrylic.

d. Water resistant.

e. Mold and mildew resistant.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

f. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Fabrication:

1. Select joints, seams, transitions, elbows, and branch connections and fabricate according to [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 2, "Specifications and Closure," and Chapter 4, "Fittings and Connections."] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section II, "Fabrication of Straight Duct Modules," Section III, "Fabrication of Fittings from Modules or Flat Board," and Section IV, "Closure."]

2. Fabricate 90-degree mitered elbows to include turning vanes.

3. Reinforcements:  Comply with requirements in [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 5, "Reinforcement"] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section V, "Reinforcement"] for channel- and tie-rod reinforcement materials, spacing, and fabrication.

Retain subparagraph below for preformed round duct.

4. Preformed Round Duct:  Comply with NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section VII, "Preformed Round Duct."

2.2 PHENOLIC-FOAM DUCTS AND FITTINGS

Maximum performance parameters are static-pressure classes from minus 4- to plus 4-inch wg (minus 1000 to plus 1000 Pa), velocity up to 5000 fpm (25 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Knauf has an exclusive agreement with Pal International in Italy to market the KoolDuct System in the U.S.

1. Knauf Insulation.

2. <Insert manufacturer's name>.

B. Duct Panel:  CFC-free phenolic-foam bonded on both sides with factory-applied 0.001-inch- (0.025-mm-) thick, aluminum foil reinforced with fiberglass scrim.

1. Maximum Temperature:  158 deg F (70 deg C) inside ducts or ambient temperature surrounding ducts.

2. Maximum Thermal Conductivity:  [0.13 Btu x in./h x sq. ft. x deg F (0.019 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

3. Permeability:  0.0002 perms (0.0115 ng/Pa x s x sq. m) maximum when tested according to ASTM E 96/E 96M, Procedure A.

4. Antimicrobial Agent:  Compound shall be tested for efficacy by an NRTL, and registered by the EPA for use in HVAC systems.

5. Noise-Reduction Coefficient:  0.65 minimum when tested according to ASTM C 423, Mounting A.

6. Required Markings:  UL label and other markings required by UL 181 on each full sheet of duct panel; UL ratings for closure materials.

C. Closure Materials:

1. V-Groove Adhesive:  Silicone.

Retain first subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

a. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain one of two subparagraphs below, or retain both to permit Contractor's choice.

2. Pressure-Sensitive Tape:  Comply with UL 181A; imprinted by the manufacturer with the coding "181A-P," the manufacturer's name, and a date code.

a. Tape:  Aluminum foil tape imprinted with listing information.

b. Minimum Tape Width:  3 inches (76 mm).

c. Water resistant.

d. Mold and mildew resistant.

3. Polymeric Sealing System:

a. Structural Membrane:  Woven glass fiber.

b. Minimum Tape Width:  3 inches (76 mm).

c. Sealant:  Water based.

d. Color:  White.

e. Water resistant.

f. Mold and mildew resistant.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

g. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Fabrication:

1. Fabricate joints, seams, transitions, reinforcement, elbows, branch connections, access doors and panels, and damage repairs according to Knauf Insulation's "Knauf KoolDuct System Design Guide," Section 4, "Duct Construction," and Section 5, "Ductwork System General."

2. Fabricate 90-degree mitered elbows to include turning vanes.

2.3 THERMOSET FRP DUCTS AND FITTINGS

Maximum performance parameters vary among manufacturers but are typically static-pressure classes from minus 4- to plus 10-inch wg (minus 1000 to plus 2500 Pa), velocity up to 2500 fpm (12.7 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed.  These ducts are installed underground or outside the building because of NFPA 90A and NFPA 90B requirements to comply with UL 181, Class 1.  Verify duct material selection with authorities having jurisdiction prior to design.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. McGill AirFlow LLC.

2. Perry Fiberglass Products, Inc.

3. Spunstrand Inc.

4. <Insert manufacturer's name>.

B. Duct and Fittings:

Retain one or both of first two subparagraphs below.  Retain the first if duct is to be installed indoors aboveground and is approved for installation in the building by authorities having jurisdiction.  Retain the second if duct is to be installed underground.  Second subparagraph is the least costly duct.

1. Thermoset FRP Resin:  Manufacture duct with resin that complies with UL 181, Class 1, maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL according to ASTM E 84.

2. Inner Liner:  FSK liner rated by an NRTL to comply with UL 181, Class 1.

Verify minimum thickness in subparagraphs below with manufacturer.  Thickness varies with manufacturer and duct size.

3. Round Duct:  ASTM D 2996, Type I, Grade 2, Class E, filament-wound duct, minimum [0.125-inch (3.2-mm)] <Insert thickness> wall thickness, with tapered bell and spigot ends for adhesive joints, or plain ends with couplings.

4. Round Fittings:  Compression or spray-up/contact, molded of same material, pressure class, and joining method as duct.

5. Rectangular Fittings:  Minimum [0.125-inch- (3.2-mm-)] <Insert thickness> thick flat sheet with fiberglass roving and resin-reinforced joints and seams.

6. Double-Wall Insulated Duct:  Inner and outer duct complying with requirements for "Round Duct" description above.  Polyurethane foam or isocyanurate insulation with maximum thermal conductivity of [0.14 Btu x in./h x sq. ft. x deg F (0.020 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature.

C. Joining Materials:  Roving and polyester resin.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use fiberglass adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Fabrication:

1. Fabricate joints, seams, transitions, reinforcement, elbows, branch connections, and access doors and panels according to SMACNA's "Thermoset FRP Duct Construction Manual," Chapter 7, "Requirements."

2. Fabricate 90-degree rectangular mitered elbows to include turning vanes, 90-degree round elbows with a minimum of three segments for 12 inches (300 mm) and smaller and a minimum of five segments for 14 inches (350 mm) and larger.

Retain paragraph below if duct is installed underground and drain piping can be run to air-gap drain.

E. Drains:  Formed drain pockets with a minimum of NPS 1 (DN 25) threaded pipe connections.

2.4 PVC DUCTS AND FITTINGS

Maximum performance parameters vary among manufacturers but are typically static-pressure classes from minus 4- to plus 10-inch wg (minus 1000 to plus 2500 Pa), velocity up to 2500 fpm (12.7 m/s), and leakage class 6 cfm/100 sq. ft. at 1-inch wg (0.29 L/s per sq. m at 250 Pa) with all joints sealed.  These ducts are installed underground or outside the building because of NFPA 90A and NFPA 90B requirements to comply with UL 181, Class 1.  Verify duct material selection with authorities having jurisdiction prior to design.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. General Plastics, Inc.

2. GPK Products, Inc.

3. Harvel Plastics, Inc.

4. Kroy Industries, Inc.

5. Northern Pipe Product Inc.; an Otter Tail company.

6. Plastinetics Inc.

7. Spears Manufacturing Company.

8. <Insert manufacturer's name>.

B. Duct and Fittings:

1. Round Duct:  Comply with cell Classification 12454-B in ASTM D 1784, with external loading properties of ASTM D 2412.

2. Round Fittings:  Socket end molded of same material, pressure class, and joining method as duct.

Verify minimum thickness in subparagraph below with manufacturer.  Thickness varies with manufacturer and duct size.

3. Rectangular Fittings:  Minimum [0.125-inch- (3.2-mm-)] <Insert thickness> thick flat sheet with heat-formed corners and continuous welded butt joints.

C. Joining Materials:  PVC solvent cement complying with ASTM D 2564.

Retain two subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

1. Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

2. Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

D. Fabrication:

1. Fabricate joints, seams, transitions, reinforcement, elbows, branch connections, and access doors and panels according to SMACNA's "Thermoplastic Duct (PVC) Construction Manual," Chapter 3, "Standards of Construction for PVC Duct Systems."

2. Fabricate 90-degree rectangular mitered elbows to include turning vanes, 90-degree round elbows with a minimum of three segments for 12 inches (300 mm) and smaller and a minimum of five segments for 14 inches (350 mm) and larger.

Retain paragraph below if duct is installed underground and drain piping can be run to air-gap drain.

E. Drains:  PVC drain pockets with a minimum of NPS 1 (DN 25) threaded PVC pipe connections.

2.5 HANGERS AND SUPPORTS

Indicate extent of corrosive environment on Drawings.

A. Hanger Rods for Noncorrosive Environments:  Cadmium-plated steel rods and nuts.

B. Hanger Rods for Corrosive Environments:  Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

C. Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1 (Table 4-1M), "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct."

D. Steel Cables:  [ASTM A 603, galvanized] [ASTM A 492, stainless] steel with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

E. Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

F. Trapeze and Riser Supports:  Steel shapes complying with ASTM A 36/A 36M.

2.6 SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this article with structural engineer and with Drawings.  See the "Seismic Considerations" Article in the Evaluations for discussion on seismic restraints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Cooper B-Line, Inc.; a division of Cooper Industries.

2. Ductmate Industries, Inc.

3. Hilti Corp.

4. Kinetics Noise Control.

5. Loos & Co.; Cableware Division.

6. Mason Industries.

7. TOLCO; a brand of NIBCO INC.

8. Unistrut Corporation; Tyco International, Ltd.

9. <Insert manufacturer's name>.

See the Evaluations in Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for discussion on seismic-restraint capacities and rating services.

B. General Requirements for Restraint Components:  Rated strengths, features, and applications shall be as defined in reports by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

1. Structural Safety Factor:  Allowable strength in tension, shear, and pullout force of components shall be at least [four] <Insert number> times the maximum seismic forces to which they will be subjected.

C. Channel Support System:  Shop- or field-fabricated support assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end.  Include matching components and corrosion-resistant coating.

D. Restraint Cables:  [ASTM A 603, galvanized] [ASTM A 492, stainless]-steel cables with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for restraining cable service; and with an automatic-locking and clamping device or double-cable clips.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause rods to buckle.  Use with either channel- or cable-type bracing assemblies when required to counter seismic forces.  Detail fabrication and indicate locations on Drawings.

E. Hanger Rod Stiffener:  [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

F. Mechanical Anchor Bolts:  Drilled-in and stud-wedge or female-wedge type.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

PART 3 -  EXECUTION

3.1 DUCT INSTALLATION

A. Install ducts with fewest possible joints.

B. Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

C. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

D. Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

E. Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges.  Overlap openings on four sides by at least 1-1/2 inches (38 mm).

F. Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers.  Comply with requirements in Division 15 Section "Duct Accessories" for fire and smoke dampers.

G. Protect duct interiors from the moisture, construction debris and dust, and other foreign materials.[ Comply with SMACNA's "Duct Cleanliness for New Construction Guidelines."]

H. Install fibrous-glass ducts and fittings to comply with [NAIMA AH116, "Fibrous Glass Duct Construction Standards] [SMACNA's "Fibrous Glass Duct Construction Standards]."

I. Install foam ducts and fittings to comply with Knauf Insulation's "Knauf KoolDuct System Design Guide."

J. Install thermoset FRP ducts and fittings to comply with SMACNA's "Thermoset FRP Duct Construction Manual."

K. Install PVC ducts and fittings to comply with SMACNA's "Thermoplastic Duct (PVC) Construction Manual."

3.2 HANGER AND SUPPORT INSTALLATION

A. Install hangers and supports for fibrous-glass ducts and fittings to comply with [SMACNA's "Fibrous Glass Duct Construction Standards," Chapter 6, "Hangers and Supports."] [NAIMA AH116, "Fibrous Glass Duct Construction Standards," Section VI, "Hangers and Supports."]

B. Install hangers and supports for phenolic-foam ducts and fittings to comply with Knauf Insulation's "Knauf KoolDuct System Design Guide," Section 5, "Ductwork System General."

C. Install hangers and supports for thermoset FRP ducts and fittings to comply with SMACNA's "Thermoset FRP Duct Construction Manual," Chapter 7, "Requirements."

D. Install hangers and supports for PVC ducts and fittings to comply with SMACNA's "Thermoplastic Duct (PVC) Construction Manual," Chapter 3, "Standards of Construction for PVC Duct Systems."

Verify attachment selection and spacing in two paragraphs below with structural engineer.

E. Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Install concrete inserts before placing concrete.

2. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

3. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches (100 mm) thick.

4. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

Retain subparagraph below for Projects that require seismic restraints.

5. Do not use powder-actuated concrete fasteners for seismic restraints.

F. Install upper attachments to structures.  Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

3.3 SEISMIC-RESTRAINT-DEVICE INSTALLATION

A. Install ducts with hangers and braces designed to support the duct and to restrain against seismic forces required by applicable building codes.  Comply with [SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."] [ASCE/SEI 7.]

Options for 40 and 80 feet (12 and 24 m) in first subparagraph below are recommended by SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."  Revise these dimensions based on the configuration of duct and the seismic hazard.

1. Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

2. Brace a change of direction longer than 12 feet (3.7 m).

B. Select sizes of components so strength will be adequate to carry present and future static and seismic loads within restraint device capacity.

C. Install cables so they do not bend across edges of adjacent equipment or building structure.

D. Install cable restraints where ducts are suspended with vibration isolators.

E. Install seismic-restraint devices using methods approved by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

F. Attachment to Structure:  If specific attachment is not indicated, anchor bracing and restraints to structure to flanges of beams, to upper truss chords of bar joists, or to concrete members.

G. Drilling for and Setting Anchors:

1. Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors.  Do not damage existing reinforcement or embedded items during drilling.  Notify the Architect if reinforcing steel or other embedded items are encountered during drilling.  Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors:  Protect threads from damage during anchor installation.  Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Set anchors to manufacturer's recommended torque, using a torque wrench.

5. Install zinc-coated steel anchors for interior applications and stainless-steel anchors for applications exposed to weather.

3.4 PAINTING

Retain this article if thermoset FRP or PVC ducts are specified.

A. Paint interior of [thermoset FRP] [and] [PVC] ducts that are visible through registers and grilles and that do not have duct liner.  Apply one coat of flat, black, latex paint over a compatible galvanized-steel primer.  Paint materials and application requirements are specified in Division 9 painting Sections.

3.5 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain first paragraph below for ducts in pressure classes higher than 3-inch wg (750 Pa) or if applying for LEED credits.  It may not be economically practical to test ducts in pressure classes less than 3-inch wg (750 Pa).

B. Leakage Tests:

1. Comply with SMACNA's "HVAC Air Duct Leakage Test Manual."  Submit a test report for each test.

2. Test the following systems:

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.2 - "Duct Leakage Tests" requires leak testing of at least 25 percent of total installed duct area with a pressure class in excess of 3-inch wg (750 Pa).  Retain first subparagraph below for minimum requirements if applying for LEED certification or complying with ASHRAE/IESNA 90.1-2004.  To define more stringent requirements, retain subsequent subparagraphs as applicable and delete first subparagraph.  Consider cost impact when specifying the extent of duct area to be tested.  It is not common to leak test all ducts or ducts with a pressure class less than 3-inch wg (750 Pa).

a. Ducts with a Pressure Class Higher Than 3-Inch wg (750 Pa):  Test representative duct sections[, selected by Architect from sections installed,] totaling no less than 25 percent of total installed duct area for each designated pressure class.

b. Supply Ducts with a Pressure Class of [2-Inch wg (500 Pa)] [3-Inch wg (750 Pa)] [4-Inch wg (1000 Pa)] <Insert value> or Higher:  Test representative duct sections[, selected by Architect from sections installed,] totaling no less than [50] [100] <Insert value> percent of total installed duct area for each designated pressure class.

c. Return Ducts with a Pressure Class of [2-Inch wg (500 Pa)] [3-Inch wg (750 Pa)] [4-Inch wg (1000 Pa)] <Insert value> or Higher:  Test representative duct sections[, selected by Architect from sections installed,] totaling no less than [50] [100] <Insert value> percent of total installed duct area for each designated pressure class.

d. Exhaust Ducts with a Pressure Class of [2-Inch wg (500 Pa)] [3-Inch wg (750 Pa)] [4-Inch wg (1000 Pa)] <Insert value> or Higher:  Test representative duct sections[, selected by Architect from sections installed,] totaling no less than [50] [100] <Insert value> percent of total installed duct area for each designated pressure class.

e. Outdoor Air Ducts with a Pressure Class of [2-Inch wg (500 Pa)] [3-Inch wg (750 Pa)] [4-Inch wg (1000 Pa)] <Insert value> or Higher:  Test representative duct sections[, selected by Architect from sections installed,] totaling no less than [50] [100] <Insert value> percent of total installed duct area for each designated pressure class.

3. Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

Retain first subparagraph below for field-insulated thermoset FRP or PVC ducts installed outside the building.

4. Test for leaks before applying external insulation.

5. Conduct tests at static pressures equal to maximum design pressure of system or section being tested.  If static-pressure classes are not indicated, test entire system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.  Give [seven] <Insert number> days' advance notice for testing.

Retain first paragraph below if duct cleaning is required.  Text was taken from NADCA ACR, dated 2005.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

C. Duct System Cleanliness Tests:

1. Visually inspect duct system to ensure that no visible contaminants are present.

2. Test sections of nonmetal duct system, chosen randomly by Owner, for cleanliness according to "Vacuum Test" in NADCA ACR, "Assessment, Cleaning and Restoration of HVAC Systems."

a. Acceptable Cleanliness Level:  Net weight of debris collected on the filter media shall not exceed 0.75 mg/100 sq. cm.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

D. Duct system will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

3.6 DUCT CLEANING

Retain this article for applications where construction dust and debris in duct system must be removed before air-system operation or if applying for LEED certification.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

A. Clean [new] [existing] [new and existing] duct system(s) before testing, adjusting, and balancing.

B. Use service openings for entry and inspection.

1. Create new openings and install access panels appropriate for duct static-pressure class if required for cleaning access.  Provide insulated panels for insulated or lined duct.  Patch duct as recommended by duct manufacturer.  Comply with Division 15 Section "Duct Accessories" for access panels and doors.

2. Disconnect and reconnect flexible ducts as needed for cleaning and inspection.

3. Remove and reinstall ceiling to gain access during the cleaning process.

C. Particulate Collection and Odor Control:

1. When venting vacuuming system inside the building, use HEPA filtration with 99.97 percent collection efficiency for 0.3-micron-size (or larger) particles.

2. When venting vacuuming system to outdoors, use filter to collect debris removed from HVAC system, and locate exhaust downwind and away from air intakes and other points of entry into building.

D. Clean the following components by removing surface contaminants and deposits:

1. Air outlets and inlets (registers, grilles, and diffusers).

2. Supply, return, and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

3. Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

4. Coils and related components.

5. Return-air ducts, dampers, actuators, and turning vanes except in ceiling plenums and mechanical equipment rooms.

6. Supply-air ducts, dampers, actuators, and turning vanes.

7. Dedicated exhaust and ventilation components and makeup air systems.

E. Mechanical Cleaning Methodology:

1. Use vacuum-collection devices that are operated continuously during cleaning.  Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

2. Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of ducts or duct accessories.

3. Clean fibrous-glass duct with HEPA vacuuming equipment; do not permit duct to get wet.  Replace fibrous-glass duct that is damaged, deteriorated, or delaminated or that has friable material, mold, or fungus growth.

4. Clean coils and coil drain pans according to NADCA 1992.  Keep drain pan operational.  Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

5. Provide drainage and cleanup for wash-down procedures.

6. Antimicrobial Agents and Coatings:  Apply EPA-registered antimicrobial agents if fungus is present.  Apply antimicrobial agents according to manufacturer's written instructions after removal of surface deposits and debris.

3.7 START UP

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004; see Section 7 - "Construction and System Start-Up."

A. Air Balance:  Comply with requirements in Division 15 Section "Testing, Adjusting, and Balancing."

3.8 DUCT SCHEDULE

Retain and revise required duct applications in this article.  Coordinate with materials specified in Part 2.

LEED-NC Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."  If using duct material alone to satisfy thermal requirements, verify that material is available in thickness needed to provide thermal performance without jeopardizing other requirements.

A. Indoor Ducts and Fittings:

Retain one or more of three subparagraphs below for materials of ducts to be installed indoors.  Indicate materials on Drawings if more than one is required.

1. Fibrous-Glass Rectangular Ducts and Fittings:

Retain first subparagraph below to require minimum flexural rigidity of fibrous-glass ducts.  Otherwise, Contractor will select EI rating as part of duct design based on size of ducts and static-pressure class.  SMACNA's "Fibrous Glass Duct Construction Standards" does not recognize EI-1400 .

a. Minimum Flexural Rigidity:  EI-[475] [800] [1400].

Retain first subparagraph below for minimum thermal performance of fibrous-glass ducts.  Otherwise, Contractor will select thickness based on structural requirements of ducts.  1-1/2- and 2-inch- (38- and 51-mm-) thick boards below are not available in EI-475.

b. Minimum Board Thickness:  [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (51 mm)].

2. Fibrous-Glass Round Ducts and Fittings:

a. Minimum Thickness:  [1 inch (25 mm)] <Insert thickness>.

3. Phenolic-Foam Rectangular Ducts and Fittings:

Retain first subparagraph below for minimum thermal performance of phenolic-foam ducts.  Otherwise, Contractor will select thickness based on structural requirements of ducts.

a. Minimum Panel Thickness:  [7/8 inch (22 mm)] [1-3/32 inches (28 mm)].

Retain subparagraph below for factory-applied aluminum cladding for indoor installation of ducts exposed to view.

b. Aluminum Cladding:  Minimum 0.025 inch (0.635 mm) thick.

B. Outdoor Ducts and Fittings:

Retain one or more of three subparagraphs below for materials of ducts to be installed outdoors.  Indicate materials on Drawings if more than one is required.

1. Phenolic-Foam Rectangular Ducts and Fittings:

Retain first subparagraph below for minimum thermal performance of phenolic-foam ducts.  Otherwise, Contractor will select thickness based on structural requirements of ducts.

a. Minimum Panel Thickness:  [7/8 inch (22 mm)] [1-3/32 inches (28 mm)].

Retain one of first two subparagraphs below for ducts installed outdoors.

b. Aluminum Cladding:  Minimum 0.032 inch (0.813 mm) thick.

c. Polymeric Sealing System:  Coat ducts, including gang-nail couplings, grip flanges, and couplings.

2. Thermoset FRP Round Ducts and Fittings:

Insulation thickness in first subparagraph below varies with manufacturer.

a. Double-Wall Insulated Ducts:  Minimum [5/8-inch (15.9-mm)] [7/8-inch (22.2-mm)] <Insert thickness> insulation thickness.

3. PVC Round Ducts and Fittings:

C. Underground Ducts:

Retain one or both subparagraphs below for materials of ducts to be installed underground.  Indicate materials on Drawings if more than one is required.

1. Thermoset FRP Round Ducts and Fittings:

a. Insulation Thickness:  [1 inch (25 mm)] <Insert thickness>.

b. Drain:  Minimum NPS 1 (DN 25) PVC pipe with P-trap to air-gap drain.

2. PVC Round Ducts and Fittings:

a. Drain:  Minimum NPS 1 (DN 25) PVC pipe with P-trap to air-gap drain.

END OF SECTION 15816

NONMETAL DUCTS
15816 - 1

