SWITCHBOARDS – low VOLTAGE (GROUP MOUNTED feeders – pow-r-line c)

Section 16429


section 16429

SWITCHBOARDS – low VOLTAGE (GROUP MOUNTED feeders – pow-r-line c)

PART 1 general

1.01 Scope

A. The Contractor shall furnish and install, where indicated, a free-standing, deadfront type low voltage distribution switchboard, utilizing group mounted circuit protective devices as specified herein, and as shown on the contract drawings. 

1.02 Related Sections

A. Section 16671 – Transient Voltage Surge Suppression

B. Section 16475 – Circuit Breakers and Fusible Switches – Low Voltage

C. Section 16901 – Microprocessor-Based Metering Equipment

D. Section 16904 – Microprocessor Trip Units for Low-Voltage Circuit Breakers

1.03 References

A. The low voltage distribution switchboards and all components shall be designed, manufactured and tested in accordance with the latest applicable following standards:

1. NEMA PB-2

2. UL Standard 891.

1.04 Submittals – for Review/approval

A. The following information shall be submitted to the Engineer:

1. Master drawing index

2. Front view elevation

3. Floor plan

4. Top view

5. Single line

6. Schematic diagram

7. Nameplate schedule

8. Component list

9. Conduit entry/exit locations

10. Assembly ratings including:

a. Short-circuit rating

b. Voltage

c. Continuous current

11. Major component ratings including:

a. Voltage

b. Continuous current

c. Interrupting ratings

12. Cable terminal sizes

13. Product data sheets.

B. Where applicable, the following additional information shall be submitted to the Engineer:

1. Busway connection

2. Connection details between close-coupled assemblies

3. Composite floor plan of close-coupled assemblies

4. Key interlock scheme drawing and sequence of operations.

1.05 Submittals – for construction

A. The following information shall be submitted for record purposes:

1. Final as-built drawings and information for items listed in paragraph 1.04

2. Wiring diagrams

3. Certified production test reports

4. Installation information

5. Seismic certification and equipment anchorage details.

B. The final (as-built) drawings shall include the same drawings as the original construction drawings and shall incorporate all changes made during the manufacturing process.

1.06 Qualifications

A. The manufacturer of the assembly shall be the manufacturer of the circuit protective devices within the assembly.

B. For the equipment specified herein, the manufacturer shall be ISO 9001 or 9002 certified.

C. The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of five (5) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

D. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of Uniform Building Code (UBC) for zone 4 application. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and be based upon testing of representative equipment. The test response spectrum shall be based upon a 5% minimum damping factor, UBC: a peak of 2.15g’s (3.2-11 Hz), and a ZPA of 0.86g’s applied at the base of the equipment. The tests shall fully envelop this response spectrum for all equipment natural frequencies up to at least 35 Hz.

-- (OR --

E. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of the California Building Code (CBC) through zone 4 application. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and be based upon testing of representative equipment. The test response spectrum shall be based upon a 5% minimum damping factor, CBC: a peak of 2.15g’s, and a ZPA of 0.86g’s applied at the base of the equipment. The tests shall fully envelop this response spectrum for all equipment natural frequencies up to at least 35 Hz.

-- (OR --

F. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of the BOCA National Building Code, paragraph 1612.6. This shall include both vertical and lateral required response spectra as specified. Alternatively, the manufacturer’s certification may be based on a detailed computer analysis of the entire assembly structure and its components. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and be based upon testing of representative equipment. The equipment manufacturer shall document the requirements necessary for proper seismic mounting of the equipment. The test response spectra shall meet or exceed the required response spectra peak acceleration of 1.6g’s (3.2-11 Hz) and a ZPA of 1.0g as specified in the BOCA National Building Code, for all equipment natural frequencies up to at least 35 Hz.

G. The following minimum mounting and installation guidelines shall be met, unless specifically modified by the above referenced standards.

1. The Contractor shall provide equipment anchorage details, coordinated with the equipment mounting provision, prepared and stamped by a licensed civil engineer in the state. Mounting recommendations shall be provided by the manufacturer based upon approved shake table tests used to verify the seismic design of the equipment.

2. The equipment manufacturer shall certify that the equipment can withstand, that is, function following the seismic event, including both vertical and lateral required response spectra as specified in above codes.

3. The equipment manufacturer shall document the requirements necessary for proper seismic mounting of the equipment. Seismic qualification shall be considered achieved when the capability of the equipment, meets or exceeds the specified response spectra.

1.07 Regulatory Requirements

A. The low-voltage switchboard shall be UL labeled.

1.08 Delivery, Storage and Handling

A. Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

1.09 Operation and Maintenance Manuals

A. Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins and renewal parts lists where applicable, for the complete assembly and each major component.

PART 2 Products

2.01 manufacturers

A. Cutler-Hammer

B. (__________

C. (__________

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

2.02 Ratings

A. The assembly shall be rated to withstand mechanical forces exerted during short-circuit conditions when connected directly to a power source having available fault current ([of (65,000) ((100,000) amperes symmetrical at rated voltage] [as shown on the drawings]. 
B. Voltage rating to be as indicated on the drawings.

2.03 Construction

A. Switchboard shall consist of the required number of vertical sections bolted together to form a rigid assembly. The sides and rear shall be covered with removable bolt-on covers. All edges of front covers or hinged front panels shall be formed. Provide adequate ventilation within the enclosure.

B. All sections of the switchboard shall be rear aligned with depth as shown on the drawings. All protective devices shall be group mounted. Devices shall be front removable and load connections front accessible enabling switchboard to be mounted against a wall.

-- (OR --

C. All sections of the switchboard shall be front and rear aligned with depth as shown on drawings. All protective devices shall be group mounted. Devices shall be front removable and load connections front and rear accessible. Rear access shall be provided.

D. The assembly shall be provided with adequate lifting means.

E. The switchboard shall be equal to Cutler-Hammer type Pow-R-Line C utilizing the components herein specified and as shown on the drawings.

F. (The switchboard shall be suitable for use as service entrance equipment and be labeled in accordance with UL requirements.

2.04 Bus

A. All bus bars shall be ([silver-plated copper] [tin-plated aluminum]. Main horizontal bus bars shall be mounted with all three phases arranged in the same vertical plane. Bus sizing shall be based on NEMA standard temperature rise criteria of 65 degrees C over a 40 degrees C ambient (outside the enclosure).

B. Provide a full capacity neutral bus where a neutral bus is indicated on the drawings.

C. A copper ground bus (minimum 1/4 x 2 inch), shall be furnished firmly secured to each vertical section structure and shall extend the entire length of the switchboard.

D. All hardware used on conductors shall be high-tensile strength and zinc-plated. All bus joints shall be provided with conical spring-type washers.

2.05 Wiring/Terminations

A. Small wiring, necessary fuse blocks and terminal blocks within the switchboard shall be furnished as required. Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, etc., shall be suitably marked for identification corresponding to appropriate designations on manufacturer’s wiring diagrams.

B. Mechanical-type terminals shall be provided for all line and load terminations suitable for copper or aluminum cable rated for 75 degrees C of the size as indicated on the drawings.

C. Lugs shall be provided in the incoming line section for connection of the main grounding conductor. Additional lugs for connection of other grounding conductors shall be provided as indicated on the drawings.

D. All control wire shall be type SIS, bundled and secured with nylon ties. Insulated locking spade terminals shall be provided for all control connections, except where saddle type terminals are provided integral to a device. All current transformer secondary leads shall first be connected to conveniently accessible short-circuit terminal blocks before connecting to any other device. All groups of control wires leaving the switchboard shall be provided with terminal blocks with suitable numbering strips. Provide wire markers at each end of all control wiring.

Note to Spec Writer:
Select main, tie and feeder device spec from section 16475 as indicated and insert under 2.06, 2.07, 2.08, and 2.09 as follows:
Power Circuit Breakers – Magnum DS


Paragraph 2.02 and 2.03
Power Circuit Breakers – DSII



Paragraph 2.04 and 2.05
Insulated Case Breakers



Paragraph 2.06 and 2.07
Molded Case Circuit Breakers 1200A and Below
Paragraph 2.08 and 2.09
Molded Case Circuit Breakers Above 1200A
 
Paragraph 2.10 and 2.11
Bolted Pressure Switches



Paragraph 2.13
Fusible Switches



Paragraph 2.14

2.06 main ([and tie] protective devices

2.07 Trip units

2.08 feeder protective devices

2.09 trip units

2.010 accessories

A. Provide shunt trips, bell alarms and auxiliary switches as shown on the contract drawings.

Note to Spec. Writer: 
For individual molded case breaker energy monitoring, add under accessories the IQ Energy Sentinel or IQ Power Sentinel from section 16901, paragraph 2.02 G or H in paragraph B below.

B. Circuit Breaker Energy Monitoring

Note to Spec. Writer: 
For centralized local monitoring of IQ Energy Sentinels select Central Energy Display (CED) from section 16901, paragraph 2.03 A. For centralized local monitoring of the IQ Energy Sentinel, Digitrip 810, 910 and OPTIM 750 or 1050, select  the Breaker Interface Module I (BIM II) from section 16901 paragraph 2.03 C.

C. Centralized Local Monitoring

2.011 miscellaneous devices

A. Key interlocks shall be provided as indicated on the drawings.

B. Control power transformers with primary and secondary protection shall be provided, as indicated on the drawings, or as required for proper operation of the equipment. ([Control power transformers shall have adequate capacity to supply power to the transformer cooling fans.]

C. (Each section of the switchboard shall be provided with a space heater ([thermostatically controlled]. Power for the space heaters shall be obtained ([from a control power transformer within the switchboard] [from a source as indicated on the drawings]. Supply voltage shall be ([120] [240] volts AC. 
2.012 utility metering

A. Where indicated on the drawings, furnish a separate barriered-off utility metering compartment complete with hinged sealable door. Bus work shall include provisions for mounting utility company current transformers and potential transformers or potential taps as required by the utility company. Provide service entrance label and provide necessary applicable service entrance features per NEC and local code requirements.

2.013 customer metering

A. Where indicated on the drawings, provide a separate customer metering compartment with front hinged door and include the following:

B. Current transformers for each meter. Current transformers shall be wired to shorting-type terminal blocks.

C. ([Potential transformers including primary and secondary fuses with disconnecting means] [Fused potential taps as the potential source] for metering as shown on the drawings.

Note to Spec. Writer:
Select devices as required for item 2.13 D. Refer to section 16901 for detailed specification for metering.
IQ Analyzer-6000 Series (Section 16901, paragraph 2.02 A.)
IQ DP-4000 Series (Section 16901, paragraph 2.02 B.)
IQ 300 Series (Section 16901, paragraph 2.02 C.)
IQ 200 Series (Section 16901, paragraph 2.02 D)

D. Microprocessor-Based Metering System

2.014 Enclosures

A. NEMA 1 Enclosure

B. Outdoor NEMA 3R Enclosure

1. Outdoor enclosure shall be non-walk-in and meet applicable NEMA 3R UL requirements.

2. Enclosure shall have ([flat roof] [sloping roof downward toward rear].

3. Outer sections shall be the same widths as indoor structures, except each end of the outdoor assembly shall have an end trim.

4. The enclosure shall be provided with ([bolt-on rear covers] [rear hinged doors] for each section.

5. Doors shall have provisions for padlocking.

6. Ventilating openings shall be provided ([complete with replaceable fiber glass air filters].

7. Provide space heaters ([thermostatically controlled] for each structure with adequate wattage to prevent the accumulation of moisture.

8. Power for space heaters, lights and receptacles shall be obtained from a ([control power transformer within the switchboard] [source as indicated on the drawings]. Supply voltage shall be ([120] [240] volts AC.

2.015 Nameplates

A. Engraved nameplates, mounted on the face of the assembly, shall be furnished for all main and feeder circuits as indicated on the drawings. Nameplates shall be laminated plastic, black characters on white background. Characters shall be 3/16-inch high, minimum. Nameplates shall give item designation and circuit number as well as frame ampere size and appropriate trip rating. Furnish master nameplate giving switchboard designation, voltage ampere rating, short-circuit rating, manufacturer’s name, general order number, and item number.

B. Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, etc., shall be suitably marked for identification corresponding to appropriate designations on manufacturer’s wiring diagrams.

2.016 Finish

A. All exterior and interior steel surfaces of the switchboard shall be properly cleaned and provided with a rust-inhibiting phosphatized coating. Color and finish of the switchboard shall be ANSI 61 light gray.

2.017 (transient voltage surge suppression

A. Provide transient voltage surge suppression as specified in Section 16671.

PART 3 execution

3.01 Factory Testing

A. The following standard factory tests shall be performed on the equipment provided under this section. All tests shall be in accordance with the latest version of ANSI and NEMA standards.

1. The switchboard shall be completely assembled, wired, adjusted, and tested at the factory. After assembly, the complete switchboard will be tested for operation under simulated service conditions to assure the accuracy of the wiring and the functioning of all equipment. The main circuits shall be given a dielectric test of 2200 volts for one (1) minute between live parts and ground, and between opposite polarities. The wiring and control circuits shall be given a dielectric test of 1500 volts for one (1) minute between live parts and ground.

B. The manufacturer shall provide three (3) certified copies of factory test reports.

C. (Factory tests as outlined above shall be witnessed by the owner’s representative.

1. The manufacturer shall notify the owner two (2) weeks prior to the date the tests are to be performed.

2. The manufacturer shall include the cost of transportation and lodging for up to three (3) owner’s representatives. The cost of meals and incidental expenses shall be the owner’s responsibility.

3.02 Manufacturer’s Certification

A. (A certified test report of all standard production tests shall be available to the Engineer upon request.

3.03 Training

A. The Contractor shall provide a training session for up to five (5) owner’s representatives for (____ normal workdays at a jobsite location determined by the owner.

B. The training session shall be conducted by a manufacturer’s qualified representative. The training program shall consist of instruction on operation of the assembly, circuit breakers, fused switches, and major components within the assembly.

3.04 Installation

A. The Contractors shall install all equipment per the manufacturer’s instructions, contract drawings and National Electrical Code.

B. The assembly shall be provided with adequate lifting means and shall be capable of being moved into installation position and bolted directly to ([Contractor supplied floor sills to be set level in concrete per manufacturer’s recommendations] [the floor without the use of floor sills provided the floor is level to 1/8 inch per 3-foot distance in any direction]. All necessary hardware to secure the assembly in place shall be provided by the Contractor.

3.05 field adjustments

A. The Contractor shall perform field adjustments of the protective devices as required to place the equipment in final operating condition. The settings shall be in accordance with the approved short-circuit study, protective device evaluation study and protective device coordination study.

B. Necessary field settings of devices and adjustments and minor modifications to equipment to accomplish conformance with an approved short circuit and protective device coordination study shall be carried out by the Contractor at no additional cost to the owner.

( Note to Spec. Writer – Select one


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one






16429-


12/02


