Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


MASTERSPEC Short Form Copyright 2002, The American Institute of Architects (AIA)

SECTION 16075 - ELECTRICAL IDENTIFICATION
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Identification for conductors and communication and control cable.

2. Warning labels and signs.

3. Equipment identification labels.

1.2 SUBMITTALS

A. Product Data:  For each electrical identification product indicated.

1.3 QUALITY ASSURANCE

A. Comply with ANSI A13.1.

1.4 COORDINATION

A. Coordinate identification names, abbreviations, colors, and other features with requirements in the Contract Documents, Shop Drawings, manufacturer's wiring diagrams, and the Operation and Maintenance Manual, and with those required by codes, standards, and 29 CFR 1910.145.  Use consistent designations throughout Project.

PART 2 -  PRODUCTS

Retain products in articles below that are retained in Part 3 "Application" Article.  Consider alternatives before specifying self-adhesive identification products.  See Editing Instruction No. 1 and "Writing Guide" Article in the Evaluations.

2.1 CONDUCTOR AND COMMUNICATION- AND CONTROL-CABLE IDENTIFICATION MATERIALS

A. Marker Tape:  Vinyl or vinyl -cloth, self-adhesive wraparound type, with circuit identification legend machine printed by thermal transfer or equivalent process.

2.2 WARNING LABELS AND SIGNS

A. Comply with NFPA 70 and 29 CFR 1910.145.

B. Self-Adhesive Warning Labels:  Factory printed, multicolor, pressure-sensitive adhesive labels, configured for display on front cover, door, or other access to equipment, unless otherwise indicated.

C. Baked-Enamel Warning Signs:  Preprinted aluminum signs, punched or drilled for fasteners, with colors, legend, and size required for application.  1/4-inch (6.4-mm) grommets in corners for mounting.  Nominal size, 7 by 10 inches (180 by 250 mm).

D. Metal-Backed, Butyrate Warning Signs:  Weather-resistant, nonfading, preprinted, cellulose-acetate butyrate signs with 0.0396-inch (1-mm) galvanized-steel backing; and with colors, legend, and size required for application.  1/4-inch (6.4-mm) grommets in corners for mounting.  Nominal size, 10 by 14 inches (250 by 360 mm).

E. Fasteners for Signs:  Self-tapping, stainless-steel screws or stainless-steel machine screws with nuts and flat and lock washers.

F. Warning label and sign shall include, but are not limited to, the following legends:

1. Multiple Power Source Warning:  "DANGER - ELECTRICAL SHOCK HAZARD - EQUIPMENT HAS MULTIPLE POWER SOURCES."

Dimension in first subparagraph below is clear space prescribed in NFPA 70 (2002 Edition), Table 110-26(A)(1), for equipment with nominal voltage to ground of 151 to 600 V, and with grounded parts, including concrete, brick, or tile walls, opposite the equipment.  Additional clear space is required at this voltage if there are unguarded exposed live parts on both sides of the workspace.  Retain below and revise to suit Project conditions or requirements of authorities having jurisdiction, or indicate varying clearance requirements on Drawings.

2. Workspace Clearance Warning:  "WARNING - OSHA REGULATION - AREA IN FRONT OF ELECTRICAL EQUIPMENT MUST BE KEPT CLEAR FOR 36 INCHES (915 mm)."

2.3 EQUIPMENT IDENTIFICATION LABELS

Retain one of two paragraphs below to specify type of labels Contractor must use to comply with NFPA 70 (2002 Edition), Article 110-22, "Identification of Disconnecting Means."  Note that, unless otherwise indicated, the labeling products selected below will also be used for labeling that is not required by NFPA 70 but may be specified in Part 3 "Application" Article to identify equipment other than disconnect devices.  See Evaluations.

A. Adhesive Film Label with Clear Protective Overlay:  Machine printed, in black, by thermal transfer or equivalent process.  Minimum letter height shall be 3/8 inch (10 mm).  Overlay shall provide a weatherproof and ultraviolet-resistant seal for label.

B. Self-Adhesive, Engraved, Laminated Acrylic or Melamine Label:  Adhesive backed, with white letters on a dark-gray background.  Minimum letter height shall be 3/8 inch (10 mm).

PART 3 -  EXECUTION

3.1 APPLICATION

Revise this Article to suit Project.

A. Auxiliary Electrical Systems Conductor and Cable Identification:  Use marker tape to identify field-installed alarm, control, signal, sound, intercommunications, voice, and data wiring connections.

1. Identify conductors, cables, and terminals in enclosures and at junctions, terminals, and cable pull points.  Identify by system and circuit designation.

2. Use system of designations that is uniform and consistent with system used by manufacturer for factory-installed connections.

B. Warning Labels for Indoor Cabinets, Boxes, and Enclosures for Power and Lighting:  Comply with 29 CFR 1910.145 and apply [self-adhesive warning labels] [baked-enamel warning signs] [metal-backed, butyrate warning signs].  Identify system voltage with black letters on an orange background.  Apply to exterior of door, cover, or other access.

1. Equipment with Multiple Power or Control Sources:  Apply to door or cover of equipment including, but not limited to, the following:

a. Power transfer switches.

b. Controls with external control power connections.

2. Equipment Requiring Workspace Clearance According to NFPA 70:  Unless otherwise indicated, apply to door or cover of equipment but not on flush panelboards and similar equipment in finished spaces.

Coordinate paragraph and subparagraphs below with electrical Sections in Divisions 2, 13, and 16.  Delete items not in Project.

C. Equipment Identification Labels:  On each unit of equipment, install unique designation label that is consistent with wiring diagrams, schedules, and Operation and Maintenance Manual.  Apply labels to disconnect switches and protection equipment, central or master units, control panels, control stations, terminal cabinets, and racks of each system.  Systems include power, lighting, control, communication, signal, monitoring, and alarm systems unless equipment is provided with its own identification.

1. Labeling Instructions:

a. Indoor Equipment:  [Adhesive film label with clear protective overlay] [Self-adhesive, engraved, laminated acrylic or melamine label].  Unless otherwise indicated, provide a single line of text with 1/2-inch- (13-mm-) high letters on 1-1/2-inch- (38-mm-) high label; where 2 lines of text are required, use labels 2 inches (50 mm) high.

b. Outdoor Equipment:  Engraved, laminated acrylic or melamine label, drilled for screw attachment.

c. Elevated Components:  Increase sizes of labels and legend to those appropriate for viewing from the floor.

2. Equipment to Be Labeled:

Identification labeling of some items listed below may be required by individual Sections or by NFPA 70.

a. Panelboards, electrical cabinets, and enclosures.

b. Electrical switchgear and switchboards.

c. Transformers.

d. Motor-control centers.

e. Disconnect switches.

f. Enclosed circuit breakers.

g. Motor starters.

h. Push-button stations.

i. Power transfer equipment.

j. Contactors.

k. <Insert equipment.>

3.2 INSTALLATION

A. Verify identity of each item before installing identification products.

Coordinate first paragraph below with Drawings.

B. Location:  Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment.

C. Apply identification devices to surfaces that require finish after completing finish work.

Retain paragraph below if self-adhesive identification products are specified.

D. Self-Adhesive Identification Products:  Clean surfaces before application, using materials and methods recommended by manufacturer of identification device.

Retain paragraph below for nonadhesive signs or labels.

E. Attach nonadhesive signs and plastic labels with screws and auxiliary hardware appropriate to the location and substrate.

Retain paragraph and subparagraphs below if color-coding of power and lighting conductors for voltage level identification is required to satisfy the Code, authorities having jurisdiction, or special Project requirements.  If retaining, coordinate with Division 16 Section "Conductors and Cables" and edit to indicate extent of color-coding required.  Below applies only to phase conductors.  Color-coding of grounded and grounding conductors is dictated by the Code.

F. Color-Coding for Phase[ and Voltage Level] Identification, 600 V and Less:  Use the colors listed below for ungrounded [service] [feeder] [branch-circuit] [service, feeder, and branch-circuit] conductors.

1. Color shall be factory applied.

2. Colors for 208/120-V Circuits:

a. Phase A:  Black.

b. Phase B:  Red.

c. Phase C:  Blue.

3. Colors for 480/277-V Circuits:

Colors specified in three subparagraphs below are those generally used for phase conductors at this voltage.

a. Phase A:  Brown.

b. Phase B:  Orange.

c. Phase C:  Yellow.

END OF SECTION 16075

ELECTRICAL IDENTIFICATION
16075 - 3

