Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16120 - CONDUCTORS AND CABLES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Building wires and cables rated 600 V and less.

2. Connectors, splices, and terminations rated 600 V and less.

3. Sleeves and sleeve seals for cables.

1.2 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Field quality-control test reports.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 CONDUCTORS AND CABLES

A. Copper Conductors:  Comply with NEMA WC 70.

B. Conductor Insulation:  Comply with NEMA WC 70 for Types THHN-THWN.

C. Multiconductor Cable:  Comply with NEMA WC 70 for armored cable, Type AC and metal-clad cable, Type MC with ground wire.

2.2 CONNECTORS AND SPLICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. AFC Cable Systems, Inc.

2. Hubbell Power Systems, Inc.

3. O-Z/Gedney; EGS Electrical Group LLC.

4. 3M; Electrical Products Division.

5. Tyco Electronics Corp.

B. Description:  Factory-fabricated connectors and splices of size, ampacity rating, material, type, and class for application and service indicated.

2.3 SLEEVES FOR CABLES

A. Steel Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.

Consider retaining first paragraph below if cables penetrate exterior walls below grade.

B. Cast-Iron Pipe Sleeves:  Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.

C. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 7 Section "Through-Penetration Firestop Systems."

2.4 SLEEVE SEALS

Retain this Article if annular space between pipe sleeves and cables must be sealed against hydrostatic pressure.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Advance Products & Systems, Inc.

2. Calpico, Inc.

3. Metraflex Co.

4. Pipeline Seal and Insulator, Inc.

B. Description:  Modular sealing device, designed for field assembly, to fill annular space between sleeve and cable.

1. Sealing Elements:  [EPDM] [NBR] <Insert sealing element> interlocking links shaped to fit surface of cable or conduit.  Include type and number required for material and size of raceway or cable.

2. Pressure Plates:  [Plastic] [Carbon steel] [Stainless steel].  Include two for each sealing element.

3. Connecting Bolts and Nuts:  [Carbon steel with corrosion-resistant coating] [Stainless steel] of length required to secure pressure plates to sealing elements.  Include one for each sealing element.

PART 3 -  EXECUTION

3.1 CONDUCTOR MATERIAL APPLICATIONS

A. Feeders:  Copper.  Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

B. Branch Circuits:  Copper.  Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

3.2 CONDUCTOR INSULATION AND MULTICONDUCTOR CABLE APPLICATIONS AND WIRING METHODS

This Article provides examples of application requirements for conductors and cables.  Edit to select wiring methods for various environments in Project.  Add other methods if required.  Revise conductor insulation and cable type designations to suit Project conditions, authorities having jurisdiction, and practice.  Refer to NFPA 70 and to UL's "Electrical Construction Equipment Directory" for additional application information about conductor sizes, insulation temperature ratings in cables, and product-use classifications and restrictions.

See Editing Instruction No. 2 in the Evaluations for use of Type MI cable as service entrance conductor inside a building.

A. Service Entrance:  Type THWN, single conductors in raceway.

B. Exposed Feeders:  Type THHN, single conductors in raceway.

C. Feeders Concealed in Ceilings, Walls, Partitions, and Crawlspaces:  Type THHN, single conductors in raceway.

D. Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type THWN, single conductors in raceway.
E. Exposed Branch Circuits, Including in Crawlspaces:  Type THWN, single conductors in raceway.
F. Branch Circuits Concealed in Ceilings, Walls, and Partitions:  Type THHN, single conductors in raceway
Coordinate first paragraph below with Division 2 Section "Underground Ducts and Utility Structures."

G. Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type THWN, single conductors in raceway.
H. Class 1 Control Circuits:  Type THHN-THWN, in raceway.

I. Class 2 Control Circuits:  Type THHN-THWN, in raceway, Power-limited tray cable, in cable tray.

3.3 INSTALLATION OF CONDUCTORS AND CABLES

A. Conceal cables in finished walls, ceilings, and floors, unless otherwise indicated.

B. Use manufacturer-approved pulling compound or lubricant where necessary; compound used must not deteriorate conductor or insulation.  Do not exceed manufacturer's recommended maximum pulling tensions and sidewall pressure values.

C. Use pulling means, including fish tape, cable, rope, and basket-weave wire/cable grips, that will not damage cables or raceway.

D. Install exposed cables parallel and perpendicular to surfaces of exposed structural members, and follow surface contours where possible.

E. Support cables according to Division 16 Section "Electrical Supports and Seismic Restraints."

F. Identify and color-code conductors and cables according to Division 16 Section "Electrical Identification."

G. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A.

H. Make splices and taps that are compatible with conductor material and that possess equivalent or better mechanical strength and insulation ratings than unspliced conductors.

Delete subparagraph below unless aluminum conductors are specified.

1. Use oxide inhibitor in each splice and tap conductor for aluminum conductors.

I. Wiring at Outlets:  Install conductor at each outlet, with at least [6 inches (150 mm)] [12 inches (300 mm)] of slack.

3.4 SLEEVE INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 7 Section "Through-Penetration Firestop Systems."

B. Concrete Slabs and Walls:  Install sleeves for penetrations unless core-drilled holes or formed openings are used.  Install sleeves during erection of slabs and walls.

C. Fire-Rated Assemblies:  Install sleeves for penetrations of fire-rated floor and wall assemblies unless openings compatible with firestop system used are fabricated during construction of floor or wall.

Edit first paragraph below as required for 2-inch (50-mm) extension above floor.

D. Cut sleeves to length for mounting flush with both wall surfaces.

E. Extend sleeves installed in floors 2 inches (50 mm) above finished floor level.

Edit paragraph below as required for Project design conditions and seismic-criteria status.

F. Size pipe sleeves to provide 1/4-inch (6.4-mm) annular clear space between sleeve and cable unless sleeve seal is to be installed.

Retain first paragraph below if external sealing is required.

G. Seal space outside of sleeves with grout for penetrations of concrete and masonry and with approved joint compound for gypsum board assemblies.

H. Interior Penetrations of Non-Fire-Rated Walls and Floors:  Seal annular space between sleeve and cable, using joint sealant appropriate for size, depth, and location of joint according to Division 7 Section "Joint Sealants."

I. Fire-Rated-Assembly Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at cable penetrations.  Install sleeves and seal with firestop materials according to Division 7 Section "Through-Penetration Firestop Systems."

J. Roof-Penetration Sleeves:  Seal penetration of individual cables with flexible boot-type flashing units applied in coordination with roofing work.

K. Aboveground Exterior-Wall Penetrations:  Seal penetrations using sleeves and mechanical sleeve seals.  Size sleeves to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

L. Underground Exterior-Wall Penetrations:  Install cast-iron "wall pipes" for sleeves.  Size sleeves to allow for 1-inch (25-mm) annular clear space between cable and sleeve for installing mechanical sleeve seals.

3.5 SLEEVE-SEAL INSTALLATION

A. Install to seal underground exterior-wall penetrations.

B. Use type and number of sealing elements recommended by manufacturer for cable material and size.  Position cable in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between cable and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

3.6 FIRESTOPPING

A. Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly according to Division 7 Section "Through-Penetration Firestop Systems."

3.7 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

B. Tests and Inspections:

Performing NETA tests on all conductors and cables can be expensive.  Consider limiting testing to a certain group of conductors, such as service entrance and feeder conductors, or to those conductors feeding critical equipment and services.  To require all conductors and cables to be tested, delete option in first subparagraph below and delete associated subparagraph.

1. After installing conductors and cables and before electrical circuitry has been energized, test service entrance and feeder conductors, for compliance with requirements.

2. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

Consider the cost and benefit of infrared scanning of cable and conductor splices before retaining subparagraph and associated subparagraphs below.

3. Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each splice in cables and conductors No. 3 AWG and larger.  Remove box and equipment covers so splices are accessible to portable scanner.

a. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each splice 11 months after date of Substantial Completion.

b. Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

c. Record of Infrared Scanning:  Prepare a certified report that identifies splices checked and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

C. Test Reports:  Prepare a written report to record the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

D. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 16120

CONDUCTORS AND CABLES
16120 - 2

