Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16130 - RACEWAYS AND BOXES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes raceways, fittings, boxes, enclosures, and cabinets for electrical wiring.

B. See Division 2 Section "Underground Ducts and Utility Structures" for exterior ductbanks and manholes, and underground handholes, boxes, and utility construction.

1.2 SUBMITTALS

A. Product Data:  For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

Retain paragraph below for custom enclosures only.

B. Shop Drawings:  For custom enclosures and cabinets.  Include plans, elevations, sections, details, and attachments to other work.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 METAL CONDUIT AND TUBING

A. Rigid Steel Conduit:  ANSI C80.1.

B. IMC:  ANSI C80.6.

C. EMT:  ANSI C80.3.

D. FMC:  Zinc-coated steel.

E. LFMC:  Flexible steel conduit with PVC jacket.

F. Fittings for Conduit (Including all Types and Flexible and Liquidtight), EMT, and Cable:  NEMA FB 1; listed for type and size raceway with which used, and for application and environment in which installed.

Coordinate first subparagraph below with Drawings.

1. Conduit Fittings for Hazardous (Classified) Locations:  Comply with UL 886.

2. Fittings for EMT:  Steel, set-screw or compression type.

2.2 NONMETALLIC CONDUIT AND TUBING

See Evaluations for descriptions of nonmetallic conduit types.

A. ENT:  NEMA TC 13.

B. RNC:  NEMA TC 2, Type EPC-40-PVC, unless otherwise indicated.

C. LFNC:  UL 1660.

D. Fittings for ENT and RNC:  NEMA TC 3; match to conduit or tubing type and material.

E. Fittings for LFNC:  UL 514B.

2.3 METAL WIREWAYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Cooper B-Line, Inc.

2. Hoffman.

3. Square D; Schneider Electric.

B. Description:  Sheet metal sized and shaped as indicated, NEMA 250, Type [1] [12] [3R], unless otherwise indicated.

C. Fittings and Accessories:  Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

D. Wireway Covers:  Screw-cover type
E. Finish:  Manufacturer's standard enamel finish.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

2.4 SURFACE RACEWAYS

Insert requirements for finish-coat paint color, if applicable, in first paragraph below.  See Division 9 for optional field-finish coats.

A. Surface Metal Raceways:  Galvanized steel with snap-on covers.  Manufacturer's standard enamel finish in color selected by Architect.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

a. Thomas & Betts Corporation.

b. Walker Systems, Inc.; Wiremold Company (The).

c. Wiremold Company (The); Electrical Sales Division.

B. Surface Nonmetallic Raceways:  Two-piece construction, manufactured of rigid PVC with texture and color selected by Architect from manufacturer's standard colors.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

a. Butler Manufacturing Company; Walker Division.

b. Enduro Systems, Inc.; Composite Products Division.

c. Hubbell Incorporated; Wiring Device-Kellems Division.

d. Lamson & Sessions; Carlon Electrical Products.

e. Panduit Corp.

f. Walker Systems, Inc.; Wiremold Company (The).

g. Wiremold Company (The); Electrical Sales Division.
2.5 BOXES, ENCLOSURES, AND CABINETS

A. Sheet Metal Outlet and Device Boxes:  NEMA OS 1.

In first paragraph below, aluminum boxes are suitable for use with steel raceways in most environments.  Type FD is a device box with extra depth.  Many other configurations are available.

B. Cast-Metal Outlet and Device Boxes:  NEMA FB 1, aluminum, Type FD, with gasketed cover.

C. Nonmetallic Outlet and Device Boxes:  NEMA OS 2.

See Editing Instruction No. 2 in the Evaluations for a discussion of floor boxes.

D. Metal Floor Boxes:  Cast or sheet metal, fully adjustable rectangular.

E. Nonmetallic Floor Boxes:  Nonadjustable, round.

F. Small Sheet Metal Pull and Junction Boxes:  NEMA OS 1.

G. Cast-Metal Access, Pull, and Junction Boxes:  NEMA FB 1, cast aluminum with gasketed cover.

Coordinate first paragraph and subparagraphs below with Drawings if hinged cover enclosures other than NEMA 250, Type 1 are required, e.g., very dusty areas, and if consideration should be given to use of NEMA 250, Type 12 enclosures.

H. Hinged-Cover Enclosures:  NEMA 250, Type 1, with continuous-hinge cover with flush latch, unless otherwise indicated.

1. Metal Enclosures:  Steel, finished inside and out with manufacturer's standard enamel.

I. Cabinets:

1. NEMA 250, Type 1, galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

2. Hinged door in front cover with flush latch and concealed hinge.

3. Key latch to match panelboards.

4. Metal barriers to separate wiring of different systems and voltage.

5. Accessory feet where required for freestanding equipment.

PART 3 -  EXECUTION

3.1 RACEWAY APPLICATION

Retain this Article to specify type of raceway to be installed.  Coordinate with conductor and cable wiring methods specified in Division 16 Section "Conductors and Cables" and in other Sections in Divisions 13 and 16.  Do not duplicate information indicated on Drawings, required by NFPA 70, or specified in other Sections in Divisions 13 and 16.  Specify exceptions to requirements.  Verify requirements with authorities having jurisdiction to avoid specifying uses not permitted.  See "Writing Guide" Article in the Evaluations for instructions on editing this Article.

A. Outdoors:  Apply raceway products as specified below, unless otherwise indicated:

1. Exposed Conduit:  Rigid steel conduit.
2. Concealed Conduit, Aboveground:  Rigid steel conduit.

Retain subparagraph below if Project includes small amounts of exterior underground wiring, 600 V and less, and Division 2 Section "Underground Ducts and Utility Structures" is not being used.

3. Underground Conduit:  RNC, Type EPC-80-PVC, direct buried or flexible HDPE directionally bored.
Select first option in first subparagraph below if raceway may be exposed to physical damage.

4. Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  LFMC.
5. Boxes and Enclosures, Aboveground:  NEMA 250, Type 4X stainless steel.

B. Comply with the following indoor applications, unless otherwise indicated:

1. Exposed, Not Subject to Physical Damage:  EMT (except RGS on first floors).
2. Exposed and Subject to Physical Damage:  Rigid steel conduit.  Includes raceways in the following locations:

a. Loading dock.

b. Corridors used for traffic of mechanized carts, forklifts, and pallet-handling units.

c. Mechanical rooms.

3. Concealed in Ceilings and Interior Walls and Partitions:  EMT (except RGS on first floors).
4. Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  LFMC.

5. Damp or Wet Locations:  Rigid steel conduit.

6. Raceways for Optical Fiber or Communications Cable:  EMT (except RGS on first floors).
7. Boxes and Enclosures:  NEMA 250, Type 1, except use NEMA 250, Type 4X, stainless steel in damp or wet locations.

C. Minimum Raceway Size:  3/4-inch (21-mm) trade size.

D. Raceway Fittings:  Compatible with raceways and suitable for use and location.

1. Rigid and Intermediate Steel Conduit:  Use threaded rigid steel conduit fittings, unless otherwise indicated.

3.2 INSTALLATION

A. Comply with NECA 1 for installation requirements applicable to products specified in Part 2 except where requirements on Drawings or in this Article are stricter.

B. Keep raceways at least 6 inches (150 mm) away from parallel runs of flues and steam or hot-water pipes.  Install horizontal raceway runs above water and steam piping.

C. Complete raceway installation before starting conductor installation.

D. Arrange stub-ups so curved portions of bends are not visible above the finished slab.

First paragraph below is more restrictive than NFPA 70, which permits up to four quarter bends in a conduit run.  Retain below for more conservative design, with less stress being placed on wire being pulled in.

E. Install no more than the equivalent of three 90-degree bends in any conduit run except for communications conduits, for which fewer bends are allowed.

F. Conceal conduit and EMT within finished walls, ceilings, and floors, unless otherwise indicated.

G. Raceways Embedded in Slabs:

1. Run conduit larger than 1-inch (27-mm) trade size, parallel or at right angles to main reinforcement.  Where at right angles to reinforcement, place conduit close to slab support.

2. Arrange raceways to cross building expansion joints at right angles with expansion fittings.

Note that some building or local electrical codes may not permit nonmetallic tubing in fire-rated slabs in subparagraph below.

3. Change from ENT to RNC, Type EPC-40-PVC, rigid steel conduit, or IMC before rising above the floor.

Retain first paragraph below to exceed NFPA 70 requirements.  NFPA 70 requires insulated bushings or other smooth rounded entry provisions for conduit terminations at all locations where conductors are No. 4 AWG and larger, regardless of the environment.

H. Raceway Terminations at Locations Subject to Moisture or Vibration:  Use insulating bushings to protect conductors, including conductors smaller than No. 4 AWG.

I. Install pull wires in empty raceways.  Use polypropylene or monofilament plastic line with not less than 200-lb (90-kg) tensile strength.  Leave at least 12 inches (300 mm) of slack at each end of pull wire.

Paragraph and subparagraphs below are applicable for EMT, ENT, FMC, IMC, RMC, and RNC.

J. Raceways for Optical Fiber and Communications Cable:  Install as follows:

1. 3/4-Inch (19-mm) Trade Size and Smaller:  Install raceways in maximum lengths of 50 feet (15 m).

2. 1-Inch (25-mm) Trade Size and Larger:  Install raceways in maximum lengths of 75 feet (23 m).

3. Install with a maximum of two 90-degree bends or equivalent for each length of raceway unless Drawings show stricter requirements.  Separate lengths with pull or junction boxes or terminations at distribution frames or cabinets where necessary to comply with these requirements.

Retain paragraph and subparagraphs below if applicable.

K. Install raceway sealing fittings at suitable, approved, and accessible locations and fill them with listed sealing compound.  For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces.  Install raceway sealing fittings at the following points:

1. Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

2. Where otherwise required by NFPA 70.

Retain paragraph and subparagraphs below unless locations for expansion fittings for PVC conduits are indicated on Drawings.  See Evaluations.

Delete option in first paragraph below if Type AC or MC cable is specified in Division 16 Section "Conductors and Cables" for lighting fixture connection.

L. Flexible Conduit Connections:  Use maximum of 72 inches (1830 mm) of flexible conduit for recessed and semirecessed lighting fixtures, equipment subject to vibration, noise transmission, or movement; and for transformers and motors.

1. Use LFMC in damp or wet locations.

M. Recessed Boxes in Masonry Walls:  Saw-cut opening for box in center of cell of masonry block, and install box flush with surface of wall.

N. Set metal floor boxes level and flush with finished floor surface.

O. Set nonmetallic floor boxes level.  Trim after installation to fit flush with finished floor surface.

3.3 INSTALLATION OF UNDERGROUND CONDUIT

Retain this Article if Project includes small amounts of exterior underground wiring, 600 V and less.  Delete if Division 2 Section "Underground Ducts and Utility Structures" is included in the Project Manual.  See Editing Instruction No. 3 in the Evaluations.

A. Direct-Buried Conduit:

1. Excavate trench bottom to provide firm and uniform support for conduit.  Prepare trench bottom as specified in Division 2 Section "Earthwork" for pipe less than 6 inches (150 mm) in nominal diameter.

2. Install backfill as specified in Division 2 Section "Earthwork."

3. After installing conduit, backfill and compact.  Start at tie-in point, and work toward end of conduit run, leaving conduit at end of run free to move with expansion and contraction as temperature changes during this process.  Firmly hand tamp backfill around conduit to provide maximum supporting strength.  After placing controlled backfill to within 12 inches (300 mm) of finished grade, make final conduit connection at end of run and complete backfilling with normal compaction as specified in Division 2 Section "Earthwork."

Retain one of two subparagraphs below to specify type of stub-ups for direct-buried conduits in Project.

4. Install manufactured duct elbows for stub-ups at poles and equipment and at building entrances through the floor, unless otherwise indicated.  Encase elbows for stub-up ducts throughout the length of the elbow.

5. Install manufactured rigid steel conduit elbows for stub-ups at poles and equipment and at building entrances through the floor.

Retain first two subparagraphs below with either subparagraph above.

a. Couple steel conduits to ducts with adapters designed for this purpose, and encase coupling with 3 inches (75 mm) of concrete.

b. For stub-ups at equipment mounted on outdoor concrete bases, extend steel conduit horizontally a minimum of 60 inches (1500 mm) from edge of equipment pad or foundation.  Install insulated grounding bushings on terminations at equipment.

6. Warning Planks:  Bury warning planks approximately 12 inches (300 mm) above direct-buried conduits, placing them 24 inches (600 mm) o.c.  Align planks along the width and along the centerline of conduit.

3.4 FIRESTOPPING

A. Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly.  Firestopping materials and installation requirements are specified in Division 7 Section "Through-Penetration Firestop Systems."

END OF SECTION 16130

RACEWAYS AND BOXES
16130 - 3

