Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16139 - CABLE TRAYS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes aluminum cable trays and accessories.

1.2 SUBMITTALS

A. Product Data:  Include data indicating dimensions and finishes for each type of cable tray indicated.

B. Shop Drawings:  Show fabrication and installation details of cable trays, including plans, elevations, and sections of components and attachments to other construction elements.  Designate components and accessories, including clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings.

Retain subparagraph and associated subparagraphs below if products are required to withstand seismic loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify product's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

C. Field quality-control reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers in this Article.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Chalfant Manufacturing Company.

2. Cooper B-Line, Inc.

3. Cope, T. J., Inc.; a subsidiary of Allied Tube & Conduit.

4. GS Metals Corp.; GLOBETRAY Products.

5. MONO-SYSTEMS, Inc.

6. MPHusky.

7. PW Industries.

2.2 MATERIALS AND FINISHES

Select one of first two paragraphs and associated subparagraphs below.  See Evaluations for discussion of cable tray materials and finishes.

A. Cable Trays, Fittings, and Accessories:  Aluminum, complying with NEMA VE 1, Aluminum Association's Alloy 6063-T6 for rails, rungs, and cable trays, and Alloy 5052-H32 or Alloy 6061-T6 for fabricated parts; with chromium-zinc, ASTM F 1136 or Type 316 stainless-steel splice-plate fasteners, bolts, and screws.

B. Sizes and Configurations:  Refer to the Cable Tray Schedule on Drawings for specific requirements for types, materials, sizes, and configurations.

1. Center-hanger supports may be used only when specifically indicated.

2.3 CABLE TRAY ACCESSORIES

A. Fittings:  Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.

Select one of four cover options in paragraph below.  If more than one type is required, delete here and indicate on Drawings or in a schedule.  Delete paragraph if only single-rail-type cable tray is used or if cable tray covers are not required.

Delete first paragraph below if not applicable.

B. Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer.

2.4 WARNING SIGNS

Revise size of lettering in first paragraph below to suit 25-foot (7.6-m) viewing distance.

A. Lettering:  1-1/2-inch- (40-mm-) high, black letters on yellow background with legend "WARNING!  NOT TO BE USED AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL."

B. Materials and fastening are specified in Division 16 Section "Electrical Identification."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with recommendations in NEMA VE 2.  Install as a complete system, including all necessary fasteners, hold-down clips, splice-plate support systems, barrier strips, hinged horizontal and vertical splice plates, elbows, reducers, tees, and crosses.

B. Remove burrs and sharp edges from cable trays.

C. Fasten cable tray supports to building structure.
1. Place supports so that spans do not exceed maximum spans on schedules.

2. Construct supports from channel members, threaded rods, and other appurtenances furnished by cable tray manufacturer.  Arrange supports in trapeze or wall-bracket form as required by application.

3. Support bus assembly to prevent twisting from eccentric loading.

4. Manufacture center-hung support, designed for 60 percent versus 40 percent eccentric loading condition, with a safety factor of 3.

5. Locate and install supports according to NEMA FG 1 / NEMA VE 1.

Retain paragraph below if cable tray connects to equipment.

D. Make connections to equipment with flanged fittings fastened to cable tray and to equipment.  Support cable tray independent of fittings.  Do not carry weight of cable tray on equipment enclosure.

Retain first paragraph below if expansion fittings are required.

E. Install expansion connectors where cable tray crosses building expansion joint and in cable tray runs that exceed dimensions recommended in NEMA FG 1 / NEMA VE 1.  Space connectors and set gaps according to applicable standard.

F. Make changes in direction and elevation using standard fittings.

G. Make cable tray connections using standard fittings.

H. Seal penetrations through fire and smoke barriers according to Division 7 Section "Through-Penetration Firestop Systems."

If cable trays are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions or use "repairable" firestop-sealing material.  Include specific firestopping requirements of this Section in a schedule developed in the Division 7 Section referenced in paragraph above.

I. Sleeves for Future Cables:  Install capped sleeves for future cables through firestop-sealed cable tray penetrations of fire and smoke barriers.

J. Workspace:  Install cable trays with enough space to permit access for installing cables.

Retain first paragraph below if systems are mixed.

K. Install barriers to separate cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600, 5000, and 15 000 V.

L. After installation of cable trays is completed, install warning signs in visible locations on or near cable trays.

Retain first two paragraphs below if applicable; these requirements are optional in NEMA VE 2.

M. Install cables only when cable tray installation has been completed and inspected.

N. Fasten cables on horizontal runs with cable clamps or cable ties as recommended by NEMA VE 2.  Tighten clamps only enough to secure the cable, without indenting the cable jacket.  Install cable ties with a tool that includes an automatic pressure-limiting device.

O. On vertical runs, fasten cables to tray every 18 inches (457 mm).  Install intermediate supports when cable weight exceeds the load-carrying capacity of the tray rungs.

P. In existing construction, remove inactive or dead cables from cable tray.

Q. Install covers after installation of cable is completed.

R. Ground cable trays according to manufacturer's written instructions.

Retain paragraph below for metallic cable trays if grounding, in addition to tray metallic path, is desired.

S. Install an insulated equipment grounding conductor with cable tray, in addition to those required by NFPA 70.

3.2 FIELD QUALITY CONTROL

A. After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements.  Perform the following field quality-control survey:

1. Visually inspect cable insulation for damage.  Correct sharp corners, protuberances in cable tray, vibration, and thermal expansion and contraction conditions, which may cause or have caused damage.

2. Verify that the number, size, and voltage of cables in cable tray do not exceed that permitted by NFPA 70.  Verify that communication or data-processing circuits are separated from power circuits by barriers.

3. Verify that there is no intrusion of such items as pipe, hangers, or other equipment that could damage cables.

4. Remove deposits of dust, industrial process materials, trash of any description, and any blockage of tray ventilation.

5. Visually inspect each cable tray joint and each ground connection for mechanical continuity.  Check bolted connections between sections for corrosion.  Clean and retorque in suspect areas.

6. Check for missing or damaged bolts, bolt heads, or nuts.  When found, replace with specified hardware.

7. Perform visual and mechanical checks for adequacy of cable tray grounding; verify that all takeoff raceways are bonded to cable tray.

B. Report results in writing.

END OF SECTION 16139

CABLE TRAYS
16139 - 1

