Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16140 - WIRING DEVICES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

1. Receptacles, receptacles with integral GFCI, and associated device plates.

2. Snap switches and wall-box dimmers.

3. Wall-switch and exterior occupancy sensors.

4.  SEQ CHAPTER \h \r 1Floor service outlets, poke-through assemblies, service poles, and multioutlet assemblies.
B. See Division 16 Section "Voice and Data Communication Cabling" for workstation outlets.

1.2 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  List of legends and description of materials and process used for premarking wall plates.

Retain first paragraph below if products have critical features needing hands-on appraisal.

C. Samples:  One for each type of device and wall plate specified, in each color specified.

D. Operation and Maintenance Data:  For wiring devices to include in all manufacturers' packing label warnings and instruction manuals that include labeling conditions.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.
1.4 COORDINATION

A.  SEQ CHAPTER \h \r 1Receptacles for Owner-Furnished Equipment:  Match plug configurations.
PART 2 -  PRODUCTS

2.1 MANUFACTURERS
A.  SEQ CHAPTER \h \r 1Manufacturers:   SEQ CHAPTER \h \r 1Subject to compliance with requirements, manufacturers offering products that may be incorporated into the work include, but are not limited to, the following:
1. Wiring Devices:

a.  SEQ CHAPTER \h \r 1Bryant Electric, Inc./Hubbell Subsidiary
b.  SEQ CHAPTER \h \r 1Hubbell Incorporated; Wiring Device-Kellems
c.  SEQ CHAPTER \h \r 1Leviton Mfg. Company Inc
d.  SEQ CHAPTER \h \r 1Pass & Seymour/Legrand; Wiring Devices Div.
2.  SEQ CHAPTER \h \r 1Poke-Through, Floor Service Outlets and Telephone/Power Poles:
a.  SEQ CHAPTER \h \r 1Hubbell Incorporated; Wiring Device-Kellems
b.  SEQ CHAPTER \h \r 1Pass & Seymour/Legrand; Wiring Devices Div.
c.  SEQ CHAPTER \h \r 1Square D/Group Schneider NA.
d.  SEQ CHAPTER \h \r 1Thomas & Betts Corporation.
e.  SEQ CHAPTER \h \r 1Wiremold Company (The).
3.  SEQ CHAPTER \h \r 1Wiring Devices for Hazardous (Classified) Locations:
a.  SEQ CHAPTER \h \r 1Crouse-Hinds/Cooper Industries, Inc.; Arrow Hart Wiring Devices.
b.  SEQ CHAPTER \h \r 1EGS/Appleton Electric Company.
c.  SEQ CHAPTER \h \r 1Killark Electric Manufacturing Co./Hubbell Incorporated.
2.2 STRAIGHT BLADE RECEPTACLES

A. Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

B.  SEQ CHAPTER \h \r 1Straight-Blade and Locking Receptacles:  Specification Grade
C.  SEQ CHAPTER \h \r 1GFCI Receptacles:  Straight blade, [feed]non-feed-through type, specification [Hospital] [Heavy-Duty] grade, with integral NEMA WD 6, Configuration 5-20R duplex receptacle; complying with UL 498 and UL 943.  Design units for installation in a 2-3/4-inch- (70-mm-) deep outlet box without an adapter.  Include indicator light that is lighted when device is tripped.
D.  SEQ CHAPTER \h \r 1TVSS Receptacles:  Straight blade, NEMA WD 6, Configuration 5-20R, with integral TVSS in line to ground, line to neutral, and neutral to ground.
1.  SEQ CHAPTER \h \r 1TVSS Components:  Multiple metal-oxide varistors; with a nominal clamp level rating of 500 volts and minimum single transient pulse energy dissipation of 140 J line to neutral, and 70 J line to ground and neutral to ground.
2.  SEQ CHAPTER \h \r 1Active TVSS Indication:  Visual and audible with light visible in face of device to indicate device is "active" or "no longer in service."
3.  SEQ CHAPTER \h \r 1Receptacle Type:  Specification grade.
4.  SEQ CHAPTER \h \r 1Identification:  Distinctive marking on face of device to denote TVSS-type unit.
See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

2.3 SNAP SWITCHES

A. Comply with NEMA WD 1 and UL 20.

B. Switches, 120/277 V, 20 A: Specification Grade, quiet type.
See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

2.4 WALL-BOX DIMMERS

A. Dimmer Switches:  Modular, full-wave, solid-state units with integral, quiet on-off switches, with audible frequency and EMI/RFI suppression filters.

Four-way switching may be added to first paragraph below after verifying availability with manufacturers.

B. Control:  Continuously adjustable slider with single-pole or three-way switching.  Comply with UL 1472.

C. Incandescent Lamp Dimmers:  120 V; control shall follow square-law dimming curve.  On-off switch positions shall bypass dimmer module.  
Use fluorescent lamp dimmer switches in paragraph below with compatible dimming-type ballasts.  Coordinate with Division 16 Section "Interior Lighting."  Use uniform ballast and lamp types to obtain consistent dimming characteristics.

D. Fluorescent Lamp Dimmer Switches:  Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming with low end not greater than 20 percent of full brightness.
2.5 WALL PLATES

A.  SEQ CHAPTER \h \r 1Single and combination types to match corresponding wiring devices.
1.  SEQ CHAPTER \h \r 1Plate-Securing Screws:  Metal with head color to match plate finish.
2.  SEQ CHAPTER \h \r 1Material for Finished Spaces:  [Steel with white baked enamel, suitable for field painting] Smooth, high-impact thermoplastic [0.035-inch- (1-mm-) thick, satin-finished stainless steel] [0.04-inch- (1-mm-) thick, brushed brass with factory polymer finish] [0.05-inch- (1.2-mm-) thick anodized aluminum] [0.04-inch- (1-mm-) thick steel with chrome-plated finish].
3.  SEQ CHAPTER \h \r 1Material for Unfinished Spaces:  Galvanized steel.
4.  SEQ CHAPTER \h \r 1Material for Wet Locations:  [Thermoplastic] Cast aluminum with spring-loaded lift cover, and listed and labeled for use in wet locations.
2.6 FLOOR SERVICE FITTINGS

A.  SEQ CHAPTER \h \r 1Type:  Modular, flush-type [flap-type] [above-floor], dual-service units suitable for wiring method used.
B.  SEQ CHAPTER \h \r 1Compartments:  Barrier separates power from voice and data communication cabling.
C.  SEQ CHAPTER \h \r 1Service Plate:  [Rectangular] Round, [die-cast aluminum] solid brass with satin finish.
D.  SEQ CHAPTER \h \r 1Power Receptacle:  NEMA WD 6, Configuration 5-20R, gray finish, unless otherwise indicated.
E. Extron Audio / Visual Inputs: As indicated on drawings.
F.  SEQ CHAPTER \h \r 1Fire Rating:  Unit is listed and labeled for fire rating of floor-ceiling assembly.
1.  SEQ CHAPTER \h \r 1Closure Plug:  Arranged to close unused 3-inch (75-mm) [4-inch (100-mm)] cored openings and reestablish fire rating of floor.
2.7 SERVICE POLES

A.  SEQ CHAPTER \h \r 1Description:  Factory-assembled and -wired units to extend power and voice and data communication from distribution wiring concealed in ceiling to devices or outlets in pole near floor.
1.  SEQ CHAPTER \h \r 1Poles:  Nominal 2.5-inch- (65-mm-) square cross section, with height adequate to extend from floor to at least 6 inches (150 mm) above ceiling, and with separate channels for power wiring and voice and data communication cabling.
2.  SEQ CHAPTER \h \r 1Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports; with pole foot and carpet pad attachment.
3.  SEQ CHAPTER \h \r 1Finishes:  Manufacturer's standard painted finish and trim combination.
4.  SEQ CHAPTER \h \r 1Wiring:  Sized for minimum of five No. 12 AWG power and ground conductors; and a minimum of four, 4-pair, Category 3 or 5 voice and data communication cables.
5. Modular Furniture Connection:  Flexible whips, end caps, openings with grommets, or other methods for connecting power and communication cables.
2.8 OCCUPANCY SENSORS

Each manufacturer's switch rating is different, but rated design values are generally not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent.

Retain one of two paragraphs and associated subparagraphs below.  Adaptive technology includes the ability to sense and memorize usage patterns in the space and help eliminate false offs.

A. Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 180-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

B. Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Adaptive-technology type, 120/277 V, adjustable time delay up to 20 minutes, 180-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

Retain one of first two paragraphs and associated subparagraphs below for square and near-square rectangular rooms.

C. Long-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 110-degree field of view, with a minimum coverage area of 1200 sq. ft. (111 sq. m).

D. Long-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Dual technology, with both passive-infrared- and ultrasonic-type sensing, 120/277 V, adjustable time delay up to 30 minutes, 110-degree field of view, and a minimum coverage area of 1200 sq. ft. (111 sq. m).

E. Wide-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 150-degree field of view, with a minimum coverage area of 1200 sq. ft. (111 sq. m).

F. Exterior Occupancy Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Description:  Passive-infrared type, 120/277 V, weatherproof, adjustable time delay up to 15 minutes, 180-degree field of view, and 110-foot (34-m) detection range.  Minimum switch rating:  1000-W incandescent, 500-VA fluorescent.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

2.9 FINISHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring device colors.  Coordinate with Drawings.

A. Color:  Wiring device catalog numbers in Section Text do not designate device color.

1. Wiring Devices Connected to Normal Power System:  Ivory unless otherwise indicated or required by NFPA 70 or device listing.

Delete first subparagraph below and edit paragraph and subparagraph above if a separate emergency power system serving wiring devices is not provided.

2. Wiring Devices Connected to Emergency Power System:  Red.
3. TVSS Devices:  Blue.

PART 3 -  EXECUTION

3.1 INSTALLATION

NECA 1 referenced in paragraph below includes device mounting-height requirements.  See "Product Selection and Application Considerations" Article in the Evaluations for device mounting heights in that standard.

A. Comply with NECA 1, including the mounting heights listed in that standard, unless otherwise noted.

See Editing Instruction No. 4 in the Evaluations for timing and sequencing of construction to assist in avoiding contamination of devices during construction.

B. Coordination with Other Trades:

1. Take steps to insure that devices and their boxes are protected.  Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of the boxes.

2. Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

3. Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

4. Install wiring devices after all wall preparation, including painting, is complete.

C. Conductors:

1. Do not strip insulation from conductors until just before they are spliced or terminated on devices.

2. Strip insulation evenly around the conductor using tools designed for the purpose.  Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

3. The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Article 300, without pigtails.

4. Existing Conductors:

a. Cut back and pigtail, or replace all damaged conductors.

b. Straighten conductors that remain and remove corrosion and foreign matter.

c. Pigtailing existing conductors is permitted provided the outlet box is large enough.

D. Device Installation:

1. Replace all devices that have been in temporary use during construction or that show signs that they were installed before building finishing operations were complete.

2. Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

3. Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

4. Connect devices to branch circuits using pigtails that are not less than 6 inches (152 mm) in length.

5. When there is a choice, use side wiring with binding-head screw terminals.  Wrap solid conductor tightly clockwise, 2/3 to 3/4 of the way around terminal screw.

6. Use a torque screwdriver when a torque is recommended or required by the manufacturer.

7. When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

8. Tighten unused terminal screws on the device.

9. When mounting into metal boxes, remove the fiber or plastic washers used to hold device mounting screws in yokes, allowing metal-to-metal contact.

E. Receptacle Orientation:

Retain subparagraph below if the position of the ground pin is important for consistency.  Trade and professional literature is inconsistent in recommending benefits of either orientation.

1. Install ground pin of vertically mounted receptacles up.
F. Device Plates:  Do not use oversized or extra-deep plates.  Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

G. Dimmers:

1. Install dimmers within terms of their listing.

2. Verify that dimmers used for fan speed control are listed for that application.

3. Install unshared neutral conductors on line and load side of dimmers according to manufacturers' device listing conditions in the written instructions.

Coordinate paragraph below with Drawings.

H. Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

3.2 IDENTIFICATION

A. Comply with Division 16 Section "Electrical Identification."

1. Receptacles:  Identify panelboard and circuit number from which served.  Use hot, stamped or engraved machine printing with white-filled lettering on face of plate, and durable wire markers or tags inside outlet boxes.

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

1. Test Instruments:  Use instruments that comply with UL 1436.

2. Test Instrument for Convenience Receptacles:  Digital wiring analyzer with digital readout or illuminated LED indicators of measurement.

B. Tests for Convenience Receptacles:

1. Line Voltage:  Acceptable range is 105 to 132 V.

2. Percent Voltage Drop under 15-A Load:  A value of 6 percent or higher is not acceptable.

3. Ground Impedance:  Values of up to 2 ohms are acceptable.

4. GFCI Trip:  Test for tripping values specified in UL 1436 and UL 943.

5. Using the test plug, verify that the device and its outlet box are securely mounted.

6. The tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems.  Correct circuit conditions, remove malfunctioning units and replace with new, and retest as specified above.

END OF SECTION 16140

WIRING DEVICES
16140 - 1

