Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16145 - LIGHTING CONTROL DEVICES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following lighting control devices:

Adjust list below to suit Project.

1. Outdoor photoelectric switches.

2. Indoor occupancy sensors.

3. Outdoor motion sensors.

4. Emergency shunt relay.

B. See Division 16 Section "Lighting Controls" for low-voltage, manual and programmable lighting control systems.

C. See Division 16 Section "Wiring Devices" for wall-box dimmers, wall-switch occupancy sensors, and manual light switches.

D. See Division 16 Section "Dimming Controls" for architectural dimming system equipment.

1.2 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Field quality-control test reports.

C. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

2.1 OUTDOOR PHOTOELECTRIC SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Lithonia Lighting; Acuity Lighting Group, Inc.

2. Square D; Schneider Electric.

3. TORK.

4. Touch-Plate, Inc.

5. Watt Stopper (The).

Retain one of two paragraphs and associated subparagraphs below.  Light-level range is typical for dusk-to-dawn lighting applications.  Inductive rating for a switch means it is UL tested at 50 percent power factor.

First paragraph describes a device with built-in, metal-oxide-varistor surge protection, selection of contact ratings, and range of adjustments to orient the photocell.  These features allow flexibility in making device suitable for a wide range of mounting and control situations.

Second paragraph describes a device with less-effective surge protection, having a fixed load-breaking contact capacity, and that may be considered for control of a single lighting fixture designed for mounting on fixture.

B. Description:  Solid state, with SPDT dry contacts rated for 1800-VA tungsten or 1000-VA inductive  to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A.

1. Light-Level Monitoring Range:  1.5 to 10 fc (16.14 to 108 lx), with an adjustment for turn-on and turn-off levels within that range, and a directional lens in front of photocell to prevent fixed light sources from causing turn-off.

2. Time Delay:  15-second minimum, to prevent false operation.

3. Surge Protection:  Metal-oxide varistor, complying with IEEE C62.41.1, IEEE C62.41.2, and IEEE 62.45 for Category A1 locations.

4. Mounting:  Twist lock complying with IEEE C136.10, with base-and-stem mounting or stem-and-swivel mounting accessories as required to direct sensor to the north sky exposure.

2.2 INDOOR OCCUPANCY SENSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Hubbell Lighting.

2. Leviton Mfg. Company Inc.

3. Lithonia Lighting; Acuity Lighting Group, Inc.

4. Novitas, Inc.

5. RAB Lighting, Inc.

6. Sensor Switch, Inc.

7. TORK.

8. Watt Stopper (The).

B. General Description:  Wall- or ceiling-mounting, solid-state units with a separate relay unit.

Retain subparagraphs and associated subparagraphs below to specify various types of units required for Project.

1. Operation:  Unless otherwise indicated, turn lights on when covered area is occupied and off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

2. Sensor Output:  Contacts rated to operate the connected relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

3. Relay Unit:  Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

4. Mounting:

a. Sensor:  Suitable for mounting in any position on a standard outlet box.

b. Relay:  Externally mounted through a 1/2-inch (13-mm) knockout in a standard electrical enclosure.

c. Time-Delay and Sensitivity Adjustments:  Recessed and concealed behind hinged door.

5. Indicator:  LED, to show when motion is being detected during testing and normal operation of the sensor.

6. Bypass Switch:  Override the on function in case of sensor failure.

7. Automatic Light-Level Sensor:  Adjustable from 2 to 200 fc (21.5 to 2152 lx); keep lighting off when selected lighting level is present.

C. PIR Type:  Ceiling mounting; detect occupancy by sensing a combination of heat and movement in area of coverage.

Revise coverage area of detectors in subparagraphs below and add detectors with different coverage patterns and features to suit Project.

1. Detector Sensitivity:  Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm).

2. Detection Coverage (Room):  Detect occupancy anywhere in a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

3. Detection Coverage (Corridor):  Detect occupancy within 90 feet (27.4 m) when mounted on a 10-foot- (3-m-) high ceiling.

2.3 OUTDOOR MOTION SENSORS (PIR)

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

1. Bryant Electric; a Hubbell Company.

2. Hubbell Lighting.

3. Lithonia Lighting; Acuity Lighting Group, Inc.

4. Paragon Electric Co.; Invensys Climate Controls.

5. RAB Lighting, Inc.

6. TORK.

7. Watt Stopper (The).

Retain features in paragraph and subparagraphs below applicable to motion sensors for Project.

B. Performance Requirements:  Suitable for operation in ambient temperatures ranging from minus 40 to plus 130 deg F (minus 40 to plus 54 deg C), rated as raintight according to UL 773A.

1. Operation:  Turn lights on when sensing infrared energy changes between background and moving body in area of coverage; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

2. Mounting:

a. Sensor:  Suitable for mounting in any position on a standard outdoor junction box.

b. Relay:  Internally mounted in a standard weatherproof electrical enclosure.

c. Time-Delay and Sensitivity Adjustments:  Recessed and concealed behind hinged door.

3. Bypass Switch:  Override the on function in case of sensor failure.

4. Automatic Light-Level Sensor:  Adjustable from 1 to 20 fc (11 to 215 lx); keep lighting off during daylight hours.

Retain one or both paragraphs below.  Revise coverage area of detectors and add detectors with different coverage patterns and features to suit Project.

C. Detector Sensitivity:  Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm).

D. Detection Coverage:  <Insert coverage area>.

Retain paragraph below for sensor with a built-in switch suitable for operating one or two lamps.  Standard unit for this purpose is typically limited to switching 300 W, such as two 150-PAR lamps.

E. Lighting Fixture Mounted Sensor:  Suitable for switching 300 W of tungsten load at 120- or 277-V ac.

Retain paragraph and subparagraphs below for split unit with wiring between relay and sensor and to specify relay suitable for contactor operation.

F. Individually Mounted Sensor:  Contacts rated to operate the connected relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

1. Relay Unit:  Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

2. Indicator:  LED, to show when motion is being detected during testing and normal operation of the sensor.
2.4 EMERGENCY SHUNT RELAY

Retain this Article for emergency lighting switched by manual, photoelectric, or other automatic switching devices.  Emergency shunt relay will bypass or shunt the manual switch or other control device and turn connected lights on when there is an outage of normal power.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Description:  Normally closed, electrically held relay, arranged for wiring in parallel with manual or automatic switching contacts; complying with UL 924.

2.5 CONDUCTORS AND CABLES

A. Power Wiring to Supply Side of Remote-Control Power Sources:  Not smaller than No. 12 AWG.  Comply with requirements in Division 16 Section "Conductors and Cables."

B. Classes 2 and 3 Control Cable:  Multiconductor cable with stranded-copper conductors not smaller than No. 18 AWG.  Comply with requirements in Division 16 Section "Conductors and Cables."

C. Class 1 Control Cable:  Multiconductor cable with stranded-copper conductors not smaller than No. 14 AWG.  Comply with requirements in Division 16 Section "Conductors and Cables."

PART 3 -  EXECUTION

3.1 SENSOR INSTALLATION

A. Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated.  Do not exceed coverage limits specified in manufacturer's written instructions.

B. When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting sensors to suit actual occupied conditions.  Provide up to two visits to Project during other than normal occupancy hours for this purpose.

3.2 CONTACTOR INSTALLATION

A. Mount electrically held lighting contactors with elastomeric isolator pads, to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

3.3 WIRING INSTALLATION

Coordinate this Article with Drawings.

A. Wiring Method:  Comply with Division 16 Section "Conductors and Cables."  Minimum conduit size shall be 1/2 inch (13 mm).

B. Wiring within Enclosures:  Comply with NECA 1.  Separate power-limited and nonpower-limited conductors according to conductor manufacturer's written instructions.

C. Size conductors according to lighting control device manufacturer's written instructions, unless otherwise indicated.

D. Splices, Taps, and Terminations:  Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

3.4 IDENTIFICATION

A. Identify components and power and control wiring according to Division 16 Section "Electrical Identification."

1. Identify controlled circuits in lighting contactors.

2. Identify circuits or luminaries controlled by photoelectric and occupancy sensors at each sensor.

B. Label time switches and contactors with a unique designation.

3.5 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. After installing time switches and sensors, and after electrical circuitry has been energized, adjust and test for compliance with requirements.

2. Operational Test:  Verify operation of each lighting control device, and adjust time delays.

B. Lighting control devices that fail tests and inspections are defective work.

END OF SECTION 16145

LIGHTING CONTROL DEVICES
16145 - 5

