Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2003 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16441 – SWITCHBOARDS AND DISTRIBUTION BOARDS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL
1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes service and distribution switchboards rated 600 V and less.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. EMI:  Electromagnetic interference.

B. GFCI:  Ground-fault circuit interrupter.

C. RFI:  Radio-frequency interference.

D. RMS:  Root mean square.

E. SPDT:  Single pole, double throw.

1.4 SUBMITTALS

A. Product Data:  For each type of switchboard, overcurrent protective device, transient voltage suppression device, ground-fault protector, accessory, and component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each switchboard and related equipment.

1. Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Enclosure types and details for types other than NEMA 250, Type 1.

b. Bus configuration, current, and voltage ratings.

c. Short-circuit current rating of switchboards and overcurrent protective devices.

Retain first subparagraph below if optional barriers are specified.

d. Descriptive documentation of optional barriers specified for electrical insulation and isolation.

e. Utility company's metering provisions with indication of approval by utility company.

f. Mimic-bus diagram.

Retain first subparagraph below if series rating of overcurrent protective devices is used.

g. UL listing for series rating of installed devices.

h. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph below if mimic bus is specified.

C. Samples:  Representative portion of mimic bus with specified finish, for color selection.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Electrical Supports and Seismic Restraints."

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For testing agency.

Retain first paragraph and subparagraphs below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports including the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Results of failed tests and corrective action taken to achieve test results that comply with requirements.

F. Operation and Maintenance Data:  For switchboards and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 1, include the following:

1. Routine maintenance requirements for switchboards and all installed components.

2. Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

3. Time-current curves, including selectable ranges for each type of overcurrent protective device.

1.5 QUALITY ASSURANCE

If an independent testing agency is required, see Division 1 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use one of first two paragraphs below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor is required to provide services of an independent testing agency in "Field Quality Control" Article in Part 3.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7.

C. Source Limitations:  Obtain switchboards through one source from a single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 1 requirements.

D. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for switchboards including clearances between switchboards and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

F. Comply with NEMA PB 2, "Deadfront Distribution Switchboards."

G. Comply with NFPA 70.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver in sections or lengths that can be moved past obstructions in delivery path.

Delete one of first two paragraphs below or edit to suit Project.

B. Store indoors in clean dry space with uniform temperature to prevent condensation.  Protect from exposure to dirt, fumes, water, corrosive substances, and physical damage.

C. If stored in areas subjected to weather, cover switchboards to provide protection from weather, dirt, dust, corrosive substances, and physical damage.  Remove loose packing and flammable materials from inside switchboards; install electric heating (250 W per section) to prevent condensation.

D. Handle switchboards according to NEMA PB 2.1 and NECA 400.

1.7 PROJECT CONDITIONS

Revise paragraph below to describe specific requirements for moving switchboards into place.  Where appropriate, indicate alterations to existing facilities that may be required to accommodate an indicated delivery path.  Coordinate with Drawings.

A. Installation Pathway:  Remove and replace access fencing, doors, lift-out panels, and structures to provide pathway for moving switchboards into place.

Retain paragraph and subparagraphs below for switchboards installed in typical environmental conditions.  For switchboards installed outdoors or in unusual environmental conditions, revise to indicate minimum ambient temperature and expected humidity range.  See Editing Instruction No. 2 in the Evaluations.

B. Environmental Limitations:  Rate equipment for continuous operation under the following conditions, unless otherwise indicated:

1. Ambient Temperature:  Not exceeding 104 deg F (40 deg C).

2. Altitude:  Not exceeding 6600 feet (2000 m).

Retain paragraph and subparagraphs below or revise to accommodate unusual service conditions that cannot be eliminated.  See Editing Instructions No. 2 and No. 3 in the Evaluations.

C. Service Conditions:  NEMA PB 2, usual service conditions, as follows:

1. Ambient temperatures within limits specified.

2. Altitude not exceeding 6600 feet (2000 m).

Retain paragraph and subparagraphs below if interruption of existing electric service is required.

D. Interruption of Existing Electric Service:  Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

1. Notify Architect, Construction Manager, and Owner no fewer than seven days in advance of proposed interruption of electric service.

2. Indicate method of providing temporary electric service.

3. Do not proceed with interruption of electric service without written permission.

1.8 COORDINATION

Edit first paragraph below for types of construction and encumbrances that affect switchboard installation.

A. Coordinate layout and installation of switchboards and components with other construction including conduit, piping, equipment, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.  Coordinate with Division 16 Section "Fuses" for quantities of spare fuses to be provided.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Potential Transformer Fuses:  Equal to 10 percent of amount installed for each size and type, but no fewer than 2 of each size and type.

2. Control-Power Fuses:  Equal to 10 percent of amount installed for each size and type, but no fewer than 2 of each size and type.

3. Fuses and Fusible Devices for Fused Circuit Breakers:  Equal to 10 percent of amount installed for each size and type, but no fewer than 3 of each size and type.

4. Fuses for Fused Switches:  Equal to 10 percent of amount installed for each size and type, but no fewer than 3 of each size and type.

5. Fuses for Fused Power-Circuit Devices:  Equal to 10 percent of amount installed for each size and type, but no fewer than 3 of each size and type.

6. Indicating Lights:  Equal to 10 percent of amount installed for each size and type, but no fewer than 1 of each size and type.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2.2 MANUFACTURED UNITS

Switchboards described in this Article include service and distribution types most commonly applied.  Select types required for Project from options provided below.  Coordinate with Drawings.  If more than one type is required, identify by Drawing identification number.

Coordinate type of switchboard with types of overcurrent protective devices and with switchboard arrangement and available space.  Consult manufacturer to determine layout requirements.  See Evaluations for further discussion.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. Manufacturers:

1. Eaton Corporation; Cutler-Hammer Products.

2. General Electric Co.; Electrical Distribution & Protection Div.

3. Siemens Energy & Automation, Inc.

4. Square D.

B. Front-Connected, Front-Accessible Switchboard:  Fixed, individually mounted main device, panel-mounted branches, and sections rear aligned.

Coordinate two paragraphs below with Drawings.  Delete rating data if on Drawings.

Retain first paragraph below for projects in seismic areas.  Coordinate with Part 1 "Submittals" Article for submittal of manufacturer's seismic qualification certification.

C. Enclosure:  Steel, NEMA 250, Type 1 (indoors) and type 3R (outdoors). 
D. Enclosure Finish for Outdoor Units:  Factory-applied finish in manufacturer's standard color, undersurfaces treated with corrosion-resistant undercoating.

E. Enclosure Finish for Indoor Units:  Factory-applied finish in manufacturer's standard gray finish over a rust-inhibiting primer on treated metal surface.

Retain paragraph below if required.

F. Barriers:  Between adjacent switchboard sections.

Add internal barriers and extra insulation to isolate energized components, such as buses and vertical sections, if required to protect against damage from arcing ground faults.  See Evaluations for further discussion.

G. Insulation and isolation for main bus of main section and main and vertical buses of feeder sections.

Heaters and controls below, usually specified for outdoor switchboards, are sometimes specified for indoor units.

H. Space Heaters:  Factory-installed electric space heaters of sufficient wattage in each vertical section to maintain enclosure temperature above expected dew point.

Where overcurrent devices are mounted on both sides of a central walk-in corridor, more than one thermostat may be required.

1. Space-Heater Control:  Thermostats to maintain temperature of each section above expected dew point.

2. Space-Heater Power Source:  Transformer, factory installed in switchboard.
Pull sections in paragraph below are often required when incoming supply is beneath switchboard.

I. Bus Transition and Incoming Pull Sections:  Matched and aligned with basic switchboard.

Retain first paragraph below for rear access.

J. Pull Box on Top of Switchboard:

1. Adequate ventilation to maintain temperature in pull box within same limits as switchboard.

Retain first subparagraph below for top-mounted, circuit-breaker removal mechanism.

2. Set back from front to clear circuit-breaker removal mechanism.

3. Removable covers shall form top, front, and sides.  Top covers at rear shall be easily removable for drilling and cutting.

4. Bottom shall be insulating, fire-resistive material with separate holes for cable drops into switchboard.

5. Cable supports shall be arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

K. Buses and Connections:  Three phase, four wire, unless otherwise indicated.

Retain one of three subparagraphs below for main-bus material.

1. Phase- and Neutral-Bus Material:  Hard-drawn copper of 98 percent conductivity with feeder circuit-breaker line connections.

Delete first subparagraph below if front-access sections are specified.

2. Load Terminals:  Insulated, rigidly braced, silver-plated, copper runback bus extensions equipped with pressure connectors for outgoing circuit conductors.  Provide load terminals for future circuit-breaker positions at full ampere rating of circuit-breaker position.

3. Ground Bus:  1/4-by-2-inch- (6-by-50-mm-) minimum-size, hard-drawn copper of 98 percent conductivity, equipped with pressure connectors for feeder and branch-circuit ground conductors.  For busway feeders, extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run.

4. Contact Surfaces of Buses:  Silver plated.

5. Main Phase Buses, Neutral Buses, and Equipment Ground Buses:  Uniform capacity for entire length of switchboard's main and distribution sections.  Provide for future extensions from both ends.

Retain subparagraph below if optional barriers are not specified.

6. Isolation Barrier Access Provisions:  Permit checking of bus-bolt tightness.

Retain one of two subparagraphs below or delete both for three-phase, three-wire systems.

7. Neutral Buses:  100 percent of the ampacity of phase buses, unless otherwise indicated, equipped with pressure connectors for outgoing circuit neutral cables.  Bus extensions for busway feeder neutral bus are braced.

Retain paragraph below for future provisions.

L. Future Devices:  Equip compartments with mounting brackets, supports, bus connections, and appurtenances at full rating of circuit-breaker compartment.

Insulation may not be required by authorities having jurisdiction.  Delete paragraph below unless Project conditions require additional bus insulation.  Uninsulated buses are standard.

M. Bus-Bar Insulation:  Factory-applied, flame-retardant, tape wrapping of individual bus bars or flame-retardant, spray-applied insulation.  Minimum insulation temperature rating: 105 deg C.

2.3 TRANSIENT VOLTAGE SUPPRESSION DEVICES

A. IEEE C62.41, integrally mounted, plug-in-style, solid-state, parallel-connected, sine-wave tracking suppression and filtering modules.

B. Minimum single-impulse current rating shall be as follows:

1. Line to Neutral:  100,000 A.

2. Line to Ground:  100,000 A.

3. Neutral to Ground:  50,000 A.

C. Protection modes shall be as follows:

1. Line to neutral.

2. Line to ground.

3. Neutral to ground.

D. EMI/RFI Noise Attenuation Using 50-ohm Insertion Loss Test:  55 dB at 100 kHz.

Retain first two paragraphs below for panels located at or near Category C locations.  For other locations, delete first paragraph and retain second.

E. Maximum Category C combination wave clamping voltage shall not exceed 1000 V, line to neutral and line to ground on 277/480 V systems.

F. Maximum UL 1449 clamping levels shall not exceed 800 V, line to neutral and line to ground on 277/480 V systems.

G. Withstand Capabilities:  3000 Category C surges with less than 5 percent change in clamping voltage.

Retain optional accessories below to suit Project.

H. Accessories:

1. Form-C contacts, one normally open and one normally closed, for remote monitoring of system operation.  Contacts to reverse position on failure of any surge diversion module.

2. Audible alarm activated on failure of any surge diversion module.

3. Six-digit transient-counter set to total transient surges that deviate from the sine-wave envelope by more than 125 V.

2.4 OVERCURRENT PROTECTIVE DEVICES

Coordinate this Article with schedules and Drawings.

A. Molded-Case Circuit Breaker:  NEMA AB 3, with interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic trip-unit circuit breakers shall have RMS sensing, field-replaceable rating plug, and the following field-adjustable settings:

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

5. Integrally Fused Circuit Breakers:  Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

6. GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

B. Molded-Case Circuit-Breaker Features and Accessories:  Standard frame sizes, trip ratings, and number of poles.

1. Lugs:  Mechanical style, suitable for number, size, trip ratings, and conductor material.

2. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

3. Ground-Fault Protection:  Integrally mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

4. Communication Capability:  Integral communication module with functions and features compatible with energy managment system, specified in Division 15 
5. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at 55 percent of rated voltage.

6. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage with field-adjustable 0.1- to 0.6-second time delay.

7. Auxiliary Contacts:  One SPDT switch with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

8. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

9. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

C. Enclosed, Insulated-Case Circuit Breaker:  Fully rated, encased-power circuit breaker with interrupting capacity rating to meet available fault current.

1. Draw-out circuit-breaker mounting.

2. Two-step, stored-energy closing.

3. Microprocessor-based trip units with interchangeable rating plug, LED trip indicators, and the following field-adjustable settings:

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments with I2t response.

d. Ground-fault pickup level, time delay, and I2t response.

4. Remote trip indication and control.

5. Communication Capability:  Integral communication module with functions and features compatible with energy management system specified in Division 15.

6. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

7. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

Retain voltage in subparagraph below to match control-power supply.

8. Control Voltage:  125-V, ac.

Retain one of first two paragraphs and associated subparagraphs below.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

D. High-Pressure, Butt-Type Contact Switch:  Operating mechanism uses butt-type contacts and a spring-charged mechanism to produce and maintain high-pressure contact when switch is closed.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

Retain one or both of first two subparagraphs below depending on switch applications in Project.  First is for switches with ground-fault protection and for remotely tripped switches.  Second is for manually tripped units.  See Editing Instruction No. 4 in the Evaluations.  Coordinate with Drawings; include notation that identifies electrically tripped and manually tripped switches.

Revise subparagraph below if relay capable of zone-selective interlocking is required.

2.5 INSTRUMENTATION

A. Instrument Transformers:  NEMA EI 21.1, IEEE C57.13, and the following:

1. Potential Transformers:  Secondary voltage rating of 120 V and NEMA accuracy class of 0.3 with burdens of W, X, and Y.

Coordinate first subparagraph below with Drawings and indicate specific accuracy classes and burdens required for each application.

2. Current Transformers:  Ratios shall be as indicated with accuracy class and burden suitable for connected relays, meters, and instruments.

3. Control-Power Transformers:  Dry type, mounted in separate compartments for units larger than 3 kV.

Retain subparagraph below for certain ground-fault protection situations such as double-ended switchboards on four-wire, grounded neutral systems.  Coordinate with Drawings.

4. Current Transformers for Neutral and Ground-Fault Current Sensing:  Connect secondaries to ground overcurrent relays to provide selective tripping of main and tie circuit breaker.  Coordinate with feeder circuit-breaker ground-fault protection.

Delete paragraph and subparagraphs below if conventional analog meter installation is required.

B. Multifunction Digital-Metering Monitor:  Microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Switch-selectable digital display of the following values with maximum accuracy tolerances as indicated:

a. Phase Currents, Each Phase:  Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase:  Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase:  Plus or minus 1 percent.

d. Megawatts:  Plus or minus 2 percent.

e. Megavars:  Plus or minus 2 percent.

f. Power Factor:  Plus or minus 2 percent.

g. Frequency:  Plus or minus 0.5 percent.

h. Megawatt Demand:  Plus or minus 2 percent; demand interval programmable from 5 to 60 minutes.

i. Accumulated Energy, Megawatt Hours:  Plus or minus 2 percent.  Accumulated values unaffected by power outages up to 72 hours.

2. Mounting:  Display and control unit flush or semiflush mounted in instrument compartment door.

Delete remaining paragraphs and subparagraphs below if all metering functions can be provided by multifunction digital meters specified above.

C. Ammeters, Voltmeters, and Power-Factor Meters:  ANSI C39.1.

1. Meters:  4-inch (100-mm) diameter or 6 inches (150 mm) square, flush or semiflush, with antiparallax 250-degree scales and external zero adjustment.

2. Voltmeters:  Cover an expanded-scale range of nominal voltage plus 10 percent.

D. Instrument Switches:  Rotary type with off position.

1. Voltmeter Switches:  Permit reading of all phase-to-phase voltages and, where a neutral is indicated, phase-to-neutral voltages.

2. Ammeter Switches:  Permit reading of current in each phase and maintain current-transformer secondaries in a closed-circuit condition at all times.

E. Feeder Ammeters:  2-1/2-inch- (64-mm-) minimum size with 90- or 120-degree scale.  Meter and transfer device with an off position, located on overcurrent device door for indicated feeder circuits only.

Revise demand interval and other meter characteristics in first paragraph below to suit Project.

F. Watt-Hour Meters:  Flush or semiflush type, rated 5 A, 120 V, 3 phase, 3 wire, with 3 elements, 15-minute-indicating-demand register, and provision for testing and adding pulse initiation.

G. Recording Demand Meter:  Usable as totalizing relay or as indicating and recording maximum-demand meter with 15-minute interval.  Meter shall count and control a succession of pulses entering two channels.  House in drawout, back-connected case arranged for semiflush mounting.

2.6 CONTROL POWER

A. Control Circuits:  120 V, supplied through secondary disconnecting devices from control-power transformer.

Retain first paragraph below if required.  See "Application Considerations" Article in the Evaluations for further discussion.

B. Control Wiring:  Factory installed, with bundling, lacing, and protection included.  Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

2.7 ACCESSORY COMPONENTS AND FEATURES

Retain paragraph below for drawout circuit breakers.

A. Furnish accessory set including tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

Retain paragraph below for circuit breakers with solid-state trip devices.

B. Furnish portable test set to test functions of solid-state trip devices without removal from switchboard.  Include relay and meter test plugs suitable for testing switchboard meters and switchboard class relays.

Retain one or both of first two paragraphs below for installations with drawout circuit breakers.

C. Furnish one portable, floor-supported, roller-based, elevating carriage arranged for movement of circuit breakers in and out of compartments for present and future circuit breakers.

D. Furnish overhead circuit-breaker lifting device, mounted at top front of switchboard, with hoist and lifting yokes matching each drawout circuit breaker.

E. Spare-Fuse Cabinet:  Suitably identified, wall-mounted, lockable, compartmented steel box or cabinet.  Arrange for wall mounting.

Retain paragraph below for installations in humid environments.

F. Fungus Proofing:  Permanent fungicidal treatment for switchboard interior, including instruments and instrument transformers.

2.8 IDENTIFICATION

Coordinate this Article with Drawings.

A. Mimic Bus:  Continuously integrated mimic bus factory applied to front of switchboard.  Arrange in single-line diagram format, using symbols and letter designations consistent with final mimic-bus diagram.  Coordinate mimic-bus segments with devices in switchboard sections to which they are applied.  Produce a concise visual presentation of principal switchboard components and connections.

Revise paragraph below to require other types of presentation media if factory-painted mimic bus is not desirable.

B. Presentation Media:  Painted graphics in color contrasting with background color to represent bus and components, complete with lettered designations.

PART 3 -  EXECUTION

3.1 PROTECTION

A. Temporary Heating:  Apply temporary heat to maintain temperature according to manufacturer's written instructions.

3.2 EXAMINATION

A. Examine elements and surfaces to receive switchboards for compliance with installation tolerances and other conditions affecting performance.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.3 INSTALLATION

A. Install switchboards and accessories according to NEMA PB 2.1 and NECA 40.

B. Install and anchor switchboards level on concrete bases, 4-inch (100-mm) nominal thickness.  Concrete base is specified in Division 16 Section "Electrical Supports and Seismic Restraints," and concrete materials and installation requirements are specified in Division 3.

Revise four subparagraphs below based on installed equipment.  Indicate dowel-rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For switchboards, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to switchboards.

C. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

D. Operating Instructions:  Frame and mount the printed basic operating instructions for switchboards, including control and key interlocking sequences and emergency procedures.  Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic.  Mount on front of switchboards.

E. Install overcurrent protective devices, transient voltage suppression devices, and instrumentation.

1. Set field-adjustable switches and circuit-breaker trip ranges.

Retain paragraph below if spare-fuse cabinets are specified in Part 2 "Accessory Components and Features" Article.

F. Install spare-fuse cabinet.

3.4 IDENTIFICATION

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section "Electrical Identification."

B. Switchboard Nameplates:  Label each switchboard compartment with engraved metal or laminated-plastic nameplate mounted with corrosion-resistant screws.

3.5 FIELD QUALITY CONTROL

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each switchboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

Retain one of three paragraphs below.

B. Testing Agency:  Engage a qualified testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

C. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs and associated subparagraphs below with either of last two paragraphs above and edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

1. Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Sections 7.1, 7.5, 7.6, 7.9, 7.10, 7.11, and 7.14 as appropriate.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3. Perform the following infrared scan tests and inspections and prepare reports:

a. Initial Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switchboard.  Remove front panels so joints and connections are accessible to portable scanner.

b. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each switchboard 11 months after date of Substantial Completion.

c. Instruments, Equipment, and Reports:

1) Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

2) Prepare a certified report that identifies switchboards included and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.6 CLEANING

A. On completion of installation, inspect interior and exterior of switchboards.  Remove paint splatters and other spots.  Vacuum dirt and debris; do not use compressed air to assist in cleaning.  Repair exposed surfaces to match original finish.

3.7 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain switchboards, overcurrent protective devices, instrumentation, and accessories.  Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 16441

SWITCHBOARDS AND DISTRIBUTION BOARDS
16441 - 12

