Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


MASTERSPEC Short Form Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16521 - EXTERIOR LIGHTING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Exterior luminaires with lamps and ballasts.

2. Luminaire-mounted photoelectric relays.

3. Poles and accessories.

B. See Division 16 Section "Interior Lighting" for exterior luminaires normally mounted on exterior surfaces of buildings.

1.2 STRUCTURAL ANALYSIS CRITERIA FOR POLE SELECTION

Retain this Article if manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4.  Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in Exterior Lighting Device Schedule or details on Drawings.  See Editing Instruction No. 1 in the Evaluations.

A. Dead Load:  Weight of luminaire and its horizontal and vertical supports and supporting structure, applied as stated in AASHTO LTS-4.

Delete paragraph below if Project is outside the area shown in AASHTO LTS-4, Figure 1.2.3.

B. Ice Load:  Load of 3 lbf/sq. ft. (143.6 Pa), applied as stated in AASHTO LTS-4.

See Editing Instruction No. 2 in the Evaluations for discussion of wind-load calculations.

C. Wind Load:  Pressure of wind on pole and luminaire, calculated and applied as stated in AASHTO LTS-4.
1. Wind speed for calculating wind load for poles 50 feet (15 m) or less in height is 130 mph (209 km/h).

1.3 SUBMITTALS

A. Product Data:  For each luminaire, pole, and support component, arranged in order of lighting unit designation.  Include data on features, accessories, and finishes.

Retain paragraph below if foundation-mounted poles are indicated.

B. Shop Drawings:  Include anchor-bolt templates keyed to specific poles and certified by manufacturer.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with IEEE C2, "National Electrical Safety Code."

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

Edit this Article with other Part 2 articles or with Exterior Lighting Device Schedule on Drawings in which manufacturers and products are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers," "Manufacturers," and "Basis-of-Design Product" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

B. Basis of Design Product:  The design of each item of exterior luminaire and its support is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by another manufacturer.

2.2 LUMINAIRES, GENERAL REQUIREMENTS

A. Luminaires shall comply with UL 1598 and be listed and labeled for installation in wet locations by an NRTL acceptable to authorities having jurisdiction.

Retain first paragraph below if some lighting units or luminaires are indicated to have Type I, II, III, IV, or V distribution pattern in Exterior Lighting Device Schedule or details on Drawings.

B. Comply with IESNA RP-8 for parameters of lateral light distribution patterns indicated for luminaires.

C. Metal Parts:  Free of burrs and sharp corners and edges.

D. Sheet Metal Components:  Corrosion-resistant aluminum, unless otherwise indicated.  Form and support to prevent warping and sagging.

E. Housings:  Rigidly formed, weather- and light-tight enclosures that will not warp, sag, or deform in use.  Provide filter/breather for enclosed luminaires.

F. Doors, Frames, and Other Internal Access:  Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools.  Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position.  Doors shall be removable for cleaning or replacing lenses.  Designed to disconnect ballast when door opens.

G. Exposed Hardware Material:  Stainless steel.

H. Plastic Parts:  High resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

Retain first paragraph below if one or more luminaires require partial shielding of light output to avoid light trespass or to meet other requirements.  Coordinate with Exterior Lighting Device Schedule on Drawings.

I. Light Shields:  Metal baffles, factory installed and field adjustable, arranged to block light distribution to indicated portion of normally illuminated area or field.

J. Reflecting surfaces shall have minimum reflectance as follows, unless otherwise indicated:

1. White Surfaces:  85 percent.

2. Specular Surfaces:  83 percent.

3. Diffusing Specular Surfaces:  75 percent.

K. Lenses and Refractors Gaskets:  Use heat- and aging-resistant resilient gaskets to seal and cushion lenses and refractors in luminaire doors.

Revise paragraph below to include custom colors.  Coordinate custom-color requirements for luminaires with those for poles and other luminaire support requirements.

L. Luminaire Finish:  Manufacturer's standard paint applied to factory-assembled and -tested luminaire before shipping.  Where indicated, match finish process and color of pole or support materials.

Retain paragraph below when luminaire material is steel that is not to be field painted and is not required to match finish of pole or support materials.

M. Factory-Applied Finish for Steel Luminaires:  Color as selected by Architect.  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

Retain paragraph below when luminaire material is aluminum that is not to be field painted and is not required to match finish of pole or support materials.

N. Factory-Applied Finish for Aluminum Luminaires:  Color shall be black.  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

2.3 LUMINAIRE-MOUNTED PHOTOELECTRIC RELAYS

A. Comply with UL 773 or UL 773A.

B. Contact Relays:  Factory mounted, single throw, designed to fail in the on position, and factory set to turn light unit on at 1.5 to 3 fc (16 to 32 lx) and off at 4.5 to 10 fc (48 to 108 lx) with 15-second minimum time delay. Relay shall have directional lens in front of photocell to prevent artificial light sources from causing false turnoff.

1. Relay with locking-type receptacle shall comply with NEMA C136.10.

2. Adjustable window slide for adjusting on-off set points.

2.4 FLUORESCENT BALLASTS AND LAMPS

See Editing Instruction No. 5 in the Evaluations for discussion of low-temperature application of fluorescent luminaires, lamps, and ballasts.

A. Low-Temperature Ballast Capability:  Rated by its manufacturer for reliable starting and operation of indicated lamp(s) at temperatures 0 deg F (minus 18 deg C) and higher.

B. Ballast Characteristics:

1. Power Factor:  90 percent, minimum.

2. Sound Rating: A.

See Evaluations for discussion of harmonic distortion in first subparagraph below.

3. Total Harmonic Distortion Rating:  Less than 10 percent.

4. Electromagnetic Ballasts:  Comply with ANSI C82.1, energy-saving, high power factor, Class P, automatic-reset thermal protection.

5. Case Temperature for Compact Lamp Ballasts:  65 deg C, maximum.

6. Transient-Voltage Protection:  Comply with IEEE C62.41 Category A or better.

C. Low-Temperature Lamp Capability:  Rated for reliable starting and operation with ballast provided at temperatures 0 deg F (minus 18 deg C) and higher.

Low-mercury lamps in paragraph below may not be available in all lamp categories.  Specifying low-mercury lamps may change the color temperature.  Consult manufacturers.

D. Fluorescent Lamps:  Low-mercury type.  Comply with the EPA's toxicity characteristic leaching procedure test; shall yield less than 0.2 mg of mercury per liter when tested according to NEMA LL 1.

2.5 BALLASTS FOR HID LAMPS

A. Comply with ANSI C82.4 and UL 1029 and capable of open-circuit operation without reduction average life.  Include the following features, unless otherwise indicated:

1. Ballast Circuit:  Constant-wattage autotransformer or regulating high-power-factor type.

2. Minimum Starting Temperature:  Minus 22 deg F (Minus 30 deg C).

3. Normal Ambient Operating Temperature:  104 deg F (40 deg C).

Retain subparagraph below if ballasts are required to be fused.  See Editing Instruction No. 4 in the Evaluations for discussion of ballast fusing.

4. Ballast Fuses:  One in each ungrounded power supply conductor.  Voltage and current ratings as recommended by ballast manufacturer.

2.6 HID LAMPS

A. Metal-Halide Lamps:  ANSI C78.1372, with a minimum CRI 65 and color temperature 4000 K.

B. Pulse-Start, Metal-Halide Lamps:  Minimum CRI 65, and color temperature 4000 K.

C. Ceramic, Pulse-Start, Metal-Halide Lamps:  Minimum CRI 80 , and color temperature 4000 K.

2.7 POLES AND SUPPORT COMPONENTS, GENERAL REQUIREMENTS

A. Structural Characteristics:  Comply with AASHTO LTS-4.

Retain two subparagraphs below if retaining Part 1 "Structural Analysis Criteria for Pole Selection" Article and manufacturer is responsible for selecting poles and other luminaire support components and certifying them to suit wind, ice, and other load conditions as expressed in AASHTO LTS-4.  Delete if structural considerations have been applied by the design team in selecting "basis-of-design" or proprietary pole products, and these products have been identified in Exterior Lighting Device Schedule or details on Drawings.  See Editing Instruction No. 1 in the Evaluations.

1. Wind-Load Strength of Poles:  Adequate at indicated heights above grade without failure, permanent deflection, or whipping in steady winds of speed indicated in Part 1 "Structural Analysis Criteria for Pole Selection" Article, with a gust factor of 1.3.

Retain subparagraph below to help ensure that poles are stiff enough to avoid excessive flexure and vibration.  Alternatively, add requirements for minimum pole wall thickness and other parameters.  See Editing Instruction No. 6 in the Evaluations.

2. Strength Analysis:  For each pole, multiply the actual equivalent projected area of luminaires and brackets by a factor of 1.1 to obtain the equivalent projected area to be used in pole selection strength analysis.

B. Luminaire Attachment Provisions:  Comply with luminaire manufacturers' mounting requirements.  Use stainless-steel fasteners and mounting bolts, unless otherwise indicated.

C. Mountings, Fasteners, and Appurtenances:  Corrosion-resistant items compatible with support components.

1. Materials:  Shall not cause galvanic action at contact points.

2. Anchor Bolts, Leveling Nuts, Bolt Caps, and Washers:  Hot-dip galvanized after fabrication, unless stainless-steel items are indicated.

3. Anchor-Bolt Template:  Plywood or steel.

D. Concrete Pole Foundations:  Cast in place, with anchor bolts to match pole-base flange.  Concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

Retain one or both paragraphs below to suit Project.

E. Power-Installed Screw Foundations:  Factory fabricated by pole manufacturer, with structural steel complying with ASTM A 36/A 36M and hot-dip galvanized according to ASTM A 123/A 123M; and with top-plate and mounting bolts to match pole base flange and strength required to support pole, luminaire, and accessories.

F. Breakaway Supports:  Frangible breakaway supports, tested by an independent testing agency acceptable to authorities having jurisdiction, according to AASHTO LTS-4.

2.8 STEEL POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Comply with ASTM A 500, Grade B, carbon steel with a minimum yield of 46,000 psig (317 MPa); 1-piece construction up to 40 feet (12 m) in height with access handhole in pole wall.

1. Shape:  Round, tapered or straight.

2. Mounting Provisions:  Butt flange for bolted mounting on foundation or breakaway support.

B. Steel Mast Arms:  Single-arm type, continuously welded to pole attachment plate.  Material and finish same as pole.

Indicate span and rise of mast arms in paragraph above and luminaire brackets in first paragraph below on Drawings.  Delete paragraph above and first paragraph and subparagraphs below if items are adequately described in Exterior Lighting Device Schedule or details on Drawings.

C. Brackets for Luminaires:  Detachable, cantilever, without underbrace.

1. Adapter fitting welded to pole and bracket, then bolted together with stainless steel bolts.

2. Cross Section:  Tapered oval, with straight tubular end section to accommodate luminaire.

3. Match pole material and finish.

D. Pole-Top Tenons:  Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

E. Steps:  Fixed steel, with nonslip treads, positioned for 15-inch (381-mm) vertical spacing, alternating on opposite sides of pole; first step at elevation 10 feet (3 m) above finished grade.

F. Grounding and Bonding Lugs:  Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Division 16 Section "Grounding and Bonding," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

G. Cable Support Grip:  Wire-mesh type with rotating attachment eye, sized for diameter of cable and rated for a minimum load equal to weight of supported cable times a 5.0 safety factor.

Retain any combination of three paragraphs below that applies to steel poles or other steel support components for this Project.  Specify field-painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field-applied coats.

H. Prime-Coat Finish:  Manufacturer's standard prime-coat finish ready for field painting.

I. Galvanized Finish:  After fabrication, hot-dip galvanize complying with ASTM A 123/A 123M.

Retain paragraph above for plain galvanized finish; retain paragraph below for factory-painted finish.

J. Factory-Painted Finish:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.  Color shall be as selected by Architect.

2.9 ALUMINUM POLES

See Editing Instruction No. 6 in the Evaluations for discussion of pole flexure and vibration resistance.

A. Poles:  Seamless, extruded structural tube complying with ASTM B 429, Alloy 6063-T6 with access handhole in pole wall.

B. Pole-Top Tenons:  Fabricated to support luminaire or luminaires and brackets indicated, and securely fastened to pole top.

C. Grounding and Bonding Lugs:  Welded 1/2-inch (13-mm) threaded lug, complying with requirements in Division 16 Section "Grounding and Bonding," listed for attaching grounding and bonding conductors of type and size listed in that Section, and accessible through handhole.

Revise paragraph and subparagraphs below to suit Project or delete if items are adequately described in Exterior Lighting Device Schedule or details on Drawings.  Indicate span and rise of luminaire brackets on Drawings.

D. Brackets for Luminaires:  Detachable, with pole and adapter fittings of cast aluminum.  Adapter fitting welded to pole and bracket, then bolted together with stainless-steel bolts.

1. Tapered oval cross section, with straight tubular end section to accommodate luminaire.

2. Finish:  Same as pole and luminaire.
Retain one of two paragraphs below.  Specify field-painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field-applied coats.

E. Prime-Coat Finish:  Manufacturer's standard prime-coat finish ready for field painting.

F. Aluminum Finish:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.  Color shall black.

2.10 POLE ACCESSORIES

Revise this Article to suit Project, safety codes, and luminaire servicing methods.  Add requirement for removable steps if necessary.  Coordinate with Exterior Lighting Device Schedule on Drawings.

A. Duplex Receptacle:  120 V, 20 A in a weatherproof assembly complying with Division 16 Section "Wiring Devices" for ground-fault circuit-interrupter type.

1. Recessed, [12 inches (300 mm)]  above pole base.

2. Nonmetallic polycarbonate plastic or reinforced fiberglass cover that when mounted results in NEMA 250, Type 4X enclosure.

3. With cord opening.

4. With lockable hasp and latch that complies with OSHA lockout and tag-out requirements.

B. Minimum 1800-W transformer, protected by replaceable fuses, mounted behind access cover.

Coordinate two paragraphs below with "Breakaway Supports" Paragraph in Part 2 "Poles and Support Components, General Requirements" Article.

C. Base Covers:  Manufacturers' standard metal units, arranged to cover pole's mounting bolts and nuts.  Finish same as pole.

PART 3 -  EXECUTION

3.1 LUMINAIRE INSTALLATION

A. Install lamps in each luminaire.

B. Fasten luminaire to indicated structural supports.

Retain subparagraph below if seismic restraint is required by local code or authorities having jurisdiction.  See Evaluations.

1. Use fastening methods and materials selected to resist seismic forces defined for the application and approved by manufacturer.

C. Adjust luminaires that require field adjustment or aiming.  Include adjustment of photoelectric device to prevent false operation of relay by artificial light sources.
3.2 POLE INSTALLATION

Retain first paragraph below if luminaire alignment for desired light distribution depends on alignment of pole.

A. Align pole foundations and poles for optimum directional alignment of luminaires and their mounting provisions on the pole.

B. Clearances:  Maintain the following minimum horizontal distances of poles from surface and underground features, unless otherwise indicated on Drawings:

1. Fire Hydrants and Storm Drainage Piping:  [60 inches (1520 mm)].
2. Water, Gas, Electric, Communication, and Sewer Lines:  [10 feet (3 m)].

See Evaluations for structural- and soil- engineering coordination.

C. Concrete Pole Foundations:  Set anchor bolts according to anchor-bolt templates furnished by pole manufacturer.  Concrete materials, installation, and finishing requirements are specified in Division 3 Section "Cast-in-Place Concrete."

D. Foundation-Mounted Poles:  Mount pole with leveling nuts, and tighten top nuts to torque level recommended by pole manufacturer.

Retain first subparagraph below if seismic restraint is required by local code or authorities having jurisdiction.  See Evaluations.

1. Use anchor bolts and nuts selected to resist seismic forces defined for the application and approved by manufacturer.

2. Grout void between pole base and foundation.  Use nonshrink or expanding concrete grout firmly packed to fill space.

3. Install base covers, unless otherwise indicated.

4. Use a short piece of 1/2-inch- (13-mm-) diameter pipe to make a drain hole through grout.  Arrange to drain condensation from interior of pole.

Retain one of two paragraphs and associated subparagraphs below for embedded poles and coordinate with Drawings.

For projects in seismic areas, retain first paragraph below to minimize possible concentration of horizontal forces during seismic events where poles or pole foundations meet the finished grade.

E. Poles and Pole Foundations Set in Concrete Paved Areas:  Install poles with minimum of 6-inch- (150-mm-) wide, unpaved gap between the pole or pole foundation and the edge of adjacent concrete slab.  Fill unpaved ring with pea gravel to a level 1 inch (25 mm) below top of concrete slab.

F. Raise and set poles using web fabric slings (not chain or cable).

3.3 BOLLARD LUMINAIRE INSTALLATION

A. Align units for optimum directional alignment of light distribution.

Retain paragraph below if bollards require protection from damage at base due to landscaping maintenance or snow removal operations.  Coordinate with Drawings.

B. Install on concrete base with top [4 inches (100 mm)] above finished grade or surface at bollard location.  Cast conduit into base, and shape base to match shape of bollard base.  Finish by troweling and rubbing smooth.  Concrete materials, installation, and finishing are specified in Division 3 Section "Cast-in-Place Concrete."

3.4 INSTALLATION OF INDIVIDUAL GROUND-MOUNTING LUMINAIRES

A. Install on concrete base with top [4 inches (100 mm)] above finished grade or surface at luminaire location.  Cast conduit into base, and finish by troweling and rubbing smooth.  Concrete materials, installation, and finishing are specified in Division 3 Section "Cast-in-Place Concrete."

3.5 CORROSION PREVENTION

A. Aluminum:  Do not use in contact with earth or concrete.  When in direct contact with a dissimilar metal, protect aluminum by insulating fittings or treatment.

B. Steel Conduits:  Comply with Division 16 Section "Raceways and Boxes."  In concrete foundations, wrap conduit with 0.010-inch- (0.254-mm-) thick, pipe-wrapping plastic tape applied with a 50 percent overlap.

3.6 GROUNDING

Coordinate first paragraph and subparagraphs below with Drawings.

A. Ground metal poles and support structures according to Division 16 Section "Grounding and Bonding."

1. Install grounding electrode for each pole, unless otherwise indicated.

2. Install grounding conductor pigtail in the base for connecting luminaire to grounding system.
B. Ground nonmetallic poles and support structures according to Division 16 Section "Grounding and Bonding."

1. Install grounding electrode for each pole.

2. Install grounding conductor and conductor protector.

3. Ground metallic components of pole accessories and foundations.

END OF SECTION 16521

EXTERIOR LIGHTING
16521 - 8

