Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2003 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16950 - LIGHTNING PROTECTION
PART 1 -  GENERAL
1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes lightning protection for buildings and building elements.

1.3 SUBMITTALS

A. Product Data: For air terminals and mounting accessories.

B. Shop Drawings: Detail lightning protection system, including air-terminal locations, conductor routing and connections, and bonding and grounding provisions. Include indications for use of raceway and data on how concealment requirements will be met.

C. Qualification data for firms and persons specified in "Quality Assurance" Article to demonstrate their capabilities and experience. Include data on listing or certification by nationally recognized testing laboratory (NRTL) or trade association.

D. Certification, signed by Contractor, that roof adhesive for air terminals is approved by manufacturers of both the terminal assembly and the single-ply membrane roofing material.

E. Field inspection reports indicating compliance with specified requirements.

1.4 QUALITY ASSURANCE

A. Installer Qualifications: Engage and experienced installer who is NRTL listed or who is certified by LPI as a Master Installer/Designer.

B. Listing and Labeling: As defined in NFPA 780, Article 2-2, "Definitions."

C. Provide UL Master Label.

D. Provide LPI certification of system.

E. Provide ETL Master Label indicating system complies with specified requirements.

1.5 COORDINATION

A. Coordinate installation of lightning protection with installation of other building systems and components, including electrical wiring, supporting structures and building materials, metal bodies requiring bonding to lightning protection components, and building finishes.

B. Coordinate installation of air terminals attached to single-membrane roof systems with roofing manufacturer and installer.
PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

1. A-C Lightning Security, Inc.

2. Automatic Lightning Protection.

3. Harger Lightning Protection, Inc.

4. Heary Bros. Lightning Protection Co. Inc.

5. Independent Protection Company, Inc.

6. Robbins Lightning, Incorporated.

7. Thompson Lightning Protection, Inc.

2.2 LIGHTING PROTECTION SYSTEM COMPONENTS

A. Comply with UL 96.

B. Roof-Mounting Air Terminals: NFPA Class I, copper, solid, unless otherwise indicated.

C. Stack-Mounting Air Terminals: Solid copper.

D. Ground Rods, Ground Loop Conductors, and Concrete-Encased Electrodes: Comply with Division 16 Section "Grounding and Bonding" and standards referenced in this Section.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install lightning protection components and systems according to UL 96A, LPI-175, and NFPA 780.

B. Install conductors with direct paths from air terminals to ground connections. Avoid sharp bends and narrow loops.

C. Conceal following conductors:

1. System conductors.

2. Down conductors

3. Interior conductors

4. Conductors within normal view from exterior locations grade within 200 feet of building.

5. Notify Architect at least 48 hours in advance of inspection before concealing lightning protection components.

D. Cable Connections: Use approved exothermic-welded connections for all conductor splices and connections between conductors and other components, except those above single-ply membrane roofing.

3.2 CORROSION PROTECTION
A. Do not combine materials that can form an electrolytic couple that will accelerate corrosion in the presence of moisture unless moisture is permanently excluded from junction of such materials.

B. Use conductors with protective coatings where conditions would cause deterioration or corrosion of conductors.

3.3 FIELD QUALITY CONTROL

A. Periodic Inspections: Engage an LPI inspector to perform periodic inspections during construction and at its completion, according to LPI-177.

B. UL Inspection: Apply for inspection by UL as required to obtain a UL Master Label for system.

END OF SECTION 16950

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

LIGHTNING PROTECTION 
16950 - 3

