Copyright 2006 AIA
MASTERSPEC Full Length
05/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 133423 - FABRICATED STRUCTURES
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes prefabricated [steel] [aluminum] control booths.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 03 Section "Cast-in-Place Concrete" for installing anchor bolts.

2. Division 05 Section "Metal Fabrications" for pipe bollards to protect control booths.

Retain this article if term in paragraph below remains after this Section has been edited.

C. ADA-ABA Accessibility Guidelines:  U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA) Accessibility Guidelines for Buildings and Facilities; Architectural Barriers Act (ABA) Accessibility Guidelines."

1.3 PERFORMANCE REQUIREMENTS

Consider deleting this article if control booths are located within parking garage.

A. Structural Performance:  Control booths shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated according to [ASCE/SEI 7] <Insert requirement>:

Insert requirements under each set of performance criteria below to suit Project.  Many manufacturers offer booths that are designed to withstand 50-lbf/sq. ft. (2.4-kPa) live load and 30-lbf/sq. ft. (1.4-kPa) wind load.  Consult a structural engineer, experienced in engineering control booths of type indicated, to quantify design loads applicable to Project.  Verify compliance with codes.  See Evaluations.

Retain subparagraphs below if design loads and load combinations are not indicated on Drawings.

1. Dead Loads:  <Insert loads>.

2. Live Loads:  <Insert loads>.

3. Roof Loads:  <Insert loads>.

4. Snow Loads:  <Insert loads>.

5. Seismic Loads:  <Insert loads>.

6. Wind Loads:  <Insert loads>.

7. <Insert loads or load combinations>.

8. Deflection Limits:  Design framing system to withstand design loads without deflections greater than the following:

a. <Insert deflection limits>.

B. Thermal Movements:  Allow for thermal movements from ambient and surface temperature changes.  Base calculations on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values in subparagraph below (for aluminum in particular) are suitable for most of the U.S.

1. Temperature Change (Range):  [120 deg F (67 deg C), ambient; 180 deg F (100 deg C)] <Insert temperature range>, material surfaces.

1.4 SUBMITTALS

First four paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for control booths.

B. Shop Drawings:  For control booths.  Include plans, elevations, sections, details, and attachments to other work.

C. Samples for Initial Selection:  For control booths with factory-applied color finishes.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above.

D. Samples for Verification:  For exposed finishes, in manufacturer's standard sizes.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

E. Delegated-Design Submittal:  For control booths indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

F. Welding certificates.

G. Maintenance Data:  For control booths to include in maintenance manuals.

H. Warranty:  Sample of special warranty.

1.5 QUALITY ASSURANCE

Retain "Welding Qualifications" Paragraph below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.

A. Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel."

2. AWS D1.2/D1.2M, "Structural Welding Code - Aluminum."

3. AWS D1.3, "Structural Welding Code - Sheet Steel."

Retain requirements in first paragraph below for accessible control booths.  See Evaluations for discussion on accessibility requirements for control booths.

B. Regulatory Requirements:  Comply with applicable provisions in [the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines] [and] [ICC/ANSI A117.1].

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Safety Glazing Products:  Category II materials complying with testing requirements in 16 CFR 1201.

Retain subparagraph below if applicable.  Not all manufacturers participate in third-party testing programs.

1. Subject to compliance with requirements, obtain safety glazing products permanently marked with certification label of [SGCC or another certification agency] [or] [manufacturer] acceptable to authorities having jurisdiction.

Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

E. Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

1.6 COORDINATION

A. Coordinate installation of anchorages for control booths.  Furnish setting drawings, templates, and directions for installing anchorages, including sleeves, concrete inserts, anchor bolts, and items with integral anchors that are to be embedded in concrete or masonry.  Deliver such items to Project site in time for installation.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair finish or replace wall panels that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for control booths with manufacturers listed in Part 2 articles.

1. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MATERIALS

A. Aluminum:  Alloy and temper recommended by aluminum producer and manufacturer for type of use and finish indicated, and as follows:

1. Sheet:  ASTM B 209 (ASTM B 209M).

2. Extruded Shapes:  ASTM B 221 (ASTM B 221M).

3. Rolled Tread Plate:  ASTM B 632/B 632M, Alloy 6061-T4 or Alloy 6061-T6.

B. Zinc-Coated (Galvanized) Steel Sheet:  ASTM A 653/A 653M, commercial quality, G90 (Z275) coating designation; mill phosphatized.

C. Galvanized, Rolled Steel Tread Plate:  ASTM A 786/A 786M, rolled from steel plate complying with ASTM A 572/A 572M, Grade 55 (380); hot-dip galvanized according to ASTM A 123/A 123M.

D. Steel Structural Tubing:  ASTM A 500, Grade B.

E. Steel Plates, Shapes, and Bars:  ASTM A 36/A 36M.

F. Steel Mechanical Tubing:  ASTM A 513, welded steel mechanical tubing.

G. Zinc-Coated (Galvanized) Steel:  Hot-dip galvanized according to ASTM A 123/A 123M.

H. Stainless-Steel Sheet:  ASTM A 666, Type 304.

I. Plastic Laminate:  NEMA LD 3, HGS or HGL grade.

J. Plywood:  DOC PS 1, Exterior grade.

K. Particleboard:  ANSI A208.1, Grade M-2.

L. Clear Float Glass:  ASTM C 1036, Type I, Class 1, Quality q3.

M. Clear Tempered Float Glass:  ASTM C 1048, Kind FT, Condition A, Type I, Class 1, and Quality q3.

Revise first paragraph below if insulating glass is required to be thicker.

N. Insulating Glass:  Units complying with ASTM E 774 for Class CBA and consisting of two lites of 2.5-mm-thick clear float glass and dehydrated air space, with a total overall unit thickness of 7/16 inch (11 mm) and with manufacturer's standard dual seal.

O. Ballistics-Resistant Glazing:  Comply with requirements specified in Division 08 Section "Security Glazing."

P. Anchorages:  Anchor bolts; [hot-dip galvanized according to ASTM A 153/A 153M or ASTM F 2329] [stainless steel].

2.2 PREFABRICATED CONTROL BOOTHS, GENERAL

Manufacturers' control booths and their components are available in a range of styles, shapes, configurations, and options, in both standard and custom designs.  Revise this article and subsequent articles, which include the most common construction, to suit Project.

Custom units can be designed with exterior wall finishes of stucco, aluminum composite panels, fiberglass panels, raised-rib metal panels, or other materials or of face brick, as specified in Division 04 Section "Unit Masonry." Interior wall finishes can be fiberglass-reinforced panels or gypsum board.

A. General:  Provide a complete, integrated set of mutually dependent components that form a completely assembled, prefabricated control booth, ready for installation on Project site.

1. Building Style:  [Standard square corners] [Radius corners] [Round corners] [Butt-glazed corners] [Wraparound type, with single rounded building end] [Wraparound type, with both building ends rounded] [As indicated on Drawings].

2. Doors:  [Sliding door on one side] [Sliding doors on both sides] [Swinging door on back] [As indicated on Drawings].

Revise first paragraph below to suit Project.  Manufacturers also offer tinted glass, clear and tinted polycarbonate, and acrylic glazing.  Most manufacturers offer ballistics-resistant glazing in UL Levels 1 through 3.  See the Evaluations in Division 08 Section "Security Windows."

B. Windows:  Extruded-aluminum sash frames glazed with [6-mm-thick, clear tempered glass] [clear insulating glass] [ballistics-resistant glazing, UL 752 Level <Insert number>].

1. Frame Finish:  [Mill] [Clear anodic].

2. Provide insect screens for each operable window.

3. Provide galvanized-steel security screens for each window.

4. Corner Shape:  [Square] [Round].

Vertical sliding windows are also available but are less common because of the possibility that they may inadvertently slide down.  Manufacturers also provide horizontal sliding windows as part of door assemblies.

C. Horizontal Sliding Windows:  Extruded-aluminum sash frames glazed with 3-mm-thick, clear tempered float glass.  Equip windows with cam locks, weather stripping, and [stainless-steel] [nylon] ball-bearing rollers.

1. Frame Finish:  [Mill] [Clear anodic].

2. Provide insect screens for each operable window.

3. Corner Shape:  [Square] [Round].

Insert requirements for ticket windows in first paragraph below if needed.

D. Work Counters:  Full width of control booth, reinforced; with 16-inch- (406-mm-) wide [storage] [cash] drawer below each counter, and an access opening for electrical cords at[ each] rear corner of counter.

1. Material:  [0.078-inch- (1.98-mm-) thick, stainless-steel sheet] [0.079-inch (2.01-mm) nominal-thickness, galvanized-steel sheet] [1/2-inch- (13-mm-) thick particleboard with plastic-laminate finish].

2. Depth:  [22 inches (559 mm)] [20 inches (508 mm)] [18 inches (457 mm)].

If required, revise first paragraph below for three-phase service.

E. Electrical Power Service:  125-A, 120/240-V ac, single-phase, three-wire [load center, with no fewer than four open circuits] [service with 8-16 circuit-breaker panel]; located under one end of work counter.  Run copper wiring in 1/2-inch (13-mm) EMT conduit.

1. Provide [one] <Insert number> 120-V[ ground-fault circuit interrupter (GFCI)] power receptacle(s).

Revise first paragraph below to include track lighting or exterior lighting fixtures and incandescent, halogen, or quartz lamps if required.  Include motion detectors, timers, and photoelectric controls for exterior lighting if required.

F. Lighting Fixtures:  [One] [Two] ceiling-mounted fluorescent lighting fixture(s), 48 inches (1219 mm) long, with acrylic lens and two 40-W lamps[ in each fixture].  Provide single-pole switch mounted adjacent to door to control lighting fixture.

Revise first paragraph below if heat pump is required.  Verify availability with manufacturers.

G. Heating Unit:  [Wall] [Roof]-mounted, thermostatically controlled, 110-V, 1500-W electric heater with fan-forced operation and with capacity of not less than 5000 Btu/h (1465 W).  Enclose in enameled-steel cabinet[ and mount under work counter].

H. Cooling Unit:  [Wall] [Roof]-mounted, thermostatically controlled air conditioner with cooling capacity of not less than [13,500 Btu/h (3956 W)] <Insert value>.  Enclose in enameled-steel cabinet.

In paragraph below, insert requirements for preplumbed interior restrooms if needed.

I. Accessories:  Provide the following for each control booth:

1. Through-wall transaction drawers[ and speaking apertures] complying with requirements specified in Division 08 Section "Security Windows."

2. Antifatigue mats.

3. Exterior stainless-steel counter.

4. [Floor] [Wall-mounted] safe.

5. Signage:  <Insert requirements>.

6. Ventilation fan.

7. Intercom.

8. Traffic control lights.

2.3 PREFABRICATED STEEL CONTROL BOOTHS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AustinMohawk and Company, Inc.

2. B.I.G. Enterprises, Inc.

3. Canada Kiosk; an NRB company.

4. Delta Scientific Corporation.

5. Keystone Structures, Inc.

6. Little Buildings, Inc.

7. Mardan Fabricators.

8. Parking Booth Company, Inc.

9. Par-Kut International, Inc.

10. Porta-King Building Systems.

11. <Insert manufacturer's name>.

C. Structural Framework:  Fabricated from 2-by-2-by-0.075-inch (50-by-50-by-1.90-mm) steel structural or mechanical tubing.  Connect framework by welding.

Retain one of first three paragraphs below.

Revise first paragraph below to suit booth design, which varies among manufacturers.  4-inch- (102-mm-) high base is typical for exterior applications; 3-inch- (76-mm-) high base is often used for interior or sheltered applications.

D. Base/Floor Assembly:  [4-inch- (102-mm-)] [3-inch- (76-mm-)] high assembly consisting of perimeter frame welded to structural framework of booth.  Fabricate frame from 2-by-4-inch (51-by-102-mm) galvanized-steel structural tubing; 0.108-inch (2.74-mm) nominal-thickness, C-shaped, galvanized-steel sheet channels; or galvanized structural-steel angles.  Include anchor clips fabricated from 1/4-inch- (6-mm-) thick galvanized-steel plate, predrilled and welded to exterior of integral floor frame.

Retain one of three subparagraphs below.  Tread plate in first subparagraph does not require a separate subfloor.

1. Finished Floor:  0.108-inch (2.74-mm) nominal-thickness, galvanized, rolled steel tread plate.

2. Subfloor and Finished Floor:  Assembly consisting of 0.079-inch (2.01-mm) nominal-thickness, galvanized-steel sheet underside with rigid insulation core; covered by 0.125-inch- (3.18-mm-) thick, aluminum rolled tread plate; with overall assembly thickness of 2 inches (51 mm).

3. Subfloor and Finished Floor:  Assembly consisting of [one] [two] layer(s) of 3/4-inch- (19-mm-) thick plywood or oriented strand board with [0.125-inch- (3.18-mm-) thick, aluminum rolled tread plate] [vinyl composition flooring] [carpeting].

Retain one of first two paragraphs below to eliminate raised step into control booth, making it accessible to people with disabilities.

E. Base/Floor Assembly:  No perimeter frame, with finished floor fabricated from 0.108-inch (2.74-mm) nominal-thickness, galvanized, rolled steel tread plate.

F. Base/Floor Assembly:  No perimeter frame, with surface of supporting concrete base as finished floor.

First option in first paragraph below is most common.

G. Wall Panel Assembly:  Assembly consisting of exterior face panel fabricated from 0.079-inch (2.01-mm) nominal-thickness, galvanized-steel sheet; and interior face panel fabricated from [0.064-inch (1.63-mm)] [0.052-inch (1.32-mm)] nominal-thickness, galvanized-steel sheet; with [2-inch- (51-mm-)] [3-inch- (76-mm-)] <Insert dimension> thick, rigid fiberglass or polystyrene board insulation in cavity between exterior and interior face panels.

1. Thermal Resistance Value (R-Value):  [R-7] <Insert R-value>.

Revise first paragraph below to suit Project.  Acoustical ceiling tile is also available.  Canopies and downspouts are often omitted on interior and sheltered applications, and scuppers are often used instead of downspouts. If needed, insert requirements for gable, hip, mansard, vaulted, and dome roof/ceiling assemblies.

H. Flat Roof/Ceiling Assembly:  Consisting of exterior roof panels, interior ceiling panels, and insulation between exterior and interior panels; sloped to drain at booth perimeter.

1. Exterior Roof Panel:  Fabricated from [0.079-inch (2.01-mm)] [0.064-inch (1.63-mm)] nominal-thickness, galvanized-steel sheet; with [painted finish] [EPDM membrane], continuously welded seams, and full-perimeter gutter.

2. Interior Ceiling Panel:  Fabricated from 0.079-inch (2.01-mm) nominal-thickness, galvanized-steel sheet; with fiberglass insulation in cavity between ceiling and roof.

a. Thermal Resistance Value (R-Value):  [R-17] <Insert R-value>.

Retain both subparagraphs above or first subparagraph below.

3. Insulated Exterior/Interior Panel:  Fabricated from [0.028-inch (0.71-mm) nominal-thickness, galvanized-steel] [0.032-inch- (0.81-mm-) thick, aluminum] sheet faces and expanded-foam insulation core.

a. Thermal Resistance Value (R-Value):  [R-17] <Insert R-value>.

Flush canopies are often used for booths located within parking garages or under overhangs.  Oversized overhangs, up to 6 feet (1.8 m), are also available.  Verify availability with manufacturers.

4. Canopy Fascia:  Fabricated from 0.079-inch (2.01-mm) nominal-thickness, galvanized-steel sheet, of [manufacturer's standard design] [custom design indicated on Drawings].

a. Height:  [6 inches (152 mm)] [8 inches (203 mm)] <Insert dimension>.

b. Overhang:  [3 inches (76 mm) beyond] [<Insert dimension> beyond] [Flush with] face of walls below.

5. Downspouts:  Integral, extending 3 inches (76 mm) beyond booth walls.

6. Roof scuppers.

7. Rooftop finial.

Standard commercial hollow-metal swinging, ballistics-resistant swinging, and ballistics-resistant sliding doors can also be included instead of or in addition to doors in first two paragraphs below.  Verify availability with manufacturers.

I. Sliding Door:  Top suspended from aluminum track with ball-bearing rollers; 1-3/4 inches (44 mm) thick; tubular-frame design fabricated from [clear-anodized aluminum] [galvanized steel]; with top half of door glazed.  Equip door with deadlock, lock support, guide hardware, and full weather stripping.

1. Glazing:  [Fixed] [Horizontal sliding] unit with 6-mm-thick, clear tempered float glass.

2. Deadlock:  Mortised, laminated-hook bolt type with removable cylinder capable of being master keyed.

J. Swinging Door:  1-3/4 inches (44 mm) thick; tubular-frame design fabricated from [clear-anodized aluminum] [galvanized steel]; with top half of door glazed.  Equip door with deadlock, three butt hinges, closer, and full weather stripping.

1. Glazing:  [Fixed] [Horizontal sliding] unit with 6-mm-thick, clear tempered float glass.

2. Deadlock:  Mortised, with lever handle and removable cylinder capable of being master keyed.

K. Finish:  Finish exposed metal surfaces, including structural framework, walls, canopy, and ceiling with rust-inhibitive primer and one finish coat of industrial air-dry [acrylic] [polyurethane] enamel.

1. Color:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

2.4 PREFABRICATED ALUMINUM CONTROL BOOTHS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AustinMohawk and Company, Inc.

2. Keystone Structures, Inc.

3. Mardan Fabricators.

4. Portafab Corporation.

5. Porta-King Building Systems.

6. Starrco.

7. <Insert manufacturer's name>.

C. Structural Framework:  Fabricated from 2-by-2-by-0.125-inch (51-by-51-by-3.18-mm) aluminum tubing, channel, angle, or tee extrusions; with [clear] [color] anodic finish.  Connect framework with[ exposed] mechanical fasteners.

Retain one of first two paragraphs below.

Revise first paragraph below to suit booth design, which varies among manufacturers.  4-inch- (102-mm-) high base is typical for exterior applications; 3-inch- (76-mm-) high base is often used for interior or sheltered applications.

D. Base/Floor Assembly:  4-inch- (102-mm-) high assembly consisting of perimeter frame welded to structural framework of booth.  Fabricate frame from 2-by-4-by-0.125-inch (51-by-102-by-3.18-mm) aluminum tubing or aluminum angles.  Include anchor clips fabricated from 1/4-inch- (6-mm-) thick aluminum, predrilled and welded to exterior of integral floor frame.

Retain one of two subparagraphs below.

1. Subfloor and Finished Floor:  Assembly consisting of 0.032-inch- (0.81-mm-) thick, aluminum sheet underside, plywood and rigid insulation core; covered by 0.125-inch- (3.18-mm-) thick, aluminum rolled tread plate; with overall assembly thickness of 2 inches (51 mm).

2. Subfloor and Finished Floor:  Assembly consisting of [one] [two] layer(s) of 3/4-inch- (19-mm-) thick plywood or oriented strand board with [0.125-inch- (3.18-mm-) thick, aluminum rolled tread plate] [vinyl composition flooring] [carpeting].

Retain first paragraph below to eliminate raised step into control booth, making it accessible to people with disabilities.

E. Base/Floor Assembly:  No perimeter frame, with surface of supporting concrete base as finished floor.

Revise first paragraph below to suit Project.  Wall panel assemblies vary considerably among manufacturers; custom fiberglass exterior panels and hardboard interior finish panels are also available.

F. Wall Panel Assembly:  Assembly consisting of exterior face panel fabricated from [0.032-inch- (0.81-mm-)] [0.063-inch- (1.60-mm-)] thick aluminum sheet, and interior face panel fabricated from [0.032-inch- (0.81-mm-)] [0.050-inch- (1.27-mm-)] thick aluminum sheet; with 2-inch- (51-mm-) thick, polystyrene or polyisocyanurate board insulation in cavity between exterior and interior face panels.

1. Thermal Resistance Value (R-Value):  [R-7] <Insert R-value>.

Revise first paragraph below to suit Project.  Acoustical ceiling tile is also available.  Canopies and downspouts are often omitted on interior and sheltered applications, and scuppers are often used instead of downspouts.

G. Flat Roof/Ceiling Assembly:  Consisting of exterior roof panels, interior ceiling panels, and insulation between exterior and interior panels; sloped to drain at booth perimeter.

1. Exterior Roof Panel:  Fabricated from 0.032-inch- (0.81-mm-) thick aluminum sheet with protective plastic sheet finish and full-perimeter gutter.

2. Interior Ceiling Panel:  Fabricated from 0.125-inch- (3.18-mm-) thick hardboard; with polyisocyanurate board insulation in cavity between ceiling and roof.

a. Thermal Resistance Value (R-Value):  [R-19] <Insert R-value>.

Retain both subparagraphs above or first subparagraph below.

3. Insulated Exterior/Interior Panel:  Fabricated from [0.032-inch- (0.81-mm-) thick, aluminum] [0.021-inch (0.53-mm) nominal-thickness, galvanized-steel] sheet faces and expanded-foam insulation core.

a. Thermal Resistance Value (R-Value):  [R-19] <Insert R-value>.

Flush canopies are often used for booths located within parking garages or under overhangs.  Oversized overhangs, up to 6 feet (1.8 m), are also available.  Verify availability with manufacturers.

4. Canopy Fascia:  Fabricated from 0.063-inch- (1.60-mm-) thick aluminum sheet, of [manufacturer's standard design] [custom design indicated on Drawings].

a. Height:  [6 inches (152 mm)] [8 inches (203 mm)] <Insert dimension>.

b. Overhang:  [3 inches (76 mm) beyond] [<Insert dimension> beyond] [Flush with] face of walls below.

5. Downspouts:  Integral, extending 3 inches (76 mm) beyond booth walls.

6. Roof scuppers.

7. Rooftop finial.

Standard commercial hollow-metal swinging, ballistics-resistant swinging, and ballistics-resistant sliding doors can also be included instead of or in addition to doors in first two paragraphs below.  Verify availability with manufacturers.

H. Sliding Door:  Top suspended from aluminum track with ball-bearing rollers; 1-3/4 inches (44 mm) thick; tubular-frame design fabricated from aluminum matching exterior and interior wall panels; with top half of door glazed and with extruded-aluminum door frame.  Equip door with deadlock, lock support, guide hardware, and full weather stripping.

1. Glazing:  [Fixed] [Horizontal sliding] unit with 6-mm-thick, clear tempered float glass.

2. Deadlock:  Mortised, laminated-hook bolt type with removable cylinder capable of being master keyed.

I. Swinging Door:  1-3/4 inches (44 mm) thick; tubular-frame design fabricated from aluminum matching exterior and interior wall panels; with top half of door glazed and with extruded-aluminum door frame.  Equip door with deadlock, three butt hinges, closer, and full weather stripping.

1. Glazing:  [Fixed] [Horizontal sliding] unit with 6-mm-thick, clear tempered float glass.

2. Deadlock:  Mortised, with lever handle and removable cylinder capable of being master keyed.

J. Finish:  Finish exposed metal surfaces, including structural framework, walls, canopy, and ceiling with [clear anodizing] [color anodizing] [baked enamel or powder coat].

1. Color:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

2.5 FABRICATION

A. Fabricate control booths completely in factory.

B. Preglaze windows and doors at factory.

C. Prewire control booths at factory, ready for connection to service at Project site.

D. Fabricate control booths with [forklift pockets in base of booth] [removable lifting eye centered in roof].

Retain paragraph below for accessible control booths.  Requirements may vary; verify with authorities having jurisdiction.  See Evaluations.

E. Accessible Control Booths:  Where indicated to be accessible, fabricate control booths as follows:

1. Provide service windows located no higher than 34 inches (865 mm) above exterior grade.

2. Provide door opening with minimum 32-inch (813-mm) clear width.

3. Provide minimum 60-inch (1525-mm) clear turning spacing within the booth.

4. Provide minimum 27-inch (685-mm) clearance beneath interior work surfaces.  Locate work surfaces 28 inches (710 mm) minimum and 34 inches (865 mm) maximum above the floor.

5. Locate controls and operable parts no lower than 15 inches (381 mm) and no higher than 48 inches (1219 mm) above the floor where reach is unobstructed.  Where side reach is obstructed, locate controls and operable parts no lower than 15 inches (381 mm) and no higher than 46 inches (1219 mm) above the floor.

2.6 GENERAL FINISH REQUIREMENTS

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

B. Appearance of Finished Work:  Noticeable variations in same piece are not acceptable.  Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

2.7 FINISHES

A. [Steel] [and] [Galvanized-Steel] Factory Finish:  Immediately after cleaning and pretreating, apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

2.8 ALUMINUM FINISHES

Retain finishes in this article to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.

Retain one of two options in first paragraph below.  Class II finish is standard with many manufacturers; Class I finish is heavy anodized.  Verify availability with manufacturers selected.

A. Clear Anodic Finish:  AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in first paragraph below.  Verify availability with manufacturers selected.

B. Color Anodic Finish:  AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

1. Color:  [Light bronze] [Medium bronze] [Dark bronze] [Black] <Insert color>.

Options in subparagraph above are examples only and may vary in color range and availability among manufacturers.  Retain one or delete all and retain one of two options in subparagraph below.

2. Color:  [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities].

Paragraph below references AAMA standard for pigmented organic coating on extrusions and panels.

C. Baked-Enamel or Powder-Coat Finish:  AAMA 2603 except with a minimum dry film thickness of 1.5 mils (0.04 mm).  Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

B. Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Revise this article if installing control booths on raised structures.

A. Install control booths according to manufacturer's written instructions.

Retain first paragraph below for accessible control booths.

B. Accessible Control Booths:  Install with interior floor surface at same elevation as adjacent paved surfaces.

C. Set control booths plumb and aligned.  Level baseplates true to plane with full bearing on concrete bases.

D. Fasten control booths securely to [cast-in anchor bolts] [concrete bases with expansion anchors].

E. Connect electrical power service to power distribution system according to requirements specified in Division 26 Sections.

3.3 ADJUSTING

A. Adjust doors, operable windows, and hardware to operate smoothly, easily, properly, and without binding.  Confirm that locks engage accurately and securely without forcing or binding.

B. Lubricate hardware and other moving parts.

C. After completing installation, inspect exposed finishes and repair damaged finishes.

END OF SECTION 133423

	FABRICATED STRUCTURES
	133423 - 1



