Copyright 2005 AIA
MASTERSPEC Full Length
08/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 02240 - DEWATERING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes construction dewatering.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 1 Section "[Construction Progress Documentation] [Photographic Documentation]" for recording preexisting conditions and dewatering system progress.

2. Division 2 Section "Excavation Support and Protection" for shoring, bracing, and sheet piling of excavations.

3. Division 2 Section "Earthwork" for excavating, backfilling, site grading, and for site utilities.

4. Division 2 Section "Subdrainage" for permanent foundation wall, underfloor, and footing drainage.

If allowances apply to Work of this Section, insert brief article here to alert Contractor and reference appropriate Division 1 Section for specific details.

1.3 PERFORMANCE REQUIREMENTS

A. Dewatering Performance:  Design, furnish, install, test, operate, monitor, and maintain dewatering system of sufficient scope, size, and capacity to control hydrostatic pressures and to lower, control, remove, and dispose of ground water and permit excavation and construction to proceed on dry, stable subgrades.

Revise paragraph above and first subparagraph below to follow customary practice in Project's location or if Contractor is not permitted by authorities having jurisdiction to assume responsibility for design.

1. Delegated Design:  Design dewatering system, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

2. Continuously monitor and maintain dewatering operations to ensure erosion control, stability of excavations and constructed slopes, that excavation does not flood, and that damage to subgrades and permanent structures is prevented.

3. Prevent surface water from entering excavations by grading, dikes, or other means.

4. Accomplish dewatering without damaging existing buildings, structures, and site improvements adjacent to excavation.

5. Remove dewatering system when no longer required for construction.

1.4 SUBMITTALS

First paragraph below is defined in Division 1 Section "Submittal Procedures" as an "Action Submittal."

A. Shop Drawings:  For dewatering system.  Show arrangement, locations, and details of wells and well points; locations of risers, headers, filters, pumps, power units, and discharge lines; and means of discharge, control of sediment, and disposal of water.

1. Include layouts of piezometers and flow-measuring devices for monitoring performance of dewatering system.

2. Include a written plan for dewatering operations including control procedures to be adopted if dewatering problems arise.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if design responsibilities have been delegated to Contractor.

B. Delegated-Design Submittal:  For dewatering system indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For qualified [Installer] [land surveyor] [and] [professional engineer].

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

D. Field quality-control reports.

E. Other Informational Submittals:

Usually retain subparagraph below for determining effect of dewatering system on permanent construction.

1. [Photographs] [or] [Videotape]:  Show existing conditions of adjoining construction and site improvements that might be misconstrued as damage caused by dewatering operations.

1.5 QUALITY ASSURANCE

Delete first paragraph below if a list of prequalified dewatering specialist installers is included in bidding documents for the Project.

A. Installer Qualifications:  An experienced installer that has specialized in [design of dewatering systems and ]dewatering work.

B. Regulatory Requirements:  Comply with governing EPA notification regulations before beginning dewatering.  Comply with hauling and disposal regulations of authorities having jurisdiction.

C. Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

Retain subparagraphs below if additional requirements are necessary; include information about conference.

1. Review methods and procedures related to dewatering including, but not limited to, the following:

a. Inspection and discussion of condition of site to be dewatered including coordination with temporary erosion control measures and temporary controls and protections.

b. Geotechnical report.

c. Proposed site clearing and excavations.

d. Existing utilities and subsurface conditions.

e. Coordination for interruption, shutoff, capping, and continuation of utility services.

f. Construction schedule.  Verify availability of Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

g. Testing and monitoring of dewatering system.

h. <Insert agenda items>.

1.6 PROJECT CONDITIONS

Retain first paragraph below if interruption of existing utility service is required.

A. Interruption of Existing Utilities:  Do not interrupt any utility serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of utility.

2. Do not proceed with interruption of utility without [Architect's] [Construction Manager's] [Owner's] written permission.

If office practice differs from first paragraph and subparagraphs below, revise to suit Project or delete.

B. Project-Site Information:  A geotechnical report has been prepared for this Project and is available for information only.  The opinions expressed in this report are those of geotechnical engineer and represent interpretations of subsoil conditions, tests, and results of analyses conducted by geotechnical engineer.  Owner will not be responsible for interpretations or conclusions drawn from this data.

1. Make additional test borings and conduct other exploratory operations necessary for dewatering.

2. The geotechnical report is [included] [referenced] elsewhere in the Project Manual.

C. Survey Work:  Engage a qualified land surveyor or professional engineer to survey adjacent existing buildings, structures, and site improvements, establishing exact elevations at fixed points to act as benchmarks.  Clearly identify benchmarks and record existing elevations.

1. During dewatering, regularly resurvey benchmarks, maintaining an accurate log of surveyed elevations for comparison with original elevations.  Promptly notify Architect if changes in elevations occur or if cracks, sags, or other damage is evident in adjacent construction.

PART 2 -  PRODUCTS (Not Used)

PART 3 -  EXECUTION

3.1 PREPARATION

A. Protect structures, utilities, sidewalks, pavements, and other facilities from damage caused by settlement, lateral movement, undermining, washout, and other hazards created by dewatering operations.

1. Prevent surface water and subsurface or ground water from entering excavations, from ponding on prepared subgrades, and from flooding site and surrounding area.

2. Protect subgrades and foundation soils from softening and damage by rain or water accumulation.

B. Install dewatering system to ensure minimum interference with roads, streets, walks, and other adjacent occupied and used facilities.

1. Do not close or obstruct streets, walks, or other adjacent occupied or used facilities without permission from Owner and authorities having jurisdiction.  Provide alternate routes around closed or obstructed traffic ways if required by authorities having jurisdiction.

C. Provide temporary grading to facilitate dewatering and control of surface water.

D. Monitor dewatering systems continuously.

E. Promptly repair damages to adjacent facilities caused by dewatering.

F. Protect and maintain temporary erosion and sedimentation controls, which are specified in [Division 1 Section "Temporary Facilities and Controls"] [Division 2 Section "Site Clearing"] during dewatering operations.

3.2 INSTALLATION

A. Install dewatering system utilizing wells, well points, or similar methods complete with pump equipment, standby power and pumps, filter material gradation, valves, appurtenances, water disposal, and surface-water controls.

1. Space well points or wells at intervals required to provide sufficient dewatering.

2. Use filters or other means to prevent pumping of fine sands or silts from the subsurface.

B. Before excavating below ground-water level, place system into operation to lower water to specified levels.  Operate system continuously until drains, sewers, and structures have been constructed and fill materials have been placed or until dewatering is no longer required.

C. Provide an adequate system to lower and control ground water to permit excavation, construction of structures, and placement of fill materials on dry subgrades.  Install sufficient dewatering equipment to drain water-bearing strata above and below bottom of foundations, drains, sewers, and other excavations.

1. Do not permit open-sump pumping that leads to loss of fines, soil piping, subgrade softening, and slope instability.

D. Reduce hydrostatic head in water-bearing strata below subgrade elevations of foundations, drains, sewers, and other excavations.

Retain one option in subparagraph below or revise to suit Project.  Depth in first option will suffice for many soil conditions.  Review with geotechnical engineer.

1. Maintain piezometric water level a minimum of [24 inches (600 mm)] [60 inches (1500 mm)] <Insert depth> below surface of excavation.

E. Dispose of water removed by dewatering in a manner that avoids endangering public health, property, and portions of work under construction or completed.  Dispose of water and sediment in a manner that avoids inconvenience to others.  Provide sumps, sedimentation tanks, and other flow-control devices as required by authorities having jurisdiction.

F. Provide standby equipment on site, installed and available for immediate operation, to maintain dewatering on continuous basis if any part of system becomes inadequate or fails.  If dewatering requirements are not satisfied due to inadequacy or failure of dewatering system, restore damaged structures and foundation soils at no additional expense to Owner.

1. Remove dewatering system from Project site on completion of dewatering.  Plug or fill well holes with sand or cut off and cap wells a minimum of 36 inches (900 mm) below overlying construction.

G. Damages:  Promptly repair damages to adjacent facilities caused by dewatering operations.

3.3 FIELD QUALITY CONTROL

Delete this article if not required.  Indicate locations of observation wells on Drawings.

A. Observation Wells:  Provide, take measurements, and maintain at least the minimum number of observation wells or piezometers indicated; additional observation wells may be required by authorities having jurisdiction.

1. Observe and record daily elevation of ground water and piezometric water levels in observation wells.

2. Repair or replace, within 24 hours, observation wells that become inactive, damaged, or destroyed.  In areas where observation wells are not functioning properly, suspend construction activities until reliable observations can be made.  Add or remove water from observation-well risers to demonstrate that observation wells are functioning properly.

3. Fill observation wells, remove piezometers, and fill holes when dewatering is completed.

B. Provide continual observation to ensure that subsurface soils are not being removed by the dewatering operation.

END OF SECTION 02240

DEWATERING
02240 - 1

