Copyright 2002 AIA
MASTERSPEC
11/02

Copyright 2002, The American Institute of Architects (AIA)

SECTION 07841 - THROUGH-PENETRATION FIRESTOP SYSTEMS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes through-penetration firestop systems for penetrations through fire-resistance-rated constructions, including both empty openings and openings containing penetrating items.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 7 Section "Fire-Resistive Joint Systems."

2. Division 13 Sections specifying fire-suppression piping penetrations.

3. Division 15 Sections specifying duct and piping penetrations.

4. Division 16 Sections specifying cable and conduit penetrations.

1.3 PERFORMANCE REQUIREMENTS

A. General:  For penetrations through [the following ]fire-resistance-rated constructions, including both empty openings and openings containing penetrating items, provide through-penetration firestop systems that are produced and installed to resist spread of fire according to requirements indicated, resist passage of smoke and other gases, and maintain original fire-resistance rating of construction penetrated.

Delete subparagraphs below if deleting the option in paragraph above.  Terms used below correspond to terms used in the IBC to describe constructions requiring protected penetrations.  Delete those constructions not included in Project.

1. Fire-resistance-rated walls including [fire walls] [fire partitions] [fire barriers] [and] [smoke barriers].

2. Fire-resistance-rated horizontal assemblies including [floors] [floor/ceiling assemblies] [and] [ceiling membranes of roof/ceiling assemblies].

If Project includes non-fire-resistance-rated constructions requiring that penetrations be protected by through-penetration firestop systems, indicate this on Drawings and insert new subparagraph below noting these exceptions.

Retain "UL 1479" option in paragraph below if firestop systems with L-ratings are required.

B. Rated Systems:  Provide through-penetration firestop systems with the following ratings determined per [ASTM E 814] [or] [UL 1479]:

Delete any requirements in subparagraphs below that do not apply to through-penetration firestop systems required for Project.

1. F-Rated Systems:  Provide through-penetration firestop systems with F-ratings indicated, but not less than that equaling or exceeding fire-resistance rating of constructions penetrated.

As a general rule, T-rated systems are required where penetrating items pass through occupiable areas where they may contact combustible materials.  See Evaluations.

2. T-Rated Systems:  For the following conditions, provide through-penetration firestop systems with T-ratings indicated, as well as F-ratings, where systems protect penetrating items exposed to potential contact with adjacent materials in occupiable floor areas:

a. Penetrations located outside wall cavities.

b. Penetrations located outside fire-resistance-rated shaft enclosures.

L-rated systems are not required by model codes in effect when this Section was updated.  L-ratings are used to determine effectiveness of firestop systems to resist passage of smoke or to further limit types of firestop systems that comply with requirements.  Only UL 1479 currently includes test for L-ratings.

3. L-Rated Systems:  [Where through-penetration firestop systems are indicated in smoke barriers, provide] [Provide] through-penetration firestop systems with L-ratings [indicated] [of not more than] [3.0 cfm/sq. ft (0.01524cu. m/s x sq. m)] <Insert rating> at both ambient temperatures and 400 deg F (204 deg C).

C. For through-penetration firestop systems exposed to view, traffic, moisture, and physical damage, provide products that, after curing, do not deteriorate when exposed to these conditions both during and after construction.

Three subparagraphs below are examples of special requirements.  Delete those not applicable; insert others to suit Project.

1. For piping penetrations for plumbing and wet-pipe sprinkler systems, provide moisture-resistant through-penetration firestop systems.

2. For floor penetrations with annular spaces exceeding 4 inches (100 mm) in width and exposed to possible loading and traffic, provide firestop systems capable of supporting floor loads involved, either by installing floor plates or by other means.

3. For penetrations involving insulated piping, provide through-penetration firestop systems not requiring removal of insulation.

Delete paragraph below if not applicable or if authorities having jurisdiction do not require firestop systems to have same Class A finish rating as wall and ceiling finishes in which firestop systems are installed.  Verify that through-penetration firestop systems selected use a fill material that complies with the requirement below.

D. For through-penetration firestop systems exposed to view, provide products with flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  For each through-penetration firestop system, show each type of construction condition penetrated, relationships to adjoining construction, and type of penetrating item.  Include firestop design designation of qualified testing and inspecting agency that evidences compliance with requirements for each condition indicated.

1. Submit documentation, including illustrations, from a qualified testing and inspecting agency that is applicable to each through-penetration firestop system configuration for construction and penetrating items.

Retain subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

2. Where Project conditions require modification to a qualified testing and inspecting agency's illustration for a particular through-penetration firestop condition, submit illustration, with modifications marked, approved by through-penetration firestop system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly.

C. Through-Penetration Firestop System Schedule:  Indicate locations of each through-penetration firestop system, along with the following information:

1. Types of penetrating items.

2. Types of constructions penetrated, including fire-resistance ratings and, where applicable, thicknesses of construction penetrated.

3. Through-penetration firestop systems for each location identified by firestop design designation of qualified testing and inspecting agency.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Assurance" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For Installer.

E. Product Certificates:  For through-penetration firestop system products, signed by product manufacturer.

Delete paragraph above or below.

F. Product Test Reports:  From a qualified testing agency indicating through-penetration firestop system complies with requirements, based on comprehensive testing of current products.

1.5 QUALITY ASSURANCE

Paragraph below represents a standard developed jointly by FMG and the Firestop Contractors International Association.  See Evaluations.

A. Installer Qualifications:  A firm that has been approved by FMG according to FMG 4991, "Approval of Firestop Contractors."

Delete paragraph above or below.  Before retaining below with option, verify with manufacturers selected that they will comply with requirements specified.  Before retaining either paragraph, also verify that installers qualifying with either paragraph are available to perform work in Project location.

B. Installer Qualifications:  A firm experienced in installing through-penetration firestop systems similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful performance.[  Qualifications include having the necessary experience, staff, and training to install manufacturer's products per specified requirements.  Manufacturer's willingness to sell its through-penetration firestop system products to Contractor or to Installer engaged by Contractor does not in itself confer qualification on buyer.]

Retain first paragraph below only after verifying with prospective contractors the feasibility of enforcing the requirement that installation of work of this Section, and possibly of Division 7 Section "Fire-Resistive Joint Systems," be assigned to a single firm.

C. Installation Responsibility:  Assign installation of through-penetration firestop systems [and fire-resistive joint systems ]in Project to a single qualified installer.

D. Source Limitations:  Obtain through-penetration firestop systems, for each kind of penetration and construction condition indicated, through one source from a single manufacturer.

E. Fire-Test-Response Characteristics:  Provide through-penetration firestop systems that comply with the following requirements and those specified in Part 1 "Performance Requirements" Article:

Retain or insert agency names in subparagraph below that are acceptable and that correspond with agencies whose designations are indicated either in the Through-Penetration Firestop System Schedule at end of Part 3 or on Drawings.

1. Firestopping tests are performed by a qualified testing and inspecting agency.  A qualified testing and inspecting agency is [UL,] [OPL] [ITS,] <Insert name,> or another agency performing testing and follow-up inspection services for firestop systems acceptable to authorities having jurisdiction.

Revise subparagraph and associated subparagraphs below if a different pressure differential is required from 0.01-inch wg (2.5 Pa) specified in ASTM E 814 as the "Standard Pressure Condition" and in UL 1479.

2. Through-penetration firestop systems are identical to those tested per testing standard referenced in "Part 1 Performance Requirements" Article.  Provide rated systems complying with the following requirements:

a. Through-penetration firestop system products bear classification marking of qualified testing and inspecting agency.

b. Through-penetration firestop systems correspond to those indicated by reference to through-penetration firestop system designations listed by the following:

Retain only the subparagraph or subparagraphs below that reference the directories of the testing and inspecting agency or agencies whose designations are indicated either in the Through-Penetration Firestop System Schedule at end of Part 3 or on Drawings.

1) UL in its "Fire Resistance Directory."

2) OPL in its "Directory of Listed Building Products, Materials, & Assemblies."

3) ITS in its "Directory of Listed Products."

4) <Insert name of qualified testing and inspecting agency.>

Delete paragraph below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 1.

F. Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 1 Section "Project Management and Coordination."

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver through-penetration firestop system products to Project site in original, unopened containers or packages with intact and legible manufacturers' labels identifying product and manufacturer, date of manufacture, lot number, shelf life if applicable, qualified testing and inspecting agency's classification marking applicable to Project, curing time, and mixing instructions for multicomponent materials.

B. Store and handle materials for through-penetration firestop systems to prevent their deterioration or damage due to moisture, temperature changes, contaminants, or other causes.

1.7 PROJECT CONDITIONS

A. Environmental Limitations:  Do not install through-penetration firestop systems when ambient or substrate temperatures are outside limits permitted by through-penetration firestop system manufacturers or when substrates are wet due to rain, frost, condensation, or other causes.

B. Ventilate through-penetration firestop systems per manufacturer's written instructions by natural means or, where this is inadequate, forced-air circulation.

1.8 COORDINATION

A. Coordinate construction of openings and penetrating items to ensure that through-penetration firestop systems are installed according to specified requirements.

B. Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to accommodate through-penetration firestop systems.

C. Notify Owner's inspecting agency at least seven days in advance of through-penetration firestop system installations; confirm dates and times on days preceding each series of installations.

Delete paragraph above and option in paragraph below if Owner does not plan to engage an inspecting agency to examine through-penetration firestop systems.

D. Do not cover up through-penetration firestop system installations that will become concealed behind other construction until each installation has been examined by[ Owner's inspecting agency and] building inspector, if required by authorities having jurisdiction.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instructions No. 1 and No. 2 in the Evaluations for cautions about naming manufacturers and products and for instructions on how to edit this Article.

A. Available Products:  Subject to compliance with requirements, through-penetration firestop systems that may be incorporated into the Work include, but are not limited to, those systems indicated [in the Through-Penetration Firestop System Schedule] [at the end of Part 3] [on Drawings] [.] [that are produced by one of the following manufacturers:]

Retain above for nonproprietary or below for semiproprietary specification if firestop system products are specified in the Through-Penetration Firestop System Schedule or are indicated on Drawings.  Refer to Division 1 Section "Product Requirements."  Retain last option in paragraph above or below if naming manufacturers in this Article.

B. Products:  Subject to compliance with requirements, provide one of the through-penetration firestop systems indicated for each application [in the Through-Penetration Firestop System Schedule] [at the end of Part 3] [on Drawings] [.] [that are produced by one of the following manufacturers:]

Retain and edit list below with either paragraph above if naming manufacturers to limit selection or to inform.  Retain in paragraph selected above the optional text "that are produced by one of the following manufacturers."

1. A/D Fire Protection Systems Inc.

2. Grace, W. R. & Co. - Conn.

3. Hilti, Inc.

4. Johns Manville.

5. Nelson Firestop Products.

6. NUCO Inc.

7. RectorSeal Corporation (The).

8. Specified Technologies Inc.

9. 3M; Fire Protection Products Division.

10. Tremco; Sealant/Weatherproofing Division.

11. USG Corporation.

12. <Insert manufacturer's name.>

2.2 FIRESTOPPING, GENERAL

A. Compatibility:  Provide through-penetration firestop systems that are compatible with one another; with the substrates forming openings; and with the items, if any, penetrating through-penetration firestop systems, under conditions of service and application, as demonstrated by through-penetration firestop system manufacturer based on testing and field experience.

B. Accessories:  Provide components for each through-penetration firestop system that are needed to install fill materials and to comply with Part 1 "Performance Requirements" Article.  Use only components specified by through-penetration firestop system manufacturer and approved by qualified testing and inspecting agency for firestop systems indicated.[  Accessories include, but are not limited to, the following items:]

Delete accessories below not required for through-penetration firestop systems indicated.  If deleting option in paragraph above, delete subparagraphs and associated subparagraphs below.

1. Permanent forming/damming/backing materials, including the following:

a. Slag-/rock-wool-fiber insulation.

b. Sealants used in combination with other forming/damming/backing materials to prevent leakage of fill materials in liquid state.

c. Fire-rated form board.

d. Fillers for sealants.

2. Temporary forming materials.

3. Substrate primers.

4. Collars.

5. Steel sleeves.

2.3 FILL MATERIALS

Delete this Article if fill materials are not specified in the Through-Penetration Firestop System Schedule at the end of Part 3 or if using the sample schedule in the Evaluations.

A. General:  Provide through-penetration firestop systems containing the types of fill materials indicated in the Through-Penetration Firestop System Schedule at the end of Part 3 by referencing the types of materials described in this Article.  Fill materials are those referred to in directories of referenced testing and inspecting agencies as "fill," "void," or "cavity" materials.

B. Cast-in-Place Firestop Devices:  Factory-assembled devices for use in cast-in-place concrete floors and consisting of an outer metallic sleeve lined with an intumescent strip, a radial extended flange attached to one end of the sleeve for fastening to concrete formwork, and a neoprene gasket.

C. Latex Sealants:  Single-component latex formulations that after cure do not re-emulsify during exposure to moisture.

D. Firestop Devices:  Factory-assembled collars formed from galvanized steel and lined with intumescent material sized to fit specific diameter of penetrant.

E. Intumescent Composite Sheets:  Rigid panels consisting of aluminum-foil-faced elastomeric sheet bonded to galvanized steel sheet.

F. Intumescent Putties:  Nonhardening dielectric, water-resistant putties containing no solvents, inorganic fibers, or silicone compounds.

G. Intumescent Wrap Strips:  Single-component intumescent elastomeric sheets with aluminum foil on one side.

H. Mortars:  Prepackaged dry mixes consisting of a blend of inorganic binders, hydraulic cement, fillers, and lightweight aggregate formulated for mixing with water at Project site to form a nonshrinking, homogeneous mortar.

I. Pillows/Bags:  Reusable heat-expanding pillows/bags consisting of glass-fiber cloth cases filled with a combination of mineral-fiber, water-insoluble expansion agents, and fire-retardant additives.

J. Silicone Foams:  Multicomponent, silicone-based liquid elastomers that, when mixed, expand and cure in place to produce a flexible, nonshrinking foam.

K. Silicone Sealants:  Single-component, silicone-based, neutral-curing elastomeric sealants of grade indicated below:

Retain first subparagraph below to allow manufacturer's standard grade (pourable or nonsag) as listed for fire-rated systems.  Delete first subparagraph and retain either second or third subparagraph, or both, if selection is limited to manufacturer(s) offering both grades.

1. Grade:  Pourable (self-leveling) formulation for openings in floors and other horizontal surfaces, and nonsag formulation for openings in vertical and other surfaces requiring a nonslumping, gunnable sealant, unless indicated firestop system limits use to nonsag grade for both opening conditions.

2. Grade for Horizontal Surfaces:  Pourable (self-leveling) formulation for openings in floors and other horizontal surfaces.

3. Grade for Vertical Surfaces:  Nonsag formulation for openings in vertical and other surfaces.

2.4 MIXING

Delete this Article if no products are specified that require mixing before application.

A. For those products requiring mixing before application, comply with through-penetration firestop system manufacturer's written instructions for accurate proportioning of materials, water (if required), type of mixing equipment, selection of mixer speeds, mixing containers, mixing time, and other items or procedures needed to produce products of uniform quality with optimum performance characteristics for application indicated.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and conditions, with Installer present, for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance of work.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Surface Cleaning:  Clean out openings immediately before installing through-penetration firestop systems to comply with firestop system manufacturer's written instructions and with the following requirements:

1. Remove from surfaces of opening substrates and from penetrating items foreign materials that could interfere with adhesion of through-penetration firestop systems.

2. Clean opening substrates and penetrating items to produce clean, sound surfaces capable of developing optimum bond with through-penetration firestop systems.  Remove loose particles remaining from cleaning operation.

3. Remove laitance and form-release agents from concrete.

Delete paragraph below if products selected do not require priming.

B. Priming:  Prime substrates where recommended in writing by through-penetration firestop system manufacturer using that manufacturer's recommended products and methods.  Confine primers to areas of bond; do not allow spillage and migration onto exposed surfaces.

Delete paragraph below if applications indicated do not require masking tape.

C. Masking Tape:  Use masking tape to prevent through-penetration firestop systems from contacting adjoining surfaces that will remain exposed on completion of Work and that would otherwise be permanently stained or damaged by such contact or by cleaning methods used to remove smears from firestop system materials.  Remove tape as soon as possible without disturbing firestop system's seal with substrates.

3.3 THROUGH-PENETRATION FIRESTOP SYSTEM INSTALLATION

A. General:  Install through-penetration firestop systems to comply with Part 1 "Performance Requirements" Article and with firestop system manufacturer's written installation instructions and published drawings for products and applications indicated.

B. Install forming/damming/backing materials and other accessories of types required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

Delete subparagraph below if none of the systems specified requires using removable forming materials and other accessories.

1. After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of firestop systems.

C. Install fill materials for firestop systems by proven techniques to produce the following results:

1. Fill voids and cavities formed by openings, forming materials, accessories, and penetrating items as required to achieve fire-resistance ratings indicated.

2. Apply materials so they contact and adhere to substrates formed by openings and penetrating items.

3. For fill materials that will remain exposed after completing Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

3.4 IDENTIFICATION

Delete this Article if labels are not required.  Revise if labeling is limited to selected applications.

A. Identify through-penetration firestop systems with preprinted metal or plastic labels.  Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of edge of the firestop systems so that labels will be visible to anyone seeking to remove penetrating items or firestop systems.  Use mechanical fasteners for metal labels.  For plastic labels, use self-adhering type with adhesives capable of permanently bonding labels to surfaces on which labels are placed and, in combination with label material, will result in partial destruction of label if removal is attempted.  Include the following information on labels:

1. The words "Warning - Through-Penetration Firestop System - Do Not Disturb.  Notify Building Management of Any Damage."

2. Contractor's name, address, and phone number.

3. Through-penetration firestop system designation of applicable testing and inspecting agency.

4. Date of installation.

5. Through-penetration firestop system manufacturer's name.

6. Installer's name.

3.5 FIELD QUALITY CONTROL

Delete this Article and paragraphs referring to services of inspecting agency in Part 1 "Coordination" Article if no field quality control will be provided by Owner.  According to ASTM E 2174, "inspectors shall be completely independent of, and divested from, the installer, contractor, manufacturer, or supplier of any material being inspected."  This statement seems to preclude making Contractor responsible for engaging inspecting agency.

A. Inspecting Agency:  Owner will engage a qualified, independent inspecting agency to inspect through-penetration firestops.  Independent inspecting agency shall comply with ASTM E 2174 requirements including those related to qualifications, conducting inspections, and preparing test reports.

B. Where deficiencies are found, repair or replace through-penetration firestop systems so they comply with requirements.

C. Proceed with enclosing through-penetration firestop systems with other construction only after inspection reports are issued and firestop installations comply with requirements.

3.6 CLEANING AND PROTECTING

A. Clean off excess fill materials adjacent to openings as Work progresses by methods and with cleaning materials that are approved in writing by through-penetration firestop system manufacturers and that do not damage materials in which openings occur.

B. Provide final protection and maintain conditions during and after installation that ensure that through-penetration firestop systems are without damage or deterioration at time of Substantial Completion.  If, despite such protection, damage or deterioration occurs, cut out and remove damaged or deteriorated through-penetration firestop systems immediately and install new materials to produce systems complying with specified requirements.

3.7 THROUGH-PENETRATION FIRESTOP SYSTEM SCHEDULE

Modify schedule below to suit Project.  Delete if schedule is placed on Drawings.

For a nonproprietary specification, retain "Available" in titles of subparagraphs below in which UL- or OPL-classified or ITS-listed systems are specified.  Coordinate with Part 2 "Manufacturers" Article by retaining "Available Products" Paragraph.  See Editing Instructions No. 1 and No. 2 in the Evaluations for more information about specifying products.  Also see the sample schedule in the Evaluations.

Retain paragraph below if UL systems are indicated.

A. Where UL-classified systems are indicated, they refer to alpha-alpha-numeric designations listed in UL's "Fire Resistance Directory" under product Category XHEZ.

Retain paragraph below if OPL systems are indicated.

B. Where OPL-classified systems are indicated, they refer to alpha-numeric design numbers in OPL's "Directory of Listed Building Products, Materials, & Assemblies."

Retain paragraph below if ITS systems are indicated.

C. Where ITS-listed systems are indicated, they refer to design numbers listed in ITS's "Directory of Listed Products," "Firestop Systems" Section.

If retaining "FS" in options below as means of identifying location of each firestop system on Drawings, insert number in place of <#> to complete designations below.

Copy and re-edit appropriate sample paragraphs and subparagraphs below for each system required.

D. Firestop Systems with No Penetrating Items[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [0001-0999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type G.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Silicone sealant.

c. Intumescent putty.

d. Mortar.

E. Firestop Systems for Metallic Pipes, Conduit, or Tubing[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [W-J-] [W-K-] [W-L-] <Insert one or more four-digit numbers> [1001-1999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type A.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Silicone sealant.

c. Intumescent putty.

d. Mortar.

F. Firestop Systems for Nonmetallic Pipe, Conduit, or Tubing[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [2001-2999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type B.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Silicone sealant.

c. Intumescent putty.

d. Intumescent wrap strips.

e. Firestop device.

G. Firestop Systems for Electrical Cables[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [3001-3999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type D.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Silicone sealant.

c. Intumescent putty.

d. Silicone foam.

e. Pillows/bags.

H. Firestop Systems for Cable Trays[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-K-] [W-L-] <Insert one or more four-digit numbers> [4001-4999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type D.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Intumescent putty.

c. Silicone foam.

d. Pillows/bags.

e. Mortar.

I. Firestop Systems for Insulated Pipes[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [F-C-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [5001-5999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type C.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Intumescent putty.

c. Silicone foam.

d. Intumescent wrap strips.

J. Firestop Systems for Miscellaneous Electrical Penetrants[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [F-A-] [W-L-] <Insert one or more four-digit numbers> [6001-6999].

2. [Available ]OPL-Classified Systems:  FS <Insert one or more OPL design numbers> [F] [W], Penetrating Item Type E.

3. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations, OPL design numbers, or ITS design numbers.

4. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Intumescent putty.

c. Mortar.

K. Firestop Systems for Miscellaneous Mechanical Penetrants[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [F-C-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [7001-7999].

2. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations or ITS design numbers.  No OPL type is listed for miscellaneous mechanical penetrations.

3. Type of Fill Materials:  One or both of the following:

a. Latex sealant.

b. Mortar.

L. Firestop Systems for Groupings of Penetrants[ FS-<#>]:

1. [Available ]UL-Classified Systems:  [C-AJ-] [C-BJ-] [F-A-] [F-C-] [W-J-] [W-L-] <Insert one or more four-digit numbers> [8001-8999].

2. [Available ]ITS-Listed Systems:  <Insert ITS design number(s).>

Delete subparagraph and list below if selections are limited to systems indicated by specific UL designations or ITS design numbers.  No OPL type is listed for groupings of penetrations.

3. Type of Fill Materials:  One or more of the following:

a. Latex sealant.

b. Mortar.

c. Intumescent wrap strips.

d. Firestop device.

e. Intumescent composite sheet.

END OF SECTION 07841

THROUGH-PENETRATION FIRESTOP SYSTEMS
07841 - 14

