Copyright 2005 AIA
MASTERSPEC Full Length
05/05 (R 05/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 10523 - FIRE EXTINGUISHERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section includes portable, [hand-carried] [wheeled] fire extinguishers[ and mounting brackets for fire extinguishers].

B. Owner-Furnished Material:  [Hand-carried] [Wheeled] fire extinguishers.

C. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 10 Section "Fire Extinguisher Cabinets."

2. Division 13 Section "Fire-Suppression Piping" for hose systems, racks, and valves.

3. Division 15 Section "Commercial Kitchen Hoods" for fire extinguishing systems provided as part of commercial kitchen exhaust hoods.

1.3 UNIT PRICES

Retain products and work included in this Section that are covered by unit prices.  Do not include amounts.  Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the unit price.

A. Work of this Section is affected by <Insert name of unit price>.

1.4 SUBMITTALS

First two paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include rating and classification, material descriptions, dimensions of individual components and profiles, and finishes for fire extinguisher[ and mounting brackets].

B. Product Schedule:  For fire extinguishers. Coordinate final fire extinguisher schedule with fire protection cabinet schedule to ensure proper fit and function.[  Use same designations indicated on Drawings.]

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

C. Operation and Maintenance Data:  For fire extinguishers to include in maintenance manuals.

D. Warranty:  Sample of special warranty.

1.5 QUALITY ASSURANCE

A. NFPA Compliance:  Fabricate and label fire extinguishers to comply with NFPA 10, "Portable Fire Extinguishers."

B. Fire Extinguishers:  Listed and labeled for type, rating, and classification by an independent testing agency acceptable to authorities having jurisdiction.

Retain subparagraph below if required for insurance purposes; verify availability with manufacturers selected because not all products comply.

1. Provide fire extinguishers approved, listed, and labeled by FMG.

Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

C. Preinstallation Conference:  Conduct conference at [Project site] <Insert location>.

Retain subparagraph below if additional requirements are necessary; include information about conference.

1. Review methods and procedures related to fire extinguishers including, but not limited to, the following:

a. Schedules and coordination requirements.

1.6 COORDINATION

Consider retaining this article if fire protection cabinets are specified by series only or for complex projects.

A. Coordinate type and capacity of fire extinguishers with fire protection cabinets to ensure fit and function.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

Hydrostatic test in first subparagraph below is required every 5 years for water, AFFF, FFFP, dry-chemical-in-stainless-steel-shell, carbon dioxide, and wet-chemical fire extinguishers; every 12 years for other dry-chemical, dry-powder, and halogenated-agent fire extinguishers.

a. Failure of hydrostatic test according to NFPA 10.

b. Faulty operation of valves or release levers.

Verify available warranties and warranty periods for fire extinguishers with manufacturers listed in Part 2 articles.  NFPA 10 requires that stored-pressure, portable fire extinguishers subject to hydrostatic tests every 12 years be subject to NFPA 10's maintenance procedures.

2. Warranty Period:  [Six] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 PORTABLE, HAND-CARRIED FIRE EXTINGUISHERS

Refer to the tables at the end of the Evaluations in Division 10 Section "Fire Protection Specialties" for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

A. Fire Extinguishers:  Type, size, and capacity for each [fire protection cabinet] [mounting bracket] [fire protection cabinet and mounting bracket] indicated.

See Editing Instruction No. 1 in the Evaluations in Division 10 Section "Fire Protection Specialties" for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Amerex Corporation.

b. Ansul Incorporated; Tyco International Ltd.

c. Badger Fire Protection; a Kidde company.

d. Buckeye Fire Equipment Company.

e. Fire End & Croker Corporation.

f. J. L. Industries, Inc.; a division of Activar Construction Products Group.

g. Kidde Residential and Commercial Division; Subsidiary of Kidde plc.

h. Larsen's Manufacturing Company.

i. Moon-American.

j. Pem All Fire Extinguisher Corp.; a division of PEM Systems, Inc.

k. Potter Roemer LLC.

l. Pyro-Chem; Tyco Safety Products.

m. <Insert manufacturer's name>.

Retain three subparagraphs below if required.  Aluminum valves, handles, and levers are sometimes used for small- and medium-size fire extinguishers.

3. Valves:  [Manufacturer's standard] [Nickel-plated, polished brass body].

4. Handles and Levers:  [Manufacturer's standard] [Stainless steel].

5. Instruction Labels:  Include pictorial marking system complying with NFPA 10, Appendix B[ and bar coding for documenting fire extinguisher location, inspections, maintenance, and recharging].

In remaining paragraphs, the letter A, B, C, D, or K indicates the class of fire on which an extinguisher is effective.  Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness.  Extinguishers for Class C, Class D, and Class K fires are not required to have a rating numeral.  See the Evaluations in Division 10 Section "Fire Protection Specialties" for fire classifications and numerical rating explanation.

In retained paragraphs below, insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

Retain one or more of first three paragraphs below for water-type extinguishers.  Potential for freezing exists with all types.  Retain second paragraph if freeze potential is high.

B. Stored-Pressure Water Type <Insert drawing designation>:  UL-rated 2-A, 2.5-gal. (9.5-L) nominal capacity, with water in stainless-steel container; with pressure-indicating gage.

C. Stored-Pressure Antifreeze Water Type <Insert drawing designation>:  UL-rated 2-A, 2.5-gal. (9.5-L) nominal capacity, with water and approved antifreeze solution mixed for temperatures as low as minus 40 deg F (minus 40 deg C) in stainless-steel container; with pressure-indicating gage.

D. Stored-Pressure Water-Mist Type <Insert drawing designation>:  UL-rated 2-A:C, 2.5-gal. (9.5-L) nominal capacity, with water in enameled-steel container; with pressure-indicating gage.

E. Pressurized, AFFF-Foam Type <Insert drawing designation>:  UL-rated [2-A:10-B, 1.6-gal. (6-L)] [3-A:20-B, 2.5-gal. (9.5-L)] nominal capacity, with AFFF foam in stainless-steel container; with pressure-indicating gage.

F. Pressurized, FFFP-Foam Type <Insert drawing designation>:  UL-rated 3-A:20-B, 2.5-gal. (9.5-L) nominal capacity, with FFFP foam in stainless-steel container; with pressure-indicating gage.

G. Wet-Chemical Type <Insert drawing designation>:  UL-rated 2-A:1-B:C:K, [1.6-gal. (6-L)] [2.5-gal. (9.5-L)] nominal capacity, with potassium [acetate] [citrate] [carbonate]-based chemical in stainless-steel container; with pressure-indicating gage.

Retain one or more of first four paragraphs below for dry-chemical-type extinguishers.

H. Regular Dry-Chemical Type <Insert drawing designation>:  UL-rated <Insert capacity> nominal capacity, with sodium bicarbonate-based dry chemical in manufacturer's standard enameled container.

I. Regular Dry-Chemical Type in Steel Container <Insert drawing designation>:  UL-rated [2-B:C, 1-lb (0.4-kg)] [10-B:C, 2.5-lb (1.1-kg)] [10-B:C, 5-lb (2.3-kg)] [40-B:C, 5.5-lb (2.5-kg)] [40-B:C, 6-lb (2.7-kg)] [60-B:C, 10-lb (4.5-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with sodium bicarbonate-based dry chemical in enameled-steel container.

J. Regular Dry-Chemical Type in Aluminum Container <Insert drawing designation>:  UL-rated [2-B:C, 1-lb (0.4-kg)] [10-B:C, 2.5-lb (1.1-kg)] [10-B:C, 5-lb (2.3-kg)] [40-B:C, 5.5-lb (2.5-kg)] [60-B:C, 10-lb (4.5-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with sodium bicarbonate-based dry chemical in enameled-aluminum container.

K. Regular Dry-Chemical Type in Brass Container <Insert drawing designation>:  UL-rated [40-B:C, 6-lb (2.7-kg)] [60-B:C, 10-lb (4.5-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with sodium bicarbonate-based dry chemical in chrome-plated brass container.

Retain one or more of first four paragraphs below for multipurpose, dry-chemical-type extinguishers.

L. Multipurpose Dry-Chemical Type <Insert drawing designation>:  UL-rated <Insert capacity> nominal capacity, with monoammonium phosphate-based dry chemical in manufacturer's standard enameled container.

M. Multipurpose Dry-Chemical Type in Steel Container <Insert drawing designation>:  UL-rated [1-A:10-B:C, 2.5-lb (1.1-kg)] [2-A:10-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 6-lb (2.7-kg)] [4-A:60-B:C, 10-lb (4.5-kg)] [20-A:120-B:C, 20-lb (9.1-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in enameled-steel container.

N. Multipurpose Dry-Chemical Type in Aluminum Container <Insert drawing designation>:  UL-rated [1-A:10-B:C, 2.5-lb (1.1-kg)] [2-A:10-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 6-lb (2.7-kg)] [4-A:60-B:C, 10-lb (4.5-kg)] [20-A:120-B:C, 20-lb (9.1-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in enameled-aluminum container.

O. Multipurpose Dry-Chemical Type in Brass Container <Insert drawing designation>:  UL-rated [2-A:10-B:C, 5-lb (2.3-kg)] [3-A:40-B:C, 6-lb (2.7-kg)] [4-A:60-B:C, 10-lb (4.5-kg)] [4-A:80-B:C, 10-lb (4.5-kg)] [20-A:120-B:C, 20-lb (9.1-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in chrome-plated brass container.

Retain one or both of first two paragraphs below for Purple-K, dry-chemical-type extinguishers.

P. Purple-K Dry-Chemical Type in Aluminum Container <Insert drawing designation>:  UL-rated [10-B:C, 2.5-lb (1.1-kg)] [30-B:C, 5-lb (2.3-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with potassium bicarbonate-based dry chemical in enameled-aluminum container.

Q. Purple-K Dry-Chemical Type in Brass Container <Insert drawing designation>:  UL-rated [80-B:C, 10-lb (4.5-kg)] [120-B:C, 20-lb (9.1-kg)] nominal capacity, with potassium bicarbonate-based dry chemical in chrome-plated brass container.

R. Carbon Dioxide Type <Insert drawing designation>:  UL-rated [5-B:C, 5-lb (2.3-kg)] [10-B:C, 10-lb (4.5-kg)] [10-B:C, 15-lb (6.8-kg)] [10-B:C, 20-lb (9.1-kg)] nominal capacity, with carbon dioxide in [manufacturer's standard enameled-metal] [enameled-steel] [enameled-aluminum] container.

S. Dry-Powder Type <Insert drawing designation>:  [FMG-approved, ]UL-rated Class D, 30-lb (13.6-kg) nominal capacity, with [sodium chloride] [copper]-based powder in enameled-steel container; with pressure-indicating gage.

Halon-type fire extinguishers in first paragraph below are still available from manufacturers.  See the Evaluations in Division 10 Section "Fire Protection Specialties" for environmental considerations.  Delete below if LEED-NC or LEED-CI Credit EA 4, which does not allow halons or HCFCs, is required.

T. Halon Type <Insert drawing designation>:  UL-rated [5-B:C, 2.5-lb (1.1-kg)] [10-B:C, 5-lb (2.3-kg)] nominal capacity, in enameled-steel container; with pressure-indicating gage.

Retain one or more of three paragraphs below.

First two paragraphs below describe fire extinguishers using Halotron I clean agent as an alternative to halon.  See the Evaluations in Division 10 Section "Fire Protection Specialties." Delete first two paragraphs below if LEED-NC or LEED-CI Credit EA 4, which does not allow halons or HCFCs, is required.

U. Clean-Agent Type in Aluminum Container <Insert drawing designation>:  UL-rated [1-B:C, 1.4-lb (0.6-kg)] [2-B:C, 2.5-lb (1.1-kg)] [5-B:C, 5-lb (2.3-kg)] nominal capacity, with HCFC Blend B agent and inert material in enameled-aluminum container; with pressure-indicating gage.

V. Clean-Agent Type in Brass Container <Insert drawing designation>:  UL-rated [1-A:10-B:C, 11-lb (5-kg)] [2-A:10-B:C, 15.5-lb (7-kg)] nominal capacity, with HCFC Blend B agent and inert material in chrome-plated brass container; with pressure-indicating gage.

Paragraph below describes Ansul's fire extinguishers using FE-36 clean agent as an alternative to halon.  See the Evaluations in Division 10 Section "Fire Protection Specialties." Below is an alternative to last three paragraphs above if LEED-NC or LEED-CI Credit EA 4, which does not allow halons or HCFCs, is required.

W. Clean-Agent Type in Steel Container <Insert drawing designation>:  UL-rated [5-B:C, 4.75-lb (2.2-kg)] [1-A:10-B:C, 10-lb (4.5-kg)] [2-A:10-B:C, 14-lb (6.4-kg)] nominal capacity, with HFC blend agent and inert material in enameled-steel container; with pressure-indicating gage.

Add other types and capacities to suit Project.

2.2 MOUNTING BRACKETS <Insert drawing designation>

Delete this article if mounting brackets separate from fire protection cabinets are not required.

Copy this article and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

A. Mounting Brackets:  Manufacturer's standard[ galvanized] steel, designed to secure fire extinguisher to wall or structure, of sizes required for types and capacities of fire extinguishers indicated, with plated or [red] [black] baked-enamel finish.

See Editing Instruction No. 1 in the Evaluations in Division 10 Section "Fire Protection Specialties" for cautions about naming manufacturers.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Amerex Corporation.

b. Ansul Incorporated; Tyco International Ltd.

c. Badger Fire Protection; a Kidde company.

d. Buckeye Fire Equipment Company.

e. Fire End & Croker Corporation.

f. J. L. Industries, Inc.; a division of Activar Construction Products Group.

g. Larsen's Manufacturing Company.

h. Potter Roemer LLC.

i. <Insert manufacturer's name>.

B. Identification:  Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location.  Locate as indicated by Architect.

1. Identify bracket-mounted fire extinguishers with the words "FIRE EXTINGUISHER" in red letter decals applied to mounting surface.

If more than one orientation is required, indicate location of each on Drawings.

a. Orientation:  [Vertical] [Horizontal].

2.3 WHEELED FIRE EXTINGUISHERS <Insert drawing designation>

Refer to the tables at the end of the Evaluations in Division 10 Section "Fire Protection Specialties" for a list of manufacturers' products.  Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

Copy this article and re-edit for each product.

Insert number to complete drawing designation.  Use these designations on Drawings to identify each product.

A. Wheeled Fire Extinguishers:  Type, size, and capacity for locations indicated, complete with carriage.

See Editing Instruction No. 1 in the Evaluations in Division 10 Section "Fire Protection Specialties" for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Amerex Corporation.

b. Ansul Incorporated; Tyco International Ltd.

c. Badger Fire Protection; a Kidde company.

d. Buckeye Fire Equipment Company.

e. Fire End & Croker Corporation.

f. Modern Metal Products; Division of Technico Inc.

g. Moon-American.

h. Pyro-Chem; Tyco Safety Products.

i. <Insert manufacturer's name>.

3. Carriage:  Fabricated from enameled-steel pipe, complete with hanger assembly, long-range nozzle, hose, and [semipneumatic solid-rubber tires] [wide-rim wheels].

a. Hose:  [15 feet (4.6 m)] [50 feet (15.2 m)] [100 feet (30.5 m)].

In remaining paragraphs, the letter A, B, C, or D indicates the class of fire on which an extinguisher is effective.  Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness.  Extinguishers for Class C and Class D fires are not required to have a rating numeral.  See the Evaluations in Division 10 Section "Fire Protection Specialties" for fire classifications and numerical rating explanation.

B. Pressurized, FFFP-Foam Type:  UL-rated 20-A:160-B, 33-gal. (125-L) nominal capacity, with FFFP foam in stainless-steel container.

C. Regular Dry-Chemical Type:  UL-rated [160-B:C, 50-lb (23-kg)] [240-B:C, 150-lb (68-kg)] [160-B:C, 250-lb (113-kg)] nominal capacity, with sodium bicarbonate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-steel container.

Verify availability of enameled-aluminum containers in first paragraph below with manufacturers selected.

D. Multipurpose Dry-Chemical Type:  UL-rated [20-A:160-B:C, 30-lb (13.6-kg)] [30-A:160-B:C, 50-lb (23-kg)] [40-A:240-B:C, 125-lb (57-kg)] [40-A:160-B:C, 250-lb (113-kg)] nominal capacity, with monoammonium phosphate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-[steel] [aluminum] [steel or -aluminum] container.

E. Purple-K Dry-Chemical Type:  UL-rated [160-B:C, 50-lb (23-kg)] [320-B:C, 125-lb (57-kg)] [160-B:C, 250-lb (113-kg)] nominal capacity, with potassium bicarbonate-based dry chemical in [regulated] [stored] [direct]-pressure, enameled-steel container.

Verify availability of enameled-aluminum containers in first paragraph below with manufacturers selected.

F. Carbon Dioxide Type:  UL-rated [20-B:C, 50-lb (23-kg)] [20-B:C, 100-lb (45-kg)] nominal capacity, with carbon dioxide in [manufacturer's standard enameled-metal] [enameled-steel] [enameled-aluminum] container.

G. Dry-Powder Type:  [FMG-approved, ]UL-rated Class D, [sodium chloride-based powder, 150-lb (68-kg)] [copper-based powder, 250-lb (113-kg)] nominal capacity, in regulated-pressure, enameled-steel container; with pressure-indicating gage.

Delete below if LEED-NC or LEED-CI Credit EA 4, which does not allow halons or HCFCs, is required.

H. Clean-Agent Type:  UL-rated [4-A:40-B:C, 65-lb (29-kg)] [10-A:80-B:C, 150-lb (68-kg)] nominal capacity, with HCFC Blend B agent and inert material in stored-pressure, enameled-steel container; with pressure-indicating gage.

Add other types and capacities to suit Project.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine fire extinguishers for proper charging and tagging.

1. Remove and replace damaged, defective, or undercharged fire extinguishers.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. General:  Install fire extinguishers[ and mounting brackets] in locations indicated and in compliance with requirements of authorities having jurisdiction.

According to NFPA 10, maximum mounting height for fire extinguishers weighing 40 lb (18 kg) or less is 60 inches (1524 mm); for those weighing more, it is 42 inches (1067 mm).

1. Mounting Brackets:  [54 inches (1372 mm)] <Insert dimension> above finished floor to top of fire extinguisher.

B. Mounting Brackets:  Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

END OF SECTION 10523

FIRE EXTINGUISHERS
10523 - 1

