Copyright 2001 AIA
MASTERSPEC
06/01 (R 06/03)

Copyright 2003 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 13810 - CLOCK AND PROGRAM CONTROL
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section specifies a master clock[ and program] control system including the following components:

Adjust list below to suit Project.

1. Master clock[ and program] control unit.

2. Secondary indicating clocks.

3. Program signal devices.

4. Clock circuit power boosters.

5. Interface with [intercom] [public-address] system.

6. System wire and cable.

1.3 DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A. GPS:  Global Positioning System .

B. NIST:  National Institute of Science and Technology.

C. PC:  Personal computer.

D. UTC:  Universal time coordinated.  The precisely measured time at zero degrees longitude; used as a worldwide standard for time synchronization.

1.4 SYSTEM DESCRIPTION

Below is a sample description of performance requirements for completed clock and program control system.  Edit description items to suit Project.  Coordinate this Article with products and features described in this Section.

A. System shall perform the following functions:

Retain option in first subparagraph below if some clocks have operating power supplied independent of correction-signal wiring.  See Evaluations.

1. Supply power to remote indicating clocks[ except those indicated to have correction signals applied through a data circuit].

2. Maintain correct synchronized time and transmit time-correction signals over dedicated system wiring from a master clock to any [one] [two] <Insert number> type(s) of secondary indicating clocks, including the following:

Retain one or more of first three subparagraphs below to suit Project, depending on types of clocks to be controlled.

a. Analog Synchronous Clocks:  Correct for minute- and second-hand synchronization at least once each hour and for hour-hand synchronization at least once each day.

b. Analog Minute Impulse Clocks:  Correct for minute-hand synchronization with master time control at least once each hour and for hour-hand synchronization at least once each day.

c. Digital Clocks:  Test clocks automatically for synchronization with master time control at least once every hour and automatically correct those not synchronized with the time reference unit.[ Automatically correct clocks immediately when power is restored after an outage of normal power to the master clock.]

3. Initiate and execute programs for scheduled automatic operation of remote devices.  Include [audible signal devices] [visual signal devices] [audible and visual signal devices] [and on and off switching of equipment and circuits].

4. Provide for manual control of programmed signal and equipment switching circuits.

5. Communicate with remote PC [for access to UTC time base] [and] [to permit programming from remote location].

6. Maintain system access security with a minimum of [one level] [two levels] [three levels] of user-access control to restrict use of system controls to authorized personnel.[ Levels of access apply to both local access and access from a remote computer.] Access to user programming and control functions is accomplished by entering a minimum three-digit code.  Access levels include the following:

Edit three subparagraphs below to suit Project and to be consistent with editing of last subparagraph above.  Select third subparagraph for single-level access.

a. Access to review existing programs only.

b. Access to normal system operating controls.

c. Access to all user-programming and control functions.

Retain one of two subparagraphs below.  Retain second subparagraph if precision time synchronization is required; edit to specify acceptable method(s) of providing automated periodic correction for system time base.  See Evaluations for discussion of alternatives.  Coordinate with Part 2 for equipment.

7. Regulate system timing functions using power-line frequency, backed up for power outages by an internal battery-powered, crystal-controlled oscillator.

8. Regulate system timing functions using power-line frequency, backed up for power outages by an internal battery-powered, crystal-controlled oscillator, and automated periodic reference to NIST or UTC time signals via [internal telephone modem and automatic dial-up connection] [internal modem and network or microcomputer Internet access] [GPS receiver and antenna] [dedicated internal radio receiver tuned to NIST time signal broadcasts].  Reference time signals shall be automatically accessed at programmable intervals.

Edit subparagraph and associated subparagraphs below to specify schedule-programming capability required for system.  Some manufacturers produce only low-capacity systems.  Specifying high system functionality increases memory requirements and costs and tends to reduce competition.

9. System shall be capable of programming multiple independent event schedules into memory and running them simultaneously for different output circuits.

a. Quantity of Programmable Schedules:  [Three] [Four] [Eight] [18] [250], minimum.

b. Number of Weekly Events That Can Be Programmed for Each Schedule:  [64] [128] [300] [600] [2500], minimum.

c. Simultaneous operation of independent schedules shall be limited only by the number of signal-device and equipment-switching output circuits.

Feature in subparagraph below, sometimes called "calendar programming," allows for programming of holiday-schedule changes up to a year in advance so they occur automatically.  Horn, bell, and other device circuits are automatically turned off at the beginning of each preprogrammed holiday period, and the system automatically reverts to the regular schedule at the end of the period.  This feature requires a more powerful microprocessor, is not available from some manufacturers, and may involve a cost premium.

d. Advance Programming for Automatic Holiday Schedule Changes:  Number of schedule changes that can be programmed to suit holidays and vacations shall be [10] [16] [50] [100], and each change may be programmed up to a year in advance to occur on any day of the calendar year.

Diagnostics in first subparagraph below are available on more expensive and complex systems.

10. System and Equipment Diagnostics:  An integral program shall automatically check functioning of LEDs, switches, input keys, central processor, read-only memory, random access memory, and output circuits.  A display on the control panel[ or a remote computer with the proper access code] shall indicate failure by identifying faulty component or circuit and shall recommend corrective action.

11. Daylight Savings Time Correction:  [Manually initiated] [Programmable for automatic correction].

12. Adjustments to Master Clock Output Signals:  Duration of momentary signal shall be individually programmable for each signal and equipment-control output circuit from 1 to 99 seconds.  Signals shall be programmable for either on or off switching to suit equipment-operation scheduling.

1.5 SUBMITTALS

A. Product Data:  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes (including available colors) for each product indicated and describe features and operating sequences, both automatic and manual, for the following:

1. Master unit.

2. Indicating clocks.

3. Signal equipment.

4. Equipment enclosures and back boxes.

5. Accessory components.

B. Shop Drawings:

1. Wiring diagrams to detail power, signal, control, and correction circuits.  Identify terminals and wiring color-codes to facilitate installation, operation, and maintenance.  Indicate recommended wire types and sizes, and circuiting arrangements for field-installed system wiring.  Show protection from overcurrent, static discharge, and voltage surge.

Retain two subparagraphs and associated subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Electrical Supports and Seismic Restraints."

2. Details of seismic restraints including mounting, anchoring, and fastening devices for the following system components:

a. Surface-mounted and semirecessed secondary indicating clocks.

b. Master clock [enclosures] [mounting racks].

c. Clock circuit power boosters.

3. Details of seismic strengthening of master clock [enclosures] [mounting racks].

Retain subparagraph below if an electronic-equipment mounting rack is specified for mounting of master clock and seismic criteria apply to Project.

4. Dimensioned Outline Drawings of Mounting Rack for Master Clock:  Show internal seismic bracing, and locate center of gravity of fully equipped and assembled unit.  Locate and describe mounting and anchorage provisions.

Retain paragraph and subparagraphs below if Samples are required by Architect.

C. Samples for Initial Selection:  Include the following:

1. Manufacturer's color photographs or color chips showing the full range of colors available for clocks, signal equipment, and control panels.

2. Representative operating models of clock type <Insert designations of clocks for which Samples are required>.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Electrical Supports and Seismic Restraints."

D. Manufacturer Seismic Qualification Certification:  Submit certification that master clock system components and their mounting and anchorage provisions are designed to remain in place without separation of any parts when subjected to the seismic forces defined in Division 16 Section "Electrical Supports and Seismic Restraints."  Include the following:

1. Basis for Certification:  Indicate whether certification is based on actual test of assembled components or on calculation.

2. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For Installer and manufacturer.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For clock and program control to include in emergency, operation, and maintenance manuals.

1.6 QUALITY ASSURANCE

Retain first paragraph below if required and available at Project location.

A. Installer Qualifications:  Master clock manufacturer's authorized representative who is trained and approved for installation and maintenance of units required for this Project.

B. Manufacturer Qualifications:  A qualified manufacturer.  Maintain, within <Insert number> miles (<Insert number> km) of Project site, a service center capable of providing training, parts, and emergency maintenance repairs.

C. Source Limitations:  Obtain master and secondary clocks and signal-device-control components through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NFPA 70 for components and installation.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. American Time & Signal Co.

2. Dukane Corporation; Communications Systems Div.

3. Lathem Time.

4. Midwest-Time Control, Inc.

5. National Time & Signal Corporation.

6. Rauland-Borg Corporation.

7. Sapling Company, Inc. (The).

8. Simplex Time Recorder Co.

9. Standard Electric Time Corp.; Unit of Faraday, Inc.

10. Telecor Inc.

11. <Insert manufacturer's name.>

2.2 MASTER CLOCK

A. Description:  Microprocessor-based, software-controlled unit complying with Class A device requirements in 47 CFR 15, and having the following components and features:

Edit subparagraphs and associated subparagraphs below to suit Project.  Delete items not required; add others as necessary.  Delete first subparagraph if programming is performed only at a remote PC or at one associated with the system.  PCs are not specified in this Section.  Coordinate with Part 1 "System Description" Article and with Drawings.

1. Programming and control switches.

2. Informational Display:  LED or backlit LCD type.

a. Normally shows current time[, date, and day of week] display.

Delete first subparagraph below if programming is performed only at a PC.

b. Provides programming cues when system is being programmed.

3. Output Circuits for Power and Correction of Secondary Indicating Clocks:

Retain one of first two subparagraphs below to suit type(s) of correction circuits required for secondary indicating clocks specified (and existing clocks to be served by the new system if any).  Retain "digital" option in first subparagraph if analog and digital synchronous clocks are to be mixed on the same power and correction circuit.  Retain second subparagraph if permissible for digital clocks to have separate circuits for power and correction.

a. Wired Synchronous Clock Power and Correction Circuits:  For [analog] [digital] [analog and digital] clocks; minimum of [one] [two] <Insert number> required.  Relay controlled.

b. Wired Synchronous Digital Clock Power and Correction Circuits:  [One] <Insert number> required.

c. Existing Clock Power and Correction Circuit:  An output circuit suitable for <Insert description of type of existing power and correction circuit and number of clocks to be connected>.

Retain subparagraph below for systems that have secondary clocks with RS485 or similar data-line correction circuits.  Most manufacturers offer digital clocks with this feature.  One manufacturer offers both digital and analog secondary clocks that can be corrected by data line.  If data-line correction is permissible for both digital and analog clocks, delete "digital" in subparagraph below.  Coordinate with Drawings and indicate separate power connections to these clocks.

4. Data Output Port for[ Digital] Secondary Clock Correction Circuit:  RS485 or similar circuit for scheduled periodic correction signals.

Retain first two subparagraphs below if master clock is indicated to communicate with local or remote PC or other device for programming or synchronizing with NIST or UTC time signals.

5. Modem and PC interface software suitable for [remote programming] [automatic NIST or UTC synchronization] [remote programming and automatic NIST or UTC synchronization].

6. RS232 data communications port.

7. Circuits for audible[ and Visual] signal devices:  Relay controlled, manually switchable, using controls on master clock.  Rated 120-V ac, [5] [10] A minimum.  A minimum of [two] [four] [six] [eight] <Insert number> circuits.

8. Circuits for Programmable Switching of Remote Equipment and Circuits:  Relay controlled, manually switchable, using controls on master clock.  Rated 120-V ac, [5] [10] A minimum.  A minimum of [two] [four] [six] [eight] <Insert number> circuits.

9. Power Supplies:  Capacity for internal loads and power and correction circuits of connected clocks.

Retain one of two subparagraphs below and edit to suit Project.  Coordinate with Drawings by indicating rack-mounting or surface, semirecessed, or flush cabinet.

10. Enclosure:  Metal cabinet with locking front panel.  When cabinet is locked, display indication shall be visible on or through front panel face.  Arrange cabinet for surface, semirecessed, or flush mounting as indicated.

11. Housing:  Rack-mounting metal enclosure with display indication visible on front panel face.

If seismic criteria apply, retain first subparagraph below with either of two subparagraphs above.

a. Reinforce mounting and attachment capable of resisting seismic forces described in Division 16 Section "Electrical Supports and Seismic Restraints."

12. Battery Backup for Time Base:  Lithium battery to maintain the timekeeping function and retain the programs in memory during outage of normal ac power supply for up to 10 years.

Retain below for installations requiring components that are electrically robust and where assured resistance to natural electrostatic discharge is required.  Also retain for clock system components that are interconnected with nurse-call or code-blue systems.  Edit to suit Project.  Some manufacturers do not test master clocks for electrostatic discharge resistance; most do not test ordinary secondary clocks for this attribute.  See Evaluations.

13. Electrostatic Discharge Resistance:  Master clock[ and secondary indicating clocks] shall be tested and certified according to IEC 61000-4-2 in both human discharge and direct injection modes.

2.3 SECONDARY INDICATING CLOCKS, GENERAL

Retain one or both paragraphs and associated subparagraphs below for new construction.  Retain third paragraph for renovations and additions where existing minute impulse clocks are to be reused.

A. Analog Clock:  Equipped with a sweep second hand.  Movement shall be driven by self-starting, permanently lubricated, sealed synchronous motor equipped with a correcting solenoid actuator, or be a microprocessor-based, second impulse unit, compatible with the master clock.

Coordinate paragraph and subparagraphs below with Drawings.  If both 2.5- and 4-inch (64- and 102-mm) clocks are used, indicate display height of each unit on Drawings.

B. Digital Clock:  Microprocessor-controlled unit complying with Class A device requirements in 47 CFR 15, with red LED digital time display of hours, minutes[, and seconds].

Retain one of first two subparagraphs below.

1. Display Height:  2.5-Inch (64-mm) Clock:  Hour and minute numerals readable at 50 feet (15 m).

2. Display Height:  4-Inch (102-mm) Clock:  Hour and minute numerals readable at 100 feet (30 m).

3. Display Format:  Selectable between 12-hour with "PM" LED display and 24-hour formats.

4. Connections for Power and Correction:

Retain one of two subparagraphs and associated subparagraphs below.  See Evaluations for discussion of these alternatives.

a. Wired synchronous connection to master clock for both operating power and correction.

Retain one of two subparagraphs below if digital clocks must display correct time immediately on restoration of power after an outage without waiting for the next regular correction cycle.  Feature in second subparagraph does not accommodate longer-duration outages but avoids ongoing maintenance associated with batteries; it may not be available from all manufacturers.

1) Time-Base Backup:  Internal alkaline battery shall back up internal time base to maintain timekeeping during outages of up to six days' duration.

2) Time-Base Backup:  Internal capacitor shall back up internal time base to maintain timekeeping during outages of up to 12 hours' duration.

If retaining subparagraph below, coordinate with Drawings to indicate separate clock operating power supply connections not normally specified in this Section.

b. Correction by RS485 or similar data line, with operating power supplied over a separate connection.

Plug connector in paragraph below facilitates maintenance and is either standard or an optional feature with most suppliers.

C. Connection Provision for Secondary Indicating Clocks:  [Plug connector] [Wire pigtail or compression splice].

Retain paragraph below if some clocks are mounted in modular architectural panels or housings.  Revise to suit Project.  Coordinate with Drawings and other Sections.

D. Provision for Modular Panel Installation:  Equip designated clock for panel mounting.  Mount flush or semirecessed with arrangement and trim as indicated.  Coordinate wiring with other modular panel components, including [room lighting switches] [intercom devices] [convenience outlets] [speaker] and other similar devices.

Retain below if some clocks are mounted in public-address speaker panels or housings used for programmed tone signals.  Revise to suit Project.  Coordinate with Drawings and with Division 16 Section "Public Address and Music Equipment."

E. Provision for Time-Tone-Unit Installation:  Equip indicated clocks for housing or mounting in an acoustically treated and baffled speaker compartment specified in Division 16 Section "Public Address and Music Equipment."

2.4 DETAILED REQUIREMENTS FOR SECONDARY INDICATING CLOCKS

Retain this Article to describe each type of secondary clock in Project.  Delete if detailed descriptions of secondary clocks are included on Drawings or are specified elsewhere.  Revise to suit Project.  If secondary clocks are described in schedules on Drawings, refer to the sample schedule at the end of the Evaluations.

Copy paragraph and subparagraphs below and edit for each type of clock required.  Use these designations on Drawings to show where each clock type is required.

A. Clock Type <Insert designation used on Drawings>:  [Analog] [Digital].

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Products:

a. <Insert manufacturer's name; product name or designation.>

2. Face Configuration:  [Single] [Double] face.

3. Mounting:  [Recessed] [Semirecessed] [Pendant] [Surface] [Suspended] [Within time-tone unit] [Within modular panel] <Insert mounting height of pendant, wall, and suspended clocks>.

Retain subparagraphs below if needed to describe important features.

4. Nominal Dimensions:  <Insert depth and nominal diameter or height and width in inches (mm).>

5. External Finish:  <Insert description, including types and colors.>

6. Trim and Hardware:  <Describe trim items and desired optional features.>

7. Special Environmental Conditions:  <Describe conditions such as corrosive, damp, or wet locations.>

8. Other Requirements:  <Insert optional or special characteristics.>

Retain first two subparagraphs below for analog clocks.

9. Crystal:  Clear [glass] [acrylic] [polycarbonate].

10. Other Features:  <Insert special features>.

11. Digital Clock Lens:  Antiglare acrylic material.

Clock type below is often used as an operating room timer in medical facilities.  For applications requiring other features, edit to suit Project.  Coordinate with Drawings.

B. Interval-Timer Clock:  Digital microprocessor-controlled, 4-inch (102-mm) unit with 2.5-inch (64-mm), red LED digital display for hours and minutes and 1.3-inch (33-mm) display for seconds; a separately mounted, mode-control switch; and the following features:

1. Display Visibility:  Hour and minute numerals readable at [30 feet (10 m)] <Insert distance> in normal ambient light.

2. Operating Modes:

a. Normal:  Clock operates as a regular secondary system clock, displaying corrected time in normal display configuration, selectable between 12- and 24-hour formats, with "PM" LED display for 12-hour format.

b. Count-Down or Count-Up Timer:  Selected by mode control switch count-up and count-down positions, and capable of being preset at the mode control station.

c. Code Blue:  Automatically selected by a signal through a wiring connection from [the code-blue system] <Insert another source for the initiating signal>.  This signal captures control of the clock regardless of current mode or correction status and instantly initiates count-up operation, starting at time 00:00:00.  While in this mode, other clock functions, including correction, shall run in the background.  The clock shall revert to normal operating mode when the initiating signal system is reset.

3. Mode Selector Switch:  Pushbutton or rotary, multiposition type, flush mounted; with start, stop, and reset capability in both count-up and count-down modes.

4. Audible tone signal:  Housed in clock or mode-selector-switch box.  Sounds at end of preset up or down count.

2.5 PROGRAM SIGNAL DEVICES

Select from signaling devices in this Article.  Coordinate with Drawings.  See Evaluations.

A. Bells:  Heavy-duty, modular, vibrating type with the following sound output ratings measured at 10 feet (3 m):

Retain sizes in subparagraphs below to suit Project.

1. 4-Inch (100-mm) Bell:  90 dB.

2. 6-Inch (150-mm) Bell:  95 dB.

3. 10-Inch (250-mm) Bell:  104 dB.

B. Chimes:  Heavy-duty, modular, vibrating chimes with polished-chrome tone bar and enamel-finished housing.  Minimum sound output rating measured at 10 feet (3 m) shall be 75 dB.

C. Clock Buzzers:  Adjustable output signal device designed for mounting within clock housing or outlet box.

1. Sound Output Rating Measured at 3 Feet (1 m):  75 dB.

2. Audible Tone Frequency:  Manufacturer's standard between 120 Hz and 2 kHz.

D. Horns:  Modular, adjustable-output, vibrating type with minimum full-intensity-rated sound output of 103 dB measured at 10 feet (3 m).

E. Projector Horns:  Adjustable-output, vibrating-type units with [single] [double] projector arranged to channel the sound in the direction of the projector axis, and with minimum full-intensity-rated sound output of 104 dB measured at 10 feet (3 m).

F. Loudspeakers for Audible Tones:  Refer to Division 16 Section "Public Address and Music Equipment."

Retain "blue" or "yellow" in paragraph below to suit authorities having jurisdiction or preference.

G. Visible Signal Devices:  Strobe lights with [blue] [yellow] polycarbonate lens and xenon flash tube with lens mounted on an aluminum faceplate and the word "Program" engraved in letters at least 1 inch (25 mm) high on lens.  Lamp unit shall have a minimum rated light output of 75 candela.

H. Combination Audible and Visible Signal Devices:  Factory-integrated horn and strobe light in a single mounting assembly.

I. Outdoor Signal Equipment:  Weatherproof models listed for outdoor use.

J. Mounting Arrangement for Signal Devices:  Designed for attachment with screws on the mounting plate of a flush-mounted back box, unless otherwise indicated.

K. Enclosures for Flush-Mounting Bells and Horns:  Enclosure, mounting plate, and grille assembly shall be furnished by device manufacturer to match features of the device to be mounted.  Enclosure shall be recessed in wall, completely enclosing the device, with the grille mounting over the open side of the enclosure and flush with the wall.

L. Connection Provision for Signal Indicating Devices:  [Plug connector] [Wire pigtail or compression splice].

2.6 CLOCK CIRCUIT POWER BOOSTER

Retain this Article for Projects where the length of clock circuits and the number of clocks per circuit may require an impractically large clock circuit wire to keep voltage drop within specified limits.  Booster may also be used to connect groups of existing clocks to new circuits, where the correction method may be the same but the voltages differ.

A. Description:  Transformer power supply, mounted in steel cabinet with hinged door, and having fuse-protected input and output circuits.

2.7 BACK BOXES FOR SECONDARY INDICATING CLOCKS AND PROGRAM DEVICES

A. Description:  Box and coverplate assembly shall be furnished by device manufacturer and be suitable for device to be mounted.  Back boxes shall be equipped with knockouts and hanger straps or mounting adapters arranged for flush mounting device, unless otherwise indicated.

2.8 GUARDS

Retain this Article if clocks or signal devices are located where they might be exposed to physical damage.  Coordinate with Drawings to indicate which units require guards.

A. Description:  Formed-steel wire, shaped to fit around guarded device, with 1-inch (25-mm) maximum clearance.

1. Mounting Provisions:  Fixed tabs, welded to guard and arranged for screw attachment to mounting surface.

2. Finish for Indoor Devices:  [Clear] <Insert desired finish color> epoxy lacquer over zinc plating.

3. Finish for Outdoor Devices:  [Black] <Insert desired finish color> powder coat over zinc plating and primer.

2.9 RACK-MOUNTING PROVISION FOR MASTER CLOCK

Retain this Article if master clock is specified to be rack mounting and rack is not specified in another Section, such as Division 16 Sections "Public Address and Music Equipment" or "School Intercom and Program Equipment."

A. Equipment Cabinet:  Rack type, [floor] [wall] mounting.  Comply with EIA-310-D and the following:

Retain rear doors in first subparagraph below for floor-mounting rack with rear access.  Coordinate with Drawings.

1. Cabinet Housing:  Construct of 0.0478-inch (1.2-mm) steel, minimum, with front[ and rear] doors with manufacturer's standard tumbler locks, keyed alike.

a. Front door shall have a clear panel in front of the master clock display.

b. Housing shall enclose master clock and auxiliary clock system components, plus a minimum of [20 percent] <Insert percent> spare capacity for future equipment.

2. Forced Ventilation:  Internal low-noise fan with a filtered intake vent.  Connect fan to operate from 105- to 130-V ac, 60 Hz; separately fused and switchable and arranged to be powered when main cabinet power switch is on.

Retain subparagraph above or below depending on amount of heat-producing equipment to be housed.

3. Natural Ventilation:  Ventilated rear and sides with louvers and solid top.

Retain first two subparagraphs below for freestanding floor-mounting cabinet.

4. Arrange inputs, outputs, interconnections, and test points so they are accessible at rear of rack for maintenance and testing, with each item removable from rack without disturbing other items or connections.

5. Service Light:  At top rear of rack and controlled by an adjacent switch.

6. Blank Panels:  Cover empty space in equipment racks so entire front of rack is occupied by equipment or panels.

7. Finish:  Uniform, baked-enamel, [manufacturer's standard color] <Insert color preference> finish over rust-inhibiting primer.

8. Power-Control Panel:  On front of equipment housing; with master power on-off switch and pilot light, and socket for a 5-A, indicating, cartridge fuse for rack equipment power.

9. Vertical Plug Strip:  Grounded receptacles, 12 inches (300 mm) o.c. the full height of rack, to supply rack-mounting equipment.

Coordinate below with Drawings for branch-circuit wiring.

10. Maintenance Receptacles:  Duplex convenience outlet with supply terminals separate from equipment plug strip and located in front of rack.

2.10 WIRE AND CABLE

Coordinate this Article with Drawings.

A. Conductors:  Insulated copper, with minimum sizes as recommended by the connected device manufacturer.  Voltage drop for signal, control, and clock correction circuits shall not exceed 10 percent under peak load conditions.

B. 120-V ac and Class 1 Signal and Control Circuits:  Stranded single conductors of size recommended by system manufacturer.  Materials and installation requirements are specified in Division 16 Section "Conductors and Cables."

C. Classes 2 and 3 Signal and Control Circuits:  Single conductor or twisted-pair cable, unshielded, unless manufacturer recommends shielded cable.

Retain paragraph below if RS232 or RS485 connections are specified.

D. Data Circuits:  Category 3 minimum, unshielded, twisted-pair cable, unless manufacturer recommends shielded cable.

Delete first paragraph below if system wiring is in raceway.

E. Plenum Cable:  Listed and labeled for use in air-handling spaces, plenums, and plenum ceilings.

F. Conductor Color-Coding:  Uniformly identified and coordinated with wiring diagrams.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain first paragraph below if seismic requirements apply.

A. Mount system components with fastening methods and devices designed to resist the seismic forces indicated in Division 16 Section "Electrical Supports and Seismic Restraints."

B. Wiring:  Install 60-Hz wiring according to NFPA 70.  Install data cable complying with TIA/EIA-568-A.  Install number of conductors recommended by system manufacturer for functions indicated, and as follows:

1. Conceal wiring except in unfinished spaces.

Retain one of three subparagraphs below.  Revise to suit Project.

2. Wiring Method:  Install wiring in raceways.

3. Wiring Method:  Install wiring in raceways except for Classes 2 and 3 remote-control and signaling circuits, as defined in NFPA 70, if installed in accessible ceiling spaces and hollow gypsum-board partitions, where unenclosed wiring method may be used.  Install listed plenum cable for Classes 2 and 3 wiring in environmental air spaces, including plenum ceilings.

4. Wiring Method:  Install metal-clad cable except for Classes 2 and 3 remote-control and signaling circuits, as defined in NFPA 70, if installed in accessible ceiling spaces and hollow gypsum-board partitions, where unenclosed wiring method may be used.  Install listed plenum cable for Classes 2 and 3 wiring in environmental air spaces, including plenum ceilings.

C. Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess; use lacing bars and distribution spools.

3.2 ELECTRICAL CONNECTIONS

A. Make splices, taps, and terminations on numbered terminal strips in junction, pull and outlet boxes, terminal cabinets, and equipment enclosures.

B. Use [plug connectors] [splices] for connections to clocks and signal devices.

C. Ground clocks, programming equipment, and conductor and cable shields to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

3.3 IDENTIFICATION

A. Comply with Division 16 Section "Electrical Identification."

B. Color-code wire and apply wire and cable marking tape to designate wires and cables so they are uniformly identified and coordinated with wiring diagrams throughout the system.

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of three options to suit Project; delete all to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in programming] [, and to assist in programming and field testing].  Report results in writing.

B. Perform the following field adjustments, tests, and inspections and prepare test reports:

1. Perform operational-system tests to verify compliance with the Specifications and make adjustments to bring system into compliance.  Include operation of all modes of clock correction and all programming and manually programmed signal and relay operating functions.

2. Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

C. Remove and replace malfunctioning units and retest as specified above.

3.5 PROGRAMMING AND ADJUSTMENTS

A. Program system according to Owner's requirements.  Set system so signal devices operate on Owner-required schedules and are activated for durations selected by Owner.  Program equipment-control output circuits to suit Owner's operating schedule for equipment controlled.

B. Adjust sound-output level of adjustable signal devices to suit Owner's requirements.

C. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance for adjusting and reprogramming system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project outside normal occupancy hours for this purpose.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain clock-and-program-control system components.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 13810

CLOCK AND PROGRAM CONTROL
13810 - 1

