Copyright 2005 AIA
MASTERSPEC
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15062 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following hangers and supports for HVAC system piping and equipment:

Adjust list below to suit Project.

1. Steel pipe hangers and supports.

2. Trapeze pipe hangers.

3. Fiberglass pipe hangers.

4. Metal framing systems.

5. Fiberglass strut systems.

6. Thermal-hanger shield inserts.

7. Fastener systems.

8. Pipe stands.

9. Equipment supports.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 5 Section "Metal Fabrications" for structural-steel shapes and plates for trapeze hangers for pipe and equipment supports.

2. Division 13 Section "Fire-Suppression Piping" for pipe hangers for fire-protection piping.

3. Division 15 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for vibration isolation devices.

4. Division 15 Section "Expansion Fittings and Loops for HVAC Piping" for pipe guides and anchors.

5. Division 15 Section(s) "[Metal Ducts] [Metal Ducts" and "Nonmetal Ducts] [Nonmetal Ducts]" for duct hangers and supports.

1.3 DEFINITIONS

Retain abbreviation and terms that remain after this Section has been edited.

A. MSS:  Manufacturers Standardization Society for The Valve and Fittings Industry Inc.

B. Terminology:  As defined in MSS SP-90, "Guidelines on Terminology for Pipe Hangers and Supports."

1.4 PERFORMANCE REQUIREMENTS

Delete this Article if not required.

A. Design supports for multiple pipes, including pipe stands, capable of supporting combined weight of supported systems, system contents, and test water.

B. Design equipment supports capable of supporting combined operating weight of supported equipment and connected systems and components.

C. Design seismic-restraint hangers and supports for piping and equipment[ and obtain approval from authorities having jurisdiction].

1.5 SUBMITTALS

A. Product Data:  For the following:

Adjust list below to suit Project.

1. Steel pipe hangers and supports.

2. Fiberglass pipe hangers.

3. Thermal-hanger shield inserts.

4. Powder-actuated fastener systems.

B. Shop Drawings:[  Signed and sealed by a qualified professional engineer.] Show fabrication and installation details and include calculations for the following:

Adjust list below to suit Project.

1. Trapeze pipe hangers.  Include Product Data for components.

2. Metal framing systems.  Include Product Data for components.

3. Fiberglass strut systems.  Include Product Data for components.

4. Pipe stands.  Include Product Data for components.

5. Equipment supports.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

1.6 QUALITY ASSURANCE

Delete this Article if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

Retain first paragraph below if only one AWS standard is applicable.  Retain second paragraph if more than one AWS standard is referenced.

A. Welding:  Qualify procedures and personnel according to [AWS D1.1, "Structural Welding Code--Steel."] [AWS D1.3, "Structural Welding Code--Sheet Steel."] [AWS D1.4, "Structural Welding Code--Reinforcing Steel."] [ASME Boiler and Pressure Vessel Code:  Section IX.]

B. Welding:  Qualify procedures and personnel according to the following:

Retain applicable standards in subparagraphs below.

1. AWS D1.1, "Structural Welding Code--Steel."

2. AWS D1.2, "Structural Welding Code--Aluminum."

3. AWS D1.3, "Structural Welding Code--Sheet Steel."

4. AWS D1.4, "Structural Welding Code--Reinforcing Steel."

5. ASME Boiler and Pressure Vessel Code:  Section IX.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 STEEL PIPE HANGERS AND SUPPORTS

A. Description:  MSS SP-58, Types 1 through 58, factory-fabricated components.  Refer to Part 3 "Hanger and Support Applications" Article for where to use specific hanger and support types.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. AAA Technology & Specialties Co., Inc.

2. Bergen-Power Pipe Supports.

3. B-Line Systems, Inc.; a division of Cooper Industries.

4. Carpenter & Paterson, Inc.

5. Empire Industries, Inc.

6. ERICO/Michigan Hanger Co.

7. Globe Pipe Hanger Products, Inc.

8. Grinnell Corp.

9. GS Metals Corp.

10. National Pipe Hanger Corporation.

11. PHD Manufacturing, Inc.

12. PHS Industries, Inc.

13. Piping Technology & Products, Inc.

14. Tolco Inc.

15. <Insert manufacturer's name.>

C. Galvanized, Metallic Coatings:  Pregalvanized or hot dipped.

D. Nonmetallic Coatings:  Plastic coating, jacket, or liner.

E. Padded Hangers:  Hanger with fiberglass or other pipe insulation pad or cushion for support of bearing surface of piping.

2.3 TRAPEZE PIPE HANGERS

Trapeze pipe hangers in this Article require calculation and detail of each unit.

A. Description:  MSS SP-69, Type 59, shop- or field-fabricated pipe-support assembly made from structural-steel shapes with MSS SP-58 hanger rods, nuts, saddles, and U-bolts.

2.4 FIBERGLASS PIPE HANGERS

A. Clevis-Type, Fiberglass Pipe Hangers:  Similar to MSS Type 1, steel pipe hanger except hanger is made of fiberglass and continuous-thread rod and nuts are made of [polyurethane] [polyurethane or stainless steel] [stainless steel] <Insert other>.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. B-Line Systems, Inc.; a division of Cooper Industries.

b. Champion Fiberglass, Inc.

c. Cope, T. J., Inc.; Tyco International, Ltd.

d. Seasafe, Inc.

e. Unistrut Corp.; Tyco International, Ltd.

f. Wesanco, Inc.

g. <Insert manufacturer's name.>

B. Strap-Type, Fiberglass Pipe Hangers:  Made of fiberglass loop with stainless-steel continuous-thread rod, nuts, and support hook.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Plasti-Fab, Inc.

b. <Insert manufacturer's name.>

2.5 METAL FRAMING SYSTEMS

Metal framing systems in this Article require calculation and detail of each unit.

A. Description:  MFMA-3, shop- or field-fabricated pipe-support assembly made of steel channels and other components.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. B-Line Systems, Inc.; a division of Cooper Industries.

2. ERICO/Michigan Hanger Co.; ERISTRUT Div.

3. GS Metals Corp.

4. Power-Strut Div.; Tyco International, Ltd.

5. Thomas & Betts Corporation.

6. Tolco Inc.

7. Unistrut Corp.; Tyco International, Ltd.

8. <Insert manufacturer's name.>

C. Coatings:  Manufacturer's standard finish, unless bare metal surfaces are indicated.

D. Nonmetallic Coatings:  Plastic coating, jacket, or liner.

2.6 FIBERGLASS STRUT SYSTEMS

Fiberglass strut systems in this Article require calculation and detail of each unit.

A. Description:  Shop- or field-fabricated pipe-support assembly, similar to MFMA-3, made of fiberglass channels and other components.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. B-Line Systems, Inc.; a division of Cooper Industries.

2. Champion Fiberglass, Inc.

3. Cope, T. J., Inc.; Tyco International Ltd.

4. Seasafe, Inc.

5. <Insert manufacturer's name.>

2.7 THERMAL-HANGER SHIELD INSERTS

A. Description:  100-psig- (690-kPa-) minimum, compressive-strength insulation insert encased in sheet metal shield.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

B. [Available ]Manufacturers:

1. Carpenter & Paterson, Inc.

2. ERICO/Michigan Hanger Co.

3. PHS Industries, Inc.

4. Pipe Shields, Inc.

5. Rilco Manufacturing Company, Inc.

6. Value Engineered Products, Inc.

7. <Insert manufacturer's name.>

C. Insulation-Insert Material for Cold Piping:  [Water-repellent treated, ASTM C 533, Type I calcium silicate] [Water-repellent treated, ASTM C 533, Type I calcium silicate or ASTM C 552, Type II cellular glass] [ASTM C 552, Type II cellular glass] with vapor barrier.

D. Insulation-Insert Material for Hot Piping:  [Water-repellent treated, ASTM C 533, Type I calcium silicate] [Water-repellent treated, ASTM C 533, Type I calcium silicate or ASTM C 552, Type II cellular glass] [ASTM C 552, Type II cellular glass].

E. For Trapeze or Clamped Systems:  Insert and shield shall cover entire circumference of pipe.

F. For Clevis or Band Hangers:  Insert and shield shall cover lower 180 degrees of pipe.

G. Insert Length:  Extend 2 inches (50 mm) beyond sheet metal shield for piping operating below ambient air temperature.

2.8 FASTENER SYSTEMS

Verify suitability of fasteners in this Article for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

A. Powder-Actuated Fasteners:  Threaded-steel stud, for use in hardened portland cement concrete with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Hilti, Inc.

b. ITW Ramset/Red Head.

c. Masterset Fastening Systems, Inc.

d. MKT Fastening, LLC.

e. Powers Fasteners.

f. <Insert manufacturer's name.>

B. Mechanical-Expansion Anchors:  Insert-wedge-type [zinc-coated] [stainless] steel, for use in hardened portland cement concrete with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. B-Line Systems, Inc.; a division of Cooper Industries.

b. Empire Industries, Inc.

c. Hilti, Inc.

d. ITW Ramset/Red Head.

e. MKT Fastening, LLC.

f. Powers Fasteners.

g. <Insert manufacturer's name.>

2.9 PIPE STAND FABRICATION

Pipe stands in this Article require calculation and detail of each unit.

A. Pipe Stands, General:  Shop or field-fabricated assemblies made of manufactured corrosion-resistant components to support roof-mounted piping.

B. Compact Pipe Stand:  One-piece plastic unit with integral-rod-roller, pipe clamps, or V-shaped cradle to support pipe, for roof installation without membrane penetration.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ERICO/Michigan Hanger Co.

b. MIRO Industries.

c. <Insert manufacturer's name.>

C. Low-Type, Single-Pipe Stand:  One-piece [plastic] [stainless-steel] base unit with plastic roller, for roof installation without membrane penetration.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. MIRO Industries.

b. <Insert manufacturer's name.>

D. High-Type, Single-Pipe Stand:  Assembly of base, vertical and horizontal members, and pipe support, for roof installation without membrane penetration.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. ERICO/Michigan Hanger Co.

b. MIRO Industries.

c. Portable Pipe Hangers.

d. <Insert manufacturer's name.>

2. Base:  [Plastic] [Stainless steel].

3. Vertical Members:  Two or more cadmium-plated-steel or stainless-steel, continuous-thread rods.

4. Horizontal Member:  Cadmium-plated-steel or stainless-steel rod with plastic or stainless-steel, roller-type pipe support.

E. High-Type, Multiple-Pipe Stand:  Assembly of bases, vertical and horizontal members, and pipe supports, for roof installation without membrane penetration.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Portable Pipe Hangers.

b. <Insert manufacturer's name.>

2. Bases:  One or more plastic.

3. Vertical Members:  Two or more protective-coated-steel channels.

4. Horizontal Member:  Protective-coated-steel channel.

5. Pipe Supports:  Galvanized-steel, clevis-type pipe hangers.

F. Curb-Mounting-Type Pipe Stands:  Shop- or field-fabricated pipe support made from structural-steel shape, continuous-thread rods, and rollers for mounting on permanent stationary roof curb.

2.10 EQUIPMENT SUPPORTS

Equipment supports in this Article require calculation and detail of each unit.

A. Description:  Welded, shop- or field-fabricated equipment support made from structural-steel shapes.

2.11 MISCELLANEOUS MATERIALS

A. Structural Steel:  ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

B. Grout:  ASTM C 1107, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink and nonmetallic grout; suitable for interior and exterior applications.

1. Properties:  Nonstaining, noncorrosive, and nongaseous.

2. Design Mix:  5000-psi (34.5-MPa), 28-day compressive strength.

PART 3 -  EXECUTION

3.1 HANGER AND SUPPORT APPLICATIONS

A. Specific hanger and support requirements are specified in Sections specifying piping systems and equipment.

B. Comply with MSS SP-69 for pipe hanger selections and applications that are not specified in piping system Sections.

C. Use hangers and supports with galvanized, metallic coatings for piping and equipment that will not have field-applied finish.

D. Use nonmetallic coatings on attachments for electrolytic protection where attachments are in direct contact with copper tubing.

E. Use padded hangers for piping that is subject to scratching.

F. Horizontal-Piping Hangers and Supports:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Adjustable, Steel Clevis Hangers (MSS Type 1):  For suspension of noninsulated or insulated stationary pipes, NPS 1/2 to NPS 30 (DN 15 to DN 750).

2. Yoke-Type Pipe Clamps (MSS Type 2):  For suspension of 120 to 450 deg F (49 to 232 deg C) pipes, NPS 4 to NPS 16 (DN 100 to DN 400), requiring up to 4 inches (100 mm) of insulation.

3. Carbon- or Alloy-Steel, Double-Bolt Pipe Clamps (MSS Type 3):  For suspension of pipes, NPS 3/4 to NPS 24 (DN 20 to DN 600), requiring clamp flexibility and up to 4 inches (100 mm) of insulation.

4. Steel Pipe Clamps (MSS Type 4):  For suspension of cold and hot pipes, NPS 1/2 to NPS 24 (DN 15 to DN 600), if little or no insulation is required.

5. Pipe Hangers (MSS Type 5):  For suspension of pipes, NPS 1/2 to NPS 4 (DN 15 to DN 100), to allow off-center closure for hanger installation before pipe erection.

6. Adjustable, Swivel Split- or Solid-Ring Hangers (MSS Type 6):  For suspension of noninsulated stationary pipes, NPS 3/4 to NPS 8 (DN 20 to DN 200).

7. Adjustable, Steel Band Hangers (MSS Type 7):  For suspension of noninsulated stationary pipes, NPS 1/2 to NPS 8 (DN 15 to DN 200).

8. Adjustable Band Hangers (MSS Type 9):  For suspension of noninsulated stationary pipes, NPS 1/2 to NPS 8 (DN 15 to DN 200).

9. Adjustable, Swivel-Ring Band Hangers (MSS Type 10):  For suspension of noninsulated stationary pipes, NPS 1/2 to NPS 2 (DN 15 to DN 50).

10. Split Pipe-Ring with or without Turnbuckle-Adjustment Hangers (MSS Type 11):  For suspension of noninsulated stationary pipes, NPS 3/8 to NPS 8 (DN 10 to DN 200).

11. Extension Hinged or 2-Bolt Split Pipe Clamps (MSS Type 12):  For suspension of noninsulated stationary pipes, NPS 3/8 to NPS 3 (DN 10 to DN 80).

12. U-Bolts (MSS Type 24):  For support of heavy pipes, NPS 1/2 to NPS 30 (DN 15 to DN 750).

13. Clips (MSS Type 26):  For support of insulated pipes not subject to expansion or contraction.

14. Pipe Saddle Supports (MSS Type 36):  For support of pipes, NPS 4 to NPS 36 (DN 100 to DN 900), with steel pipe base stanchion support and cast-iron floor flange.

15. Pipe Stanchion Saddles (MSS Type 37):  For support of pipes, NPS 4 to NPS 36 (DN 100 to DN 900), with steel pipe base stanchion support and cast-iron floor flange and with U-bolt to retain pipe.

16. Adjustable, Pipe Saddle Supports (MSS Type 38):  For stanchion-type support for pipes, NPS 2-1/2 to NPS 36 (DN 65 to DN 900), if vertical adjustment is required, with steel pipe base stanchion support and cast-iron floor flange.

17. Single Pipe Rolls (MSS Type 41):  For suspension of pipes, NPS 1 to NPS 30 (DN 25 to DN 750), from 2 rods if longitudinal movement caused by expansion and contraction might occur.

18. Adjustable Roller Hangers (MSS Type 43):  For suspension of pipes, NPS 2-1/2 to NPS 20 (DN 65 to DN 500), from single rod if horizontal movement caused by expansion and contraction might occur.

19. Complete Pipe Rolls (MSS Type 44):  For support of pipes, NPS 2 to NPS 42 (DN 50 to DN 1050), if longitudinal movement caused by expansion and contraction might occur but vertical adjustment is not necessary.

20. Pipe Roll and Plate Units (MSS Type 45):  For support of pipes, NPS 2 to NPS 24 (DN 50 to DN 600), if small horizontal movement caused by expansion and contraction might occur and vertical adjustment is not necessary.

21. Adjustable Pipe Roll and Base Units (MSS Type 46):  For support of pipes, NPS 2 to NPS 30 (DN 50 to DN 750), if vertical and lateral adjustment during installation might be required in addition to expansion and contraction.

G. Vertical-Piping Clamps:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Extension Pipe or Riser Clamps (MSS Type 8):  For support of pipe risers, NPS 3/4 to NPS 20 (DN 20 to DN 500).

2. Carbon- or Alloy-Steel Riser Clamps (MSS Type 42):  For support of pipe risers, NPS 3/4 to NPS 20 (DN 20 to DN 500), if longer ends are required for riser clamps.

H. Hanger-Rod Attachments:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Steel Turnbuckles (MSS Type 13):  For adjustment up to 6 inches (150 mm) for heavy loads.

2. Steel Clevises (MSS Type 14):  For 120 to 450 deg F (49 to 232 deg C) piping installations.

3. Swivel Turnbuckles (MSS Type 15):  For use with MSS Type 11, split pipe rings.

4. Malleable-Iron Sockets (MSS Type 16):  For attaching hanger rods to various types of building attachments.

5. Steel Weldless Eye Nuts (MSS Type 17):  For 120 to 450 deg F (49 to 232 deg C) piping installations.

I. Building Attachments:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Steel or Malleable Concrete Inserts (MSS Type 18):  For upper attachment to suspend pipe hangers from concrete ceiling.

2. Top-Beam C-Clamps (MSS Type 19):  For use under roof installations with bar-joist construction to attach to top flange of structural shape.

3. Side-Beam or Channel Clamps (MSS Type 20):  For attaching to bottom flange of beams, channels, or angles.

4. Center-Beam Clamps (MSS Type 21):  For attaching to center of bottom flange of beams.

5. Welded Beam Attachments (MSS Type 22):  For attaching to bottom of beams if loads are considerable and rod sizes are large.

6. C-Clamps (MSS Type 23):  For structural shapes.

7. Top-Beam Clamps (MSS Type 25):  For top of beams if hanger rod is required tangent to flange edge.

8. Side-Beam Clamps (MSS Type 27):  For bottom of steel I-beams.

9. Steel-Beam Clamps with Eye Nuts (MSS Type 28):  For attaching to bottom of steel I-beams for heavy loads.

10. Linked-Steel Clamps with Eye Nuts (MSS Type 29):  For attaching to bottom of steel I-beams for heavy loads, with link extensions.

11. Malleable Beam Clamps with Extension Pieces (MSS Type 30):  For attaching to structural steel.

12. Welded-Steel Brackets:  For support of pipes from below, or for suspending from above by using clip and rod.  Use one of the following for indicated loads:

a. Light (MSS Type 31):  750 lb (340 kg).

b. Medium (MSS Type 32):  1500 lb (680 kg).

c. Heavy (MSS Type 33):  3000 lb (1360 kg).

13. Side-Beam Brackets (MSS Type 34):  For sides of steel or wooden beams.

14. Plate Lugs (MSS Type 57):  For attaching to steel beams if flexibility at beam is required.

15. Horizontal Travelers (MSS Type 58):  For supporting piping systems subject to linear horizontal movement where headroom is limited.

J. Saddles and Shields:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Steel Pipe-Covering Protection Saddles (MSS Type 39):  To fill interior voids with insulation that matches adjoining insulation.

2. Protection Shields (MSS Type 40):  Of length recommended in writing by manufacturer to prevent crushing insulation.

3. Thermal-Hanger Shield Inserts:  For supporting insulated pipe.

K. Spring Hangers and Supports:  Unless otherwise indicated and except as specified in piping system Sections, install the following types:

1. Restraint-Control Devices (MSS Type 47):  Where indicated to control piping movement.

2. Spring Cushions (MSS Type 48):  For light loads if vertical movement does not exceed 1-1/4 inches (32 mm).

3. Spring-Cushion Roll Hangers (MSS Type 49):  For equipping Type 41 roll hanger with springs.

4. Spring Sway Braces (MSS Type 50):  To retard sway, shock, vibration, or thermal expansion in piping systems.

5. Variable-Spring Hangers (MSS Type 51):  Preset to indicated load and limit variability factor to 25 percent to absorb expansion and contraction of piping system from hanger.

6. Variable-Spring Base Supports (MSS Type 52):  Preset to indicated load and limit variability factor to 25 percent to absorb expansion and contraction of piping system from base support.

7. Variable-Spring Trapeze Hangers (MSS Type 53):  Preset to indicated load and limit variability factor to 25 percent to absorb expansion and contraction of piping system from trapeze support.

8. Constant Supports:  For critical piping stress and if necessary to avoid transfer of stress from one support to another support, critical terminal, or connected equipment.  Include auxiliary stops for erection, hydrostatic test, and load-adjustment capability.  These supports include the following types:

a. Horizontal (MSS Type 54):  Mounted horizontally.

b. Vertical (MSS Type 55):  Mounted vertically.

c. Trapeze (MSS Type 56):  Two vertical-type supports and one trapeze member.

L. Comply with MSS SP-69 for trapeze pipe hanger selections and applications that are not specified in piping system Sections.

M. Comply with MFMA-102 for metal framing system selections and applications that are not specified in piping system Sections.

N. Use [powder-actuated fasteners] [or] [mechanical-expansion anchors] instead of building attachments where required in concrete construction.

3.2 HANGER AND SUPPORT INSTALLATION

A. Steel Pipe Hanger Installation:  Comply with MSS SP-69 and MSS SP-89.  Install hangers, supports, clamps, and attachments as required to properly support piping from building structure.

Each trapeze pipe hanger in first paragraph and subparagraphs below requires calculation and detail.

B. Trapeze Pipe Hanger Installation:  Comply with MSS SP-69 and MSS SP-89.  Arrange for grouping of parallel runs of horizontal piping and support together on field-fabricated trapeze pipe hangers.

1. Pipes of Various Sizes:  Support together and space trapezes for smallest pipe size or install intermediate supports for smaller diameter pipes as specified above for individual pipe hangers.

2. Field fabricate from ASTM A 36/A 36M, steel shapes selected for loads being supported.  Weld steel according to AWS D1.1.

C. Fiberglass Pipe Hanger Installation:  Comply with applicable portions of MSS SP-69 and MSS SP-89.  Install hangers and attachments as required to properly support piping from building structure.

Each metal framing system in paragraph below requires calculation and detail.

D. Metal Framing System Installation:  Arrange for grouping of parallel runs of piping and support together on field-assembled metal framing systems.

Each fiberglass strut system in first paragraph below requires calculation and detail.

E. Fiberglass Strut System Installation:  Arrange for grouping of parallel runs of piping and support together on field-assembled fiberglass struts.

F. Thermal-Hanger Shield Installation:  Install in pipe hanger or shield for insulated piping.

G. Fastener System Installation:

Verify suitability of fasteners in two subparagraphs below for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

1. Install powder-actuated fasteners for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick in concrete after concrete is placed and completely cured.  Use operators that are licensed by powder-actuated tool manufacturer.  Install fasteners according to powder-actuated tool manufacturer's operating manual.

2. Install mechanical-expansion anchors in concrete after concrete is placed and completely cured.  Install fasteners according to manufacturer's written instructions.

Each pipe stand in first paragraph and subparagraphs below requires calculation and detail.

H. Pipe Stand Installation:

1. Pipe Stand Types except Curb-Mounting Type:  Assemble components and mount on smooth roof surface.  Do not penetrate roof membrane.

2. Curb-Mounting-Type Pipe Stands:  Assemble components or fabricate pipe stand and mount on permanent, stationary roof curb.  Refer to Division 7 Section "Roof Accessories" for curbs.

I. Install hangers and supports complete with necessary inserts, bolts, rods, nuts, washers, and other accessories.

Each equipment support in first paragraph below requires calculation and detail.

J. Equipment Support Installation:  Fabricate from welded-structural-steel shapes.

K. Install hangers and supports to allow controlled thermal and seismic movement of piping systems, to permit freedom of movement between pipe anchors, and to facilitate action of expansion joints, expansion loops, expansion bends, and similar units.

L. Install lateral bracing with pipe hangers and supports to prevent swaying.

M. Install building attachments within concrete slabs or attach to structural steel.  Install additional attachments at concentrated loads, including valves, flanges, and strainers, [NPS 2-1/2 (DN 65)] <Insert other> and larger and at changes in direction of piping.  Install concrete inserts before concrete is placed; fasten inserts to forms and install reinforcing bars through openings at top of inserts.

N. Load Distribution:  Install hangers and supports so piping live and dead loads and stresses from movement will not be transmitted to connected equipment.

O. Pipe Slopes:  Install hangers and supports to provide indicated pipe slopes and so maximum pipe deflections allowed by ASME B31.1 (for power piping) and ASME B31.9 (for building services piping) are not exceeded.

P. Insulated Piping:  Comply with the following:

Specify parts as galvanized or painted, as required, in first three subparagraphs and associated subparagraphs below.  Other materials are available in place of wooden blocks.

1. Attach clamps and spacers to piping.

a. Piping Operating above Ambient Air Temperature:  Clamp may project through insulation.

b. Piping Operating below Ambient Air Temperature:  Use thermal-hanger shield insert with clamp sized to match OD of insert.

c. Do not exceed pipe stress limits according to ASME B31.1 for power piping and ASME B31.9 for building services piping.

2. Install MSS SP-58, Type 39, protection saddles if insulation without vapor barrier is indicated.  Fill interior voids with insulation that matches adjoining insulation.

a. Option:  Thermal-hanger shield inserts may be used.  Include steel weight-distribution plate for pipe NPS 4 (DN 100) and larger if pipe is installed on rollers.

High compressive-strength inserts may permit use of shorter shields or shields with less arc span.  Edit first subparagraph and associated subparagraph below to suit Project.

3. Install MSS SP-58, Type 40, protective shields on cold piping with vapor barrier.  Shields shall span an arc of 180 degrees.

a. Option:  Thermal-hanger shield inserts may be used.  Include steel weight-distribution plate for pipe NPS 4 (DN 100) and larger if pipe is installed on rollers.

4. Shield Dimensions for Pipe:  Not less than the following:

a. NPS 1/4 to NPS 3-1/2 (DN 8 to DN 90):  12 inches (305 mm) long and 0.048 inch (1.22 mm) thick.

b. NPS 4 (DN 100):  12 inches (305 mm) long and 0.06 inch (1.52 mm) thick.

c. NPS 5 and NPS 6 (DN 125 and DN 150):  18 inches (457 mm) long and 0.06 inch (1.52 mm) thick.

d. NPS 8 to NPS 14 (DN 200 to DN 350):  24 inches (610 mm) long and 0.075 inch (1.91 mm) thick.

e. NPS 16 to NPS 24 (DN 400 to DN 600):  24 inches (610 mm) long and 0.105 inch (2.67 mm) thick.

5. Pipes NPS 8 (DN 200) and Larger:  Include wood inserts.

6. Insert Material:  Length at least as long as protective shield.

7. Thermal-Hanger Shields:  Install with insulation same thickness as piping insulation.

3.3 EQUIPMENT SUPPORTS

Edit first paragraph below to suit Project.

A. Fabricate structural-steel stands to suspend equipment from structure overhead or to support equipment above floor.

B. Grouting:  Place grout under supports for equipment and make smooth bearing surface.

C. Provide lateral bracing, to prevent swaying, for equipment supports.

3.4 METAL FABRICATIONS

A. Cut, drill, and fit miscellaneous metal fabrications for [trapeze pipe hangers] [and] [equipment supports].

B. Fit exposed connections together to form hairline joints.  Field weld connections that cannot be shop welded because of shipping size limitations.

C. Field Welding:  Comply with AWS D1.1 procedures for shielded metal arc welding, appearance and quality of welds, and methods used in correcting welding work, and with the following:

1. Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

2. Obtain fusion without undercut or overlap.

3. Remove welding flux immediately.

4. Finish welds at exposed connections so no roughness shows after finishing and contours of welded surfaces match adjacent contours.

3.5 ADJUSTING

A. Hanger Adjustments:  Adjust hangers to distribute loads equally on attachments and to achieve indicated slope of pipe.

B. Trim excess length of continuous-thread hanger and support rods to [1-1/2 inches (40 mm)] <Insert other>.

3.6 PAINTING

Delete paragraph and subparagraph below if a Division 9 painting Section is in Project Manual.

A. Touch Up:  Clean field welds and abraded areas of shop paint.  Paint exposed areas immediately after erecting hangers and supports.  Use same materials as used for shop painting.  Comply with SSPC-PA 1 requirements for touching up field-painted surfaces.

1. Apply paint by brush or spray to provide minimum dry film thickness of 2.0 mils (0.05 mm).

Retain first paragraph below if a Division 9 painting Section is in Project Manual.  Revise reference if Division 9 Section "High-Performance Coatings" applies instead.

B. Touch Up:  Cleaning and touchup painting of field welds, bolted connections, and abraded areas of shop paint on miscellaneous metal are specified in Division 9 [painting Sections.] [Section "High-Performance Coatings."]

C. Galvanized Surfaces:  Clean welds, bolted connections, and abraded areas and apply galvanizing-repair paint to comply with ASTM A 780.

END OF SECTION 15062

HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT
15062 - 1

