Copyright 2004 AIA
MASTERSPEC
12/04

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15072 - VIBRATION AND SEISMIC CONTROLS FOR FIRE-SUPPRESSION PIPING AND EQUIPMENT
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Isolation pads.

2. Isolation mounts.

3. Restrained elastomeric isolation mounts.

4. Restraining braces.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. IBC:  International Building Code.

B. ICC-ES:  ICC-Evaluation Service.

C. OSHPD:  Office of Statewide Health Planning and Development for the State of California.

1.4 PERFORMANCE REQUIREMENTS

A. Seismic-Restraint Loading:

Obtain values for items in subparagraphs and associated subparagraphs below from Project structural engineer or from SEI/ASCE 7.  If the code at Project site is other than the IBC or NFPA 5000, revise parameters to comply with applicable code.

Specify design spectral response acceleration at short periods (0.2 second) and at 1 second based on site class in subparagraph below.  Typical values range from 2 to 200 percent.  Design spectral response acceleration is required for seismic force calculations to size seismic restraints.  For each seismic restraint, include component importance factor, component response modification factor, and component amplification factor in the Fire-Suppression Vibration-Control and Seismic-Restraint Device Schedule.

1. Site Class as Defined in the IBC:  [A] [B] [C] [D] [E] [F].

In subparagraph below, retain Seismic Use Group or Building Category for Project structure from three classifications defined in the IBC.

2. Assigned Seismic Use Group or Building Category as Defined in the IBC:  [I] [II] [III].

Retain first three subparagraphs below if these values are not included in the Fire-Suppression Vibration-Control and Seismic-Restraint Device Schedule on Drawings.  Factors below often vary among supported equipment.  However, it is possible to specify maximum values for these factors for various classes of equipment or for all equipment instead of scheduling each piece of equipment.

a. Component Importance Factor:  [1.0] [1.5] <Insert value>.

b. Component Response Modification Factor:  [1.5] [2.5] [3.5] [5.0] <Insert value>.

c. Component Amplification Factor:  [1.0] [2.5] <Insert value>.

3. Design Spectral Response Acceleration at Short Periods (0.2 Second):  <Insert percent>.

4. Design Spectral Response Acceleration at 1-Second Period:  <Insert percent>.

1.5 SUBMITTALS

A. Product Data: For the following:

1. Include rated load, rated deflection, and overload capacity for each vibration isolation device.

2. Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic-restraint component used.

See Evaluations for a discussion on seismic-restraint capacities and rating services.

a. Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

b. Annotate to indicate application of each product submitted and compliance with requirements.

Paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

B. Delegated-Design Submittal:  For vibration isolation and seismic-restraint details indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations:  Calculate static and dynamic loading due to equipment weight and operation, seismic forces required to select vibration isolators, seismic restraints, and for designing vibration isolation bases.

Retain subparagraph and associated subparagraphs below only if seismic design requirements apply but calculations have not been made and details or charts on Drawings do not describe seismic restraints in detail.  Retaining subparagraph will require Contractor to submit seismic-restraint Delegated-Design Drawings prepared by a professional engineer.  Revise to suit local requirements.

2. Seismic-Restraint Details:

a. Design Analysis:  To support selection and arrangement of seismic restraints.  Include calculations of combined tensile and shear loads.

b. Details:  Indicate fabrication and arrangement.  Detail attachments of restraints to the restrained items and to the structure.  Show attachment locations, methods, and spacings.  Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events.  Indicate association with vibration isolation devices.

c. Preapproval and Evaluation Documentation:  By [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For [professional engineer] [and] [testing agency].

1.6 QUALITY ASSURANCE

If an independent testing agency is required, see Division 1 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7.  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

B. Comply with seismic-restraint requirements in the IBC and NFPA 13 unless requirements in this Section are more stringent.

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

C. Welding:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

D. Seismic-restraint devices shall have horizontal and vertical load testing and analysis and shall bear anchorage preapproval OPA number from OSHPD, preapproval by ICC-ES, or preapproval by another agency acceptable to authorities having jurisdiction, showing maximum seismic-restraint ratings.  Ratings based on independent testing are preferred to ratings based on calculations.  If preapproved ratings are not available, submittals based on independent testing are preferred.  Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

PART 2 -  PRODUCTS

2.1 VIBRATION ISOLATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Ace Mountings Co., Inc.

2. Amber/Booth Company, Inc.

3. California Dynamics Corporation.

4. Isolation Technology, Inc.

5. Kinetics Noise Control.

6. Mason Industries.

7. Vibration Eliminator Co., Inc.

8. Vibration Isolation.

9. Vibration Mountings & Controls, Inc.

10. <Insert manufacturer's name>.

Copy paragraph and subparagraph below for each type of pad configuration required for Project.  Use drawing designation and coordinate with the Fire-Suppression Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

D. Pads <Insert drawing designation>:  Arranged in single or multiple layers of sufficient stiffness for uniform loading over pad area, molded with a nonslip pattern and galvanized-steel baseplates, and factory cut to sizes that match requirements of supported equipment.

Verify availability of various pad materials with manufacturers.

1. Resilient Material:  Oil- and water-resistant [neoprene] [rubber] [hermetically sealed compressed fiberglass].

Copy paragraph and subparagraphs below for each type of mount configuration required for Project.  Use drawing designation and coordinate with the Fire-Suppression Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

E. Mounts <Insert drawing designation>:  Double-deflection type, with molded, oil-resistant rubber, hermetically sealed compressed fiberglass, or neoprene isolator elements with factory-drilled, encapsulated top plate for bolting to equipment and with baseplate for bolting to structure.  Color-code or otherwise identify to indicate capacity range.

1. Materials:  Cast-ductile-iron or welded steel housing containing two separate and opposing, oil-resistant rubber or neoprene elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

2. Neoprene:  Shock-absorbing materials compounded according to the standard for bridge-bearing neoprene as defined by AASHTO.

Copy paragraph and subparagraphs below for each type of restrained mount configuration required for Project.  Use drawing designation and coordinate with the Fire-Suppression Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

F. Restrained Mounts <Insert drawing designation>:  All-directional mountings with seismic restraint.

1. Materials:  Cast-ductile-iron or welded steel housing containing two separate and opposing, oil-resistant rubber or neoprene elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

2. Neoprene:  Shock-absorbing materials compounded according to the standard for bridge-bearing neoprene as defined by AASHTO.

2.2 SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this Article with structural engineer and with Drawings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amber/Booth Company, Inc.

2. California Dynamics Corporation.

3. Cooper B-Line, Inc.; a division of Cooper Industries.

4. Hilti, Inc.

5. Kinetics Noise Control.

6. Loos & Co.; Cableware Division.

7. Mason Industries.

8. TOLCO Incorporated; a brand of NIBCO INC.

9. Unistrut; Tyco International, Ltd.

10. <Insert manufacturer's name>.

See Evaluations for a discussion on seismic-restraint capacities and rating services.

D. General Requirements for Restraint Components:  Rated strengths, features, and applications shall be as defined in reports by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

1. Structural Safety Factor:  Allowable strength in tension, shear, and pullout force of components shall be at least [four] <Insert number> times the maximum seismic forces to which they will be subjected.

E. Channel Support System:  MFMA-3, shop- or field-fabricated support assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; and rated in tension, compression, and torsion forces.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings.  Use with either channel- or cable-type bracing assemblies when required to counter seismic forces.  Detail fabrication and indicate locations on Drawings.

F. Hanger Rod Stiffener:  [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

G. Bushings for Floor-Mounted Equipment Anchor Bolts:  Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

H. Bushing Assemblies for Wall-Mounted Equipment Anchorage:  Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings and matched to type and size of attachment devices used.

I. Resilient Isolation Washers and Bushings:  One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

Expansion-type anchor bolts are not permitted by SEI/ASCE 7 for nonisolated equipment in excess of 10 hp (7.46 kW).

J. Mechanical Anchor Bolts:  Drilled-in and stud-wedge or female-wedge type in zinc-coated steel for interior applications and stainless steel for exterior applications.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.  Minimum length of eight times diameter.

K. Adhesive Anchor Bolts:  Drilled-in and capsule anchor system containing polyvinyl or urethane methacrylate-based resin and accelerator, or injected polymer or hybrid mortar adhesive.  Provide anchor bolts and hardware with zinc-coated steel for interior applications and stainless steel for exterior applications.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

2.3 FACTORY FINISHES

Specify field-painting requirements in Division 9 painting Sections.  Verify compatibility of factory finishes with field-applied coats.

A. Finish:  Manufacturer's standard prime-coat finish ready for field painting.

Edit paragraph and subparagraphs below to include custom colors.  Coordinate custom-color requirements with sample submittal requirements.

B. Finish:  Manufacturer's standard paint applied to factory-assembled and -tested equipment before shipping.

1. Powder coating on springs and housings.

2. All hardware shall be galvanized.  Hot-dip galvanize metal components for exterior use.

3. Baked enamel or powder coat for metal components on isolators for interior use.

4. Color-code or otherwise mark vibration isolation and seismic-control devices to indicate capacity range.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and equipment to receive vibration isolation and seismic-control devices for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

A. Multiple Pipe Supports:  Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger rod stiffeners.

B. Hanger Rod Stiffeners:  Install hanger rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

C. Strength of Support and Seismic-Restraint Assemblies:  Where not indicated, select sizes of components so strength will be adequate to carry present and future static and seismic loads within specified loading limits.

3.3 VIBRATION-CONTROL AND SEISMIC-RESTRAINT DEVICE INSTALLATION

A. Equipment Restraints:

1. Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

2. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] providing required submittals for component.

B. Piping Restraints:

1. Comply with requirements in MSS SP-127 and NFPA 13.

In first subparagraph below, options for 40 and 80 feet (12 and 24 m) are recommended by MSS SP-127.  Consider reducing these dimensions based on the configuration of piping.

2. Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

3. Brace a change of direction longer than 12 feet (3.7 m).

C. Install cables so they do not bend across edges of adjacent equipment or building structure.

D. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] providing required submittals for component.

E. Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

F. Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

G. Attachment to Structure:  If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

H. Drilled-in Anchors:

1. Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors.  Do not damage existing reinforcing or embedded items during coring or drilling.  Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling.  Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors:  Protect threads from damage during anchor installation.  Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Adhesive Anchors:  Clean holes to remove loose material and drilling dust prior to installation of adhesive.  Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

5. Set anchors to manufacturer's recommended torque, using a torque wrench.

6. Install zinc-coated steel anchors for interior and stainless-steel anchors for exterior applications.

3.4 ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this Article with Drawings.

A. Install flexible connections in piping where they cross seismic joints, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment.  Comply with requirements in Division 13 Section "Fire-Suppression Piping" for piping flexible connections.

3.5 FIRE-SUPPRESSION VIBRATION-CONTROL AND SEISMIC-RESTRAINT DEVICE SCHEDULE

Revise schedule below to suit Project.  Do not duplicate requirements in Part 2.  Refer to a completed example in the Evaluations for an explanation on how to use schedules.  If a schedule is not included on Drawings, retain below to indicate location and type of required vibration isolators and seismic restraints.

Copy and re-edit paragraph and subparagraphs below for each piece of supported or suspended equipment required.

A. Supported or Suspended Equipment:  <Insert name and drawing designation>.

1. Equipment Location:  <Insert room number>.

2. Pads:

a. Material:  [Neoprene] [Rubber] [Hermetically sealed compressed fiberglass].

b. Thickness:  <Insert inches (mm)>.

c. Number of Pads:  <Insert number> thick.

3. Isolator Type:  <Insert generic name or designation used in Part 2>.

4. Minimum Deflection:  <Insert inches (mm)>.

5. Component Importance Factor:  [1.0] [1.5].

6. Component Response Modification Factor:  [1.5] [2.5] [3.5] [5.0].

7. Component Amplification Factor:  [1.0] [2.5].

END OF SECTION 15072

VIBRATION AND SEISMIC CONTROLS FOR FIRE-SUPPRESSION PIPING AND EQUIPMENT
15072 - 1

